## Sheet1
Job order No | Timestamp | Email Address | Client Name | Container No | Container Size | Machine Make | Work Type | Client Type | Job Type | Issue(s) found | Remedial Action | List of Spares Required | Spares Required | Reason / Cause | Form Link | Reefer Unit | Reefer Unit Model Name (Thinline / MP) | Reefer Unit Serial No | Controller Configuration Number | Controller Version | Brand new / Used | Crystal Smart Sr No. | Technician Name | Technician Required at Client Site | What's the complaint?
JUL001 | 2024-07-11 11:14 | pravin.shinde@crystalgroup.in | Bharat Petroleum | CXRU1043337 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | NA | Installation & Training provided | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL001 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | SHAHBUDDIN
JUL002 | 2024-07-11 11:15 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9231009 | 40-SUPERSTORE | DAIKIN | SERVICE-ON CALL | LEASE | FOC | Due to power fluctuation container not working | Reset the unit and found working | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL002 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | RAMIZ
JUL003 | 2024-07-11 11:17 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | APRU5091606 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Evaporator motor and contactor defective | need to replaced part currently container not working | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL003 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | SHAHBUDDIN
JUL004 | 2024-07-11 11:19 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9230980 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Condenser coil leak and keypad, display required | need parts | Condenser coil - 1 no keypad - 1 no display - 1 no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL004 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | SHAHBUDDIN
JUL005 | 2024-07-11 11:20 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9231009 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Display & Keypad defective | need parts | Display - 1 no Keypad - 1 no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL005 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | SHAHBUDDIN
JUL006 | 2024-07-11 11:21 | pravin.shinde@crystalgroup.in | Andabar | TRIU6616531 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | SALE | FOC | Brazing not done properly | doing rework of brazing and working well | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL006 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Used |  | VIRENDRA
JUL007 | 2024-07-11 11:23 | pravin.shinde@crystalgroup.in | Crystal Yard-Chennai | PCIU6010243 | 40-REEFER | DAIKIN | SERVICE-AT SITE | STOCK | FOC | DISPLAY, SHEETKEY, FILTER REQU | REPLACED ALL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL007 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | VIRENDRA
JUL008 | 2024-07-11 11:24 | pravin.shinde@crystalgroup.in | Qwik Supply | CICU2779940 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR CONTACTOR FAULTY | NEED TO REPLACED | Compressor Contactor - 1 NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL008 | Thermoking | Magnum Plus | E0GM030268 | ABC782800322010065 |  | BrandNew |  | SHAHBUDDIN
JUL009 | 2024-07-11 11:28 | pravin.shinde@crystalgroup.in | Symbiotech | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-ON CALL | SALE | FOC | EVP COIL RUSTY | NEED TO REPLACED | DAIKIN EVP COIL - 1 NO DAIKIN STAINER - 1 NO REFRIGERANT GAS - 5 KGS BRAZING SET - 1 SET VACUUM PUMP - 1 NO NITROGEN - 1 NO BRAZING ROD - 15 NOS |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL009 | Daikin | Daikin |  |  |  | Used |  | UMESH
JUL010 | 2024-07-11 11:30 | pravin.shinde@crystalgroup.in | Qwik Supply | TITU7263521 | 20-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | COMPRESSOR NOISY | NEE TO TOP UP GAS AND OIL | REFRIGERANT GAS 2 KGS COMPRESSOR OIL 1 LTR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL010 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH
JUL011 | 2024-07-11 11:31 | pravin.shinde@crystalgroup.in | Qwik Supply | TRIU6681440 | 20-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | NOT ABLE TO IDENTIFY ON CALL | NEED TO ATTEND PHYSICALLY | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL011 | Carrier - Transcold | Transcold |  |  |  | Used |  | UMESH
JUL012 | 2024-07-11 11:33 | pravin.shinde@crystalgroup.in | Qwik Supply | TRIU6681440 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DISPLAY, KEYPAD, AMBIENT & SUPPLY SENSOR, CONTACTOR, FILTER REQ | NEED PARTS | CARRIER THINLINE DISPLAY - 1 NO CARRIER THINLINE KEYPAD - 1 NO CARRIER AMBIENT SENSOR - 1 NO CARRIER SUPPLY SENSOR - 1 NO CARRIER COMPRESSOR CONTACTOR 30A - 1 NO LIQUID FILTER - 1 NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL012 | Carrier - Transcold | Transcold |  |  |  | Used |  | UMESH
JUL013 | 2024-07-16 22:32 | support@crystalgroup.in | Crystal Yard-JNPT | GESU9379498 | 40-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | NA | NA | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL013 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH
JUL014 | 2024-07-16 22:41 | support@crystalgroup.in | Jubilant Consumer | GRMU3607418 | NA | NA | NA | NA | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL014 | Daikin |  |  |  |  | Used |  | UMESH
JUL015 | 2024-07-16 22:47 | support@crystalgroup.in | Jubilant Consumer | GRMU3607418 | NA | NA | SERVICE-AT SITE | NA | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL015 | Daikin |  |  |  |  | Used |  | UMESH
JUL016 | 2024-07-16 22:54 | support@crystalgroup.in | Crystal Yard-Vizag | KKFU6712802 | 40-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | no gas in system, filter need to repair, need to check leak in gas and supply sensor req, ISO plug & Gas required | Need spares | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL016 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | TP-FLAGSHIP DEPOT
JUL017 | 2024-07-16 23:10 | support@crystalgroup.in | Qwik Supply | MYRU4518356 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | CONTROL PANEL BURN | Need spares | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL017 | Daikin | LXE10E136 A2 | M005086 | DCOZ3E |  | Used | JSGA622180065 | UMESH
JUL018 | 2024-07-16 23:15 | support@crystalgroup.in | APL Health | APRU5093234 | 40-REEFER | CARRIER-THINLINE | INSTALLATION | LEASE | FOC | Condenser coil leak, EVP motor heavy sound, strip curtain req | Need to close leak and required motor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL018 | Carrier - Thinline | Thinline | [5 empty] | VIRENDRA
JUL019 | 2024-07-16 23:20 | support@crystalgroup.in | APL Health | CXRU1032327 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | Sheetkey not working well and suction gas sensor required | required part | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL019 | DAikin | LXE10E147F2 | M000737 | K31405125030 | DECOS 3F 2553 / 1 | Used | JSGA622340153 | VIRENDRA
JUL020 | 2024-07-16 23:24 | support@crystalgroup.in | APL Health | PCIU6007065 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | display, led light, filter, strip curtain required | required part | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL020 | Daikin |  |  |  |  | Refurbished |  | VIRENDRA
JUL021 | 2024-07-16 23:29 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6706142 | 40-REEFER | CARRIER-THINLINE | PREVENTIVE MAINTENANCE | LEASE | FOC | Coil dirty, supply sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL021 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040294 | VIRENDRA
JUL022 | 2024-07-16 23:34 | support@crystalgroup.in | Ajinomoto Bio Pharma | BMOU9766180 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty, return sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL022 | Daikin |  |  |  |  | used |  | VIRENDRA
JUL023 | 2024-07-16 23:36 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6994964 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Coil dirty, supply sensor defective & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL023 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | VIRENDRA
JUL024 | 2024-07-16 23:40 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6712079 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Coil dirty, supply battery pack & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL024 | Carrier - Thinline | Thinline |  | 69NT40541321 |  | brand New | JSGA623040320 | VIRENDRA
JUL025 | 2024-07-28 10:32 | pravin.shinde@crystalgroup.in | Jubilant Consumer | GRMU3607418 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EVP INLET SENSOR FAULTY | REPLACED AND FOUND OKAY | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL025 | Daikin |  |  |  |  | Used |  | UMESH
JUL026 | 2024-07-28 10:33 | pravin.shinde@crystalgroup.in | DHL Supply | DFOU6120281 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | COIL DIRTY, LOW GAS | GAS REFILED AND CHECKED ALL PARAMETER WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL026 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | VIRENDRA
JUL027 | 2024-07-28 10:34 | pravin.shinde@crystalgroup.in | Shivamrut | CXRU1032498 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | SHEETKEY NEED TO REPLACED - DEFROST BUTTON NOT WORKING | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL027 | DAikin | LXE10E147F2 | M000892 | K31410139812 | DECOS 3F 2606 / 1 | used | JSGA622340362 | RAMIZ
JUL028 | 2024-07-28 10:35 | pravin.shinde@crystalgroup.in | Oriental Yeast | CICU1938117 | 20-SUPERFREEZER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | SET TEMP IS M20 & CONTAINER GOES TO M28 | NEED TO CHECK SENSOR | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL028 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | RAMIZ
JUL029 | 2024-07-28 10:36 | pravin.shinde@crystalgroup.in | Mochan Foods | MYRU4515260 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | INSTALLATION | done | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL029 | Daikin | Daikin | M0001112 | LXECOE136A2 | 24C2 | Used |  | RAMIZ
JUL030 | 2024-07-28 10:37 | pravin.shinde@crystalgroup.in | Mochan Foods | MYRU4515260 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | SHEETKEY & DISPLAY NOT PROPER, INLET SENSOR FAULTY, door damage | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL030 | Daikin | Daikin | M0001112 | LXECOE136A2 | 24C2 | Used |  | RAMIZ
JUL031 | 2024-07-28 10:38 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9230980 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Condenser coil leak and keypad, display required | REPLACED CONDENSER COIL AND NITROGEN TEST DONE AND GAS CHARGED | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL031 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | SHAHBUDDIN
JUL032 | 2024-07-28 10:40 | pravin.shinde@crystalgroup.in | GMR Hydrabad Air cargo | CGMU2990461 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | NEED AMBIENT & SUPPLY SENSOR | REQUIRED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL032 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | VIRENDRA
JUL033 | 2024-07-28 10:41 | pravin.shinde@crystalgroup.in | Qwik Supply | TCLU1903088 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL033 | Daikin | Daikin |  |  |  | Used | JSGA622180051 | UMESH
JUL034 | 2024-07-28 10:41 | pravin.shinde@crystalgroup.in | Reliance Industries | TITU7263521 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Leak in ESV and ISV valve | required parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL034 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH
JUL035 | 2024-07-28 10:42 | pravin.shinde@crystalgroup.in | Reliance Industries | GESU9440432 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | VALVE LEAK | required parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL035 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | UMESH
JUL036 | 2024-07-28 10:44 | pravin.shinde@crystalgroup.in | Reliance Industries | TDRU7151675 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL036 | Daikin | Daikin |  |  |  |  | JSGA622180053 | UMESH
JUL037 | 2024-07-28 10:45 | pravin.shinde@crystalgroup.in | North West logistic | TITU9928040 | 40-REEFER | TK-MP4000 | SERVICE-ON CALL | LEASE | FOC | NOT ABLE TO FIND ON CALL | NEED TO VISIT | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL037 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | PRAVIN
JUL038 | 2024-07-28 10:46 | pravin.shinde@crystalgroup.in | Siemens | TRIU6617646 | 20-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | SALE | FOC | SPARES SENT | REQ TECHNICIAN FOR FITTING | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL038 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | VINIT
JUL039 | 2024-07-28 10:47 | pravin.shinde@crystalgroup.in | Reliance Industries | CXRU1043912 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL039 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH
JUL040 | 2024-07-28 10:48 | pravin.shinde@crystalgroup.in | Jubilant Consumer | GRMU3607418 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | VERIFICATION | SATISFIED CONTAINER RUNNING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL040 | Daikin |  |  |  |  | Used |  | UMESH
JUL041 | 2024-07-28 23:51 | pravin.shinde@crystalgroup.in | Kiranakart | KKFU6711832 | 40-REEFER | CARRIER-THINLINE | INSTALLATION | LEASE | FOC | installation | INSTALLATION & TRANING DONE | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL041 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA623040288 | UMESH
JUL042 | 2024-07-28 23:53 | pravin.shinde@crystalgroup.in | Kiranakart | GESU9460634 | 40-REEFER | CARRIER-ELITLINE | INSTALLATION | LEASE | FOC | INSTALLATION | INSTALLATION DONE BUT NEED SOME PARTS TO RECTIFY | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL042 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH
JUL043 | 2024-07-28 23:55 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | APRU5091606 | 40-REEFER | CARRIER-THINLINE | REPAIR | LEASE | FOC | MOTORS DEFECTIVE | MOTOR CHANGED AND GAS FILL NOW WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL043 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | SHAHBUDDIN
JUL044 | 2024-07-28 23:58 | pravin.shinde@crystalgroup.in | Kiranakart | GESU9460634 | 40-REEFER | CARRIER-ELITLINE | REPAIR | LEASE | FOC | AL-66 &AL-24 OBSERVED | VALVE CHANGED GAS REFILL AND NOW WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL044 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH
JUL045 | 2024-07-29 00:01 | pravin.shinde@crystalgroup.in | Heterp Plasma | CXRU1030387 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | ICE FORMATION ON COMPRESSOR | SUGGEST TO DO NOT CHANGE OVER DIRECTLY FIRST DO THE DEFROST AND THEN CHANGE THE SAME | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL045 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | VIRENDRA
JUL046 | 2024-07-29 00:03 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | WNGU3021858 | 20-DRY GP | NA - DRY | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL046 | [7 empty] | KSHIROD
JUL047 | 2024-07-29 00:04 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | HDMU2595002 | 20-DRY GP | NA-DRY | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL047 | [7 empty] | KSHIROD
JUL048 | 2024-07-29 00:20 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | HDMU2574289 | 20-DRY GP | NA | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL048 | [7 empty] | KSHIROD
JUL049 | 2024-07-29 00:21 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | SITE CABIN | 20-DRY GP | NA-dry | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL049 | [7 empty] | KSHIROD
JUL057 | 2024-08-20 04:00 | support@crystalgroup.in | Qwik Supply | MYRU4518356 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL057 | Daikin | LXE10E136 A2 | M005086 | DCOZ3E |  | Used | JSGA622180065 | UMESH
JUL054 | 2024-08-20 04:00
JUL058 | 2024-08-20 06:37 | vinit.mewada@crystalgroup.in | Qwik Supply | TCLU1903088 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL058 | Daikin | Daikin |  |  |  | Used | JSGA622180051 | UMESH
AUG016 | 2024-08-21 04:01 | vinit.mewada@crystalgroup.in | MOCHAN FOOD | CXRU1026582 | 40FT | 2011 | SERVICE-AT SITE | LEASE | NA | SHEET KEY DEFECTIVE, SUCATION GAS SENSOR | NEED TO REPLACE SHEET KEY AND SUCATION GAS SENSOR | SHEET KEY AND SUCATION GAS SENSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG016 | DAikin | LXE10E147F2 | M001597 | K31408135807 | DECOS 3F 2551 / 1 | Used | JSGA621320212 | RAMIZ
AUG017 | 2024-08-21 04:16 | vinit.mewada@crystalgroup.in | VERKA AMRITSAR | CXRU1186385 | 40FT | 2012 | SERVICE-AT SITE | LEASE | NA | PRE MAINTANCE REQUIRED | PRE MAINTAINCE | NA |  |  |  | Daikin | LXE10E136F2 | M002086 | K31505147912 | DECOS 3F 2557 / 1 | Used | JSGA622180073 | SHAHBUDDIN
AUG015 | 2024-08-21 04:24 | vinit.mewada@crystalgroup.in | SHIVAMRUT - AKLUJ | CXRU1032498 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | ALF803, SHEET KEY NOT WORKING , UNIT OFF | NEED TO REPLACE HUS SENSOR AND SHEET KEY, CONTROLLER AND EXPANCTION VALVE AND COIL | HUMADITY SENSOR , SHEET KEY, CONTROLLER AND EXPANCTION VALVE AND COIL |  |  |  | DAikin | LXE10E147F2 | M000892 | K31410139812 | DECOS 3F 2606 / 1 | used | JSGA622340362 | RAMIZ
AUG014 | 2024-08-21 04:35 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | CICU3876631 | 10 FT | Thermoking 2023 | SERVICE-AT SITE | LEASE | AMC | UNIT NOT WORKING | DISCONNECTED THE BATTERY MODULE ( NEED TO REPLACE BATTERY ) | BATTERY PACK -MP4000 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG014 | Thermoking | Magnum + | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New |  | RAMIZ
AUG013 | 2024-08-21 04:44 | vinit.mewada@crystalgroup.in | FDC PHARMA | TRIU6616911 | 20 FT | 2010 | SERVICE-AT SITE | LEASE | NA | CARRIER UNIT OFF LODGE INSPECTION AND PTI, FIND DISPLAY IS FADED AND NEED TO COMPRESSOR OIL FOR REFILING. | NEED TO CKECK ALL PARTS WITH CONTAINER STATUS | DISPLAY - 1, COMPRESSOR - 1, BATTERY PACE CARRIER (AC53) --1 , RISLU C- 1KG |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG013 | Carrier - Thinline | Thinline |  | M3X60329564 |  | Used |  | SHAHBUDDIN
AUG012 | 2024-08-21 04:49 | vinit.mewada@crystalgroup.in | QWIK SUPPLY SHRIHID | NYKU7931452 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | PRE MAINTANANCE | NEED PRE MAINTAINANCE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG012 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | SHAHBUDDIN
AUG011 | 2024-08-21 04:55 | vinit.mewada@crystalgroup.in | QWIK SUPPLY | MYRU4501435 | 40 FT | 2010 | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PM SERVICES | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG011 | Daikin | Daikin |  | LXE10E136A |  | Refurbished |  | SHAHBUDDIN
AUG010 | 2024-08-21 04:59 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURU | CICU1799140 | 10 FT | 2020 | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PRE MAINTAINACE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG010 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | SHAHBUDDIN
AUG009 | 2024-08-21 05:01 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | TCLU1130265 | 40 FT | 2010 | SERVICE-AT SITE | NA | NA | PM SERVICES | PRE MAINTAINACE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG009 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN
AUG008 | 2024-08-21 05:06 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | CXRU1045453 | 40 FT | 2011 | SERVICE-AT SITE | NA | NA | UNIT NOT WORKING WITH AC F803 / F 809 | NA | GAS R13HA, FLITER DRIVER , TEMP SENSOR , INLET SENSOR, VACCUM PUMP |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG008 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | SHAHBUDDIN
AUG007 | 2024-08-21 05:11 | vinit.mewada@crystalgroup.in | BIOCON | TDPU5800414 | 40FT | 2011 | SERVICE-AT SITE | LEASE | NA | ALE107, COMPRESSOR STOP | NA | R13YA DISCHARGE CENTER , INLET SENSOR ELDER DRIVER COMPRESSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG007 | [7 empty] | RAMIZ
AUG004 | 2024-08-21 05:16 | vinit.mewada@crystalgroup.in | LAURUS LAB UNIT 2 | CICU1442180 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PM SERVICES | SHEET KEY LOGO, SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG004 | [7 empty] | VIRENDRA
AUG003 | 2024-08-21 05:22 | vinit.mewada@crystalgroup.in | LAURUS LAB UNIT 2 | CICU1442220 | 40 FT | NA | SERVICE-AT SITE | SALE | CHARGEABLE | DISMENTAL AND REFIX THE ISSUE | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG003 | [7 empty] | VIRENDRA
AUG002 | 2024-08-21 05:39 | vinit.mewada@crystalgroup.in | MOCHAN FOOD | MYRU4500552 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | TEMP NOT PULL DOWN AS DESIRE | CLEAN CONDENSER COIL WITH FREAH WATER, MANUAL DEFROST DONE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG002 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | RAMIZ
AUG001 | 2024-08-21 22:32 | vinit.mewada@crystalgroup.in | ORIENTAL YEAST SATARA | CICU1938117 | NA | 2021 | SERVICE-AT SITE | NA | NA | TEMPERATURE ISSUE | CHECKED AND FOUND CONTAINER RAISEDTHE TEMP -10* TO 12* . THE SET POINT IS -20* AND COMPRESSOR AT OFF -28 TO -32 *. TO SOLVE THIS ISSUE NEED TO MAINTAIN 3 TO 5 TON MIN. VOLUME. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG001 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | UMESH
JUL059 | 2024-08-21 23:02 | vinit.mewada@crystalgroup.in | LUPIN LIMITED | TCLU1908599 | 20 FT | NA | SERVICE-AT SITE | NA | NA | REGULAR SURVEY | NA | UMESH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL059 | DAIKIN LXE |  |  |  |  | USed |  | UMESH
JUL060 | 2024-08-21 23:10 | vinit.mewada@crystalgroup.in | BHARAT PETROLEUM | TCLU1908599 | 20 FT | 2010 | SERVICE-AT SITE | LEASE | NA | PREMAINTANCE | PREMAINTANCE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL060 | DAIKIN LXE |  |  |  |  | USed |  | UMESH
JUL061 | 2024-08-21 23:20 | vinit.mewada@crystalgroup.in | QWIK SUPPLY LUCKNOW | TRIU6618391 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | DATA SUPPLY, RETURN, DEFROST X 2 NOS REQUIRED | coil cleaned with water, checked settings all found okay, checked all parameters, required spares | DATA SUPPLY SENSOR, RETURN SENSOR, DEFROST SENSOR ( MAIN UNIT ) AND DEFROST SENSOR ( STANDBY UNIT ) |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL061 | Carrier - Thinline | Thinline |  |  |  | Used |  | UMESH
JUL062 | 2024-08-21 23:24 | vinit.mewada@crystalgroup.in | Qwik Supply | CICU2779914 | 20 FT | 2022 | SERVICE-AT SITE | LEASE | NA | PRE MAINTAINANCE | PRE MAINTAINANCE | EVP SENSOR, SUPPLY SENSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL062 | Thermoking | Magnum Plus | E0GM030254 | ABC782800322010282 |  | BrandNew |  | UMESH
JUL063 | 2024-08-21 23:33 | vinit.mewada@crystalgroup.in | ITC LTD | PCIU6003244 | 40 FT | 2007 | SERVICE-AT SITE | LEASE | NA | Panle foaming weak, Filter rusty, Evp motor noisy | required spares | FILLTER , RISEUP MOTOR , REFORMING R/S- 2,3,67 AND L/S- 5TH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL063 | Daikin |  |  |  |  | used |  | VIRENDRA
JUL064 | 2024-08-21 23:39 | vinit.mewada@crystalgroup.in | ITC LIMITED | MYRU4519748 | 40 FT | 2010 | SERVICE-AT SITE | LEASE | NA | body work and evaporaor motor heavy noisy | REQUIRED SPARES | ALUMINIUM DAMPER SHEET, EVP MOTOR HEAVY SOUNDS |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL064 | Daikin | Daikin | M003143 | LXE10E136A |  | Used | JSGA623040176 | VIRENDRA
JUL065 | 2024-08-21 23:47 | vinit.mewada@crystalgroup.in | QWIK SUPPLY | TITU9927240 | 40 FT | 2013 | SERVICE-AT SITE | LEASE | NA | keypad, mantrap & patch work required | required spares | KEYPAB (MP400), MANTRAP , R/S PANEL NO.5 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL065 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | UMESH
JUL066 | 2024-08-21 23:51 | vinit.mewada@crystalgroup.in | APL Health | APRU5093234 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | MOTOR NOISY | WORKING WELL | R 134A |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL066 | Carrier - Thinline | Thinline | [5 empty] | VIRENDRA
JUL067 | 2024-08-22 00:01 | vinit.mewada@crystalgroup.in | APL HEALTHCARE | CXRU1032320 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | REPLACED THE SUCTION GAS SENSOR | WORKING WELL | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL067 | [7 empty] | VIRENDRA
JUL068 | 2024-08-22 00:04 | vinit.mewada@crystalgroup.in | APL HEALTHCARE | CXRU1032327 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | COIL DAIRTY | Coil cleaned with water, checked settings all found okay, checked all parameters | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL068 | DAikin | LXE10E147F2 | M000737 | K31405125030 | DECOS 3F 2553 / 1 | Used | JSGA622340153 | VIRENDRA
JUL069 | 2024-08-22 00:09 | vinit.mewada@crystalgroup.in | KIRANAKART ( ZEPTO ) | GESU9460634 | 40 FT | 2008 | SERVICE-AT SITE | LEASE | NA | SPT WITH JACK REQUIRED AND CONTROLLER SUSPECTED | REQUIRED SPARES | SPT WITH JACK , CONTROLLER |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL069 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH
JUL070 | 2024-08-22 00:18 | vinit.mewada@crystalgroup.in | LUPIN LIMITED | CCLU1036859 | 20 FT | NA | SERVICE-AT SITE | LEASE | NA | CONDENSER MOTOR IS NOISY | NEED TO CHANGE BEARINGS | CONDENSER FAN MOTOR BEARING ( SMALL AND BIG ) |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL070 | Carrier |  |  |  |  | Used | JSGA623040314 | RAMIZ
JUL071 | 2024-08-22 00:20 | vinit.mewada@crystalgroup.in | JUBILANT CONSUMER | TRIU6687350 | 20 FT | 2011 | SERVICE-AT SITE | LEASE | NA | LOW GAS IN THE SYSTEM | LOW GAS IN THE SYSTEM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL071 | Carrier |  |  |  |  | USed |  | SHAHBUDDIN
JUL072 | 2024-08-22 00:25 | vinit.mewada@crystalgroup.in | Symbiotech | TRIU6617292 | 20 FT | NA | SERVICE-AT SITE | LEASE | NA | LEFT SIDE EVAPORATOR MOTOR IS NOT WOLRING PROPERLY | REQUIRED SPARE | EVAPORATOR MOTOR SINGLE PHASE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL072 | Carrier - Thinline | Thinline |  |  |  | Used |  | RAMIZ
JUL073 | 2024-08-22 00:29 | vinit.mewada@crystalgroup.in | QWIK SUPPLY SILIGURI | CXRU1042578 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | ABNORMAL POWER SUPPLY AND SUPPLY SENSOR DEFECTIVE | REQUIRED SPARE | SUPPLY SENSORS - 2 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL073 | Daikin | LXE10E147F2 | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032 | RAMIZ
JUL074 | 2024-08-22 00:33 | vinit.mewada@crystalgroup.in | Qwik Supply | CXRU1045453 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | EXPANSION VALVE DEFECTIVE | REQUIRED SPARES | EXPENSION VALVE BODY , EXPENSION VALVE COIL |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL074 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ
JUL075 | 2024-08-27 01:22 | vinit.mewada@crystalgroup.in | DR. REDDY BIOTECHNOLOGY | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL075 | [7 empty] | VIRENDRA
JUL076 | 2024-08-27 01:23 | vinit.mewada@crystalgroup.in | SYMBIOTECH | NA | NA | NA | SERVICE-AT SITE | LEASE | NA | NA | NA | UMESH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL076 | [7 empty] | UMESH
AUG005 | 2024-08-29 22:06 | chaurasiagarima97@gmail.com | QWIK SUPPLY | NA | NA | NA | NA | NA | NA | NA | NEED TO COLLECT COMPRESSOR FROM NEW DELHI CARRIER TRANSPORT | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG005 | [7 empty] | SHAHBUDDIN
AUG018 | 2024-08-29 22:09 | chaurasiagarima97@gmail.com | QWIK SUPPLY | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR MAKING NOISE | need to switch off the unit | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG018 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | RAMIZ
AUG020 | 2024-08-29 22:12 | chaurasiagarima97@gmail.com | Samora Stud | TCIU1904607 | 20 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | UNIT NOT WORKING AND EVAPORATOR COIL LEAKAGE | REPLACE AND FIXED THE REEFER MAIN UIT ALIMMENTS. ALSO CHCKED GAS LEVEL. UNIT IS IN WORKING CONDIACTION | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG020 | [7 empty] | SHAHBUDDIN
AUG021 | 2024-08-29 22:14 | chaurasiagarima97@gmail.com | QWIK SUPPLY | CICU3876626 | 10 FT | TK - MP4000 | SERVICE-AT SITE | LEASE | NA | Temperature Issue | CHECKED COMPRESSOR AND CONTROLLER , RESOLVED THE ISSUE AND UNIT WORKING PROPERLY | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG021 | Thermoking | Magnum + | 21K2124JT | ABC782800322110152 | ABC782900322110202 | Brand New |  | RAMIZ
AUG026 | 2024-08-29 22:16 | chaurasiagarima97@gmail.com | QWIK SUPPLY | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR NOISY | NEED TO REPLACE COMPRESSOR AD GAS | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG026 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH
AUG030 | 2024-08-29 22:41 | chaurasiagarima97@gmail.com | Andabar | TRIU6616531 | 10 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | MINOR ISSUE | The client reported a minor issue, which the Clima's technician addressed at the client's request. Unit operating efficiently | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG030 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Used |  | VIRENDRA
AUG032 | 2024-08-29 22:48 | chaurasiagarima97@gmail.com | QWIK SUPPLY | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Compressor leakage | SPARES REQUIRED | COMPRESSOR WITH OIL, GASLET , R134A, N2, VACUMM |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG032 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH
AUG034 | 2024-08-29 22:52 | chaurasiagarima97@gmail.com | QWIK SUPPLY | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Compressor Issue | SHPARES REQUIRED | DPRV, LSV, EXPENSION VALVE, BYPASS VALVE, COMPRESSOR OIL, GAS,VACCUM, BEAZZING SET WITH N2 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG034 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH
AUG036 | 2024-08-29 22:55 | chaurasiagarima97@gmail.com | DR REDDY FTO 07 | TITU9930074 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Temperature Issue | Clean and restored the sensor port and unit is working normal | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG036 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | SHAHBUDDIN
AUG038 | 2024-08-29 23:02 | chaurasiagarima97@gmail.com | DR REDDY FTO 07 | PCIU6025808 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Condensor coil dirty | Condenser coil clean with fresh water. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG038 | Daikin | Daikin | A950890 | LXE10EA36B | NA | Used | JSGA622340507 | VIRENDRA
AUG039 | 2024-08-29 23:04 | chaurasiagarima97@gmail.com | DIVIS LAB | CON 1 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | container shown alarm DEL 70 | Need PM service and compressor defective | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG039 | [7 empty] | SHAHBUDDIN
AUG040 | 2024-08-29 23:08 | chaurasiagarima97@gmail.com | QWIK SUPPLY | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Temperature Issue | NEED TO SET VOLTAGE ISSUE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG040 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | MUKESH
AUG050 | 2024-08-31 02:13 | chaurasiagarima97@gmail.com | KRIOSKAR | NYKU7931452 | NA | NA | SERVICE-ON CALL | LEASE | NA | CONTAINER NOT WORKING | ERROR - AA22 SHOWING DUE TO R/S EVP MOTOR DEFECTIVE, NEED TO REPLACE | EVP MOTOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG050 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | VIRENDRA
AUG006 | 2024-09-06 02:09 | chaurasiagarima97@gmail.com | QWIK SUPPLY | TITU7263521 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR MAKING NOISE | REPLACED COMPRASSURE AND FILTER AND REFILL THE GAS, EXPENSION VALVE, VACUMME SYSTEM, | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG006 | Daikin |  |  |  |  | brand New | JSGA622180055 | SHAHBUDDIN
AUG019 | 2024-09-06 02:17 | chaurasiagarima97@gmail.com | Earl Corvus Habitat | APRU5091606 | 40 FT | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | NA | FLUCTUATIONS IN TEMEPRATURE | NEED TO REPLACE SYSTEM EVAPRATOR COIL, REFILL THE GAS R 134 A, N2, VACCUM PUMPS. | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG019 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | VIRENDRA | No
AUG020 | 2024-09-06 02:21 | chaurasiagarima97@gmail.com | Samora Stud | TCIU1904607 | 20 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | UNIT NOT WORKING AND EVAPORATOR COIL LEAKAGE | REPLACE AND FIXED THE REEFER MAIN UIT ALIMMENTS. ALSO CHCKED GAS LEVEL. UNIT IS IN WORKING CONDIACTION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG020 | [7 empty] | SHAHBUDDIN
AUG023 | 2024-09-06 02:31 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9469328 | 40 FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | DISPLAY ISSUE | NEED TO REPLACE THE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG023 | Carrier - Thinline | Elite line |  |  |  | Used |  | VIRENDRA
AUG024 | 2024-09-06 02:36 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9379498 | 40 FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | container controller defective, No gas in system, Solonerd Coil defected, Power Cable short | NEED SPARES | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG024 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH
AUG025 | 2024-09-06 02:41 | chaurasiagarima97@gmail.com | Cipla Unit 1 | CXRU1033787 | 40FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG025 | DAikin | LXE10E147F2 | M001107 | K31412141829 | DECOS 3F 2557 / 1 | used | JSGA622340249 | MUKESH
AUG027 | 2024-09-06 02:44 | chaurasiagarima97@gmail.com | QWIK SUPPLY | TCLU1130265 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | FOUND ICE ON EVAPROTOTER COIL ,EXSP. COIL SENSOR ANDREALY BOARD SUSPECTED. | WHILE PHYSICAL INSPECTION HE SUGGESTED NEED TO REPLACE THE SENSOR. UNIT WORKING WELL | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG027 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN
AUG028 | 2024-09-06 02:58 | chaurasiagarima97@gmail.com | Dr Reddy Biotechnology | TITU9930114 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | PM SERVICES AD INTERNAL INSPECTION | INSPECTION DONE AND RESOLVE THE ISSUE OF BLUESTAR UNIT 2 AFTER CLEANING CONDENSOR COIL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG028 | Thermoking | MP-4000 | 14E219055 | EOG1000667 |  |  | JSGA622180063 ¦ JSGA622180011 | SHAHBUDDIN
AUG029 | 2024-09-06 03:03 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9379498 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | CONTAINER NOT WORKING | NEED SPARES | Daikin Keypad, Daikin Display, Liquid Filter, Refrigerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG029 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH
AUG031 | 2024-09-06 03:08 | chaurasiagarima97@gmail.com | SHIVAMRUT | TITU9930074 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | SUPPLY SENSOR GOT STUCK AND POCKET SUPPY SENSOR DEFECTIVE | NEED SPARES | Daikin EVP inlet sensor, Daikin Suction Gas Sensor |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG031 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | RAMIZ
AUG033 | 2024-09-06 03:11 | chaurasiagarima97@gmail.com | Chemplast Sanmar Limited | TITU9930222 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | Compressor Defective | SPARES REQUIRED | Daikin Inlet Sensor, Liquid Filter, Daikin Return Temperature Sensor, Refrigerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG033 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | RAMIZ
AUG035 | 2024-09-06 03:15 | chaurasiagarima97@gmail.com | Qwik Supply | PCIU6015055 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | NEED COMPRESSURE , FILTER, GAS KET , GAS - N32 , R134A AND VACCUM PUMP | SPARES REQUIRED | Daikin Inlet Sensor, Refirgerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG035 | Daikin | Daikin | NA | NA | NA | used |  | SHAHBUDDIN
AUG037 | 2024-09-06 03:18 | chaurasiagarima97@gmail.com | Dr Reddy CTO 6 | KKFU6712802 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | FLUCTUATIONS IN TEMEPRATURE | NEED FUSE | Carrier Keypad, USB RS232 ADAPTOR WITH CASE & SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG037 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | SHAHBUDDIN
AUG038 | 2024-09-06 03:21 | chaurasiagarima97@gmail.com | Dr Reddy FTO-7 | PCIU6025808 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Condensor coil dirty | Condensor coil clean with fresh water. | TK-4000 Display, USB RS232 ADAPTOR WITH CASE & SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG038 | Daikin | Daikin | A950890 | LXE10EA36B | NA | Used | JSGA622340507 | VIRENDRA
AUG041 | 2024-09-06 03:44 | chaurasiagarima97@gmail.com | Laurus Unit 3 | APRU5091340 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | COMPRESSOR DEFECTIVE | NEED TO REPLACED COMPRESSOR | USB RS232 ADAPTOR WITH CASE & SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG041 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA
AUG042 | 2024-09-06 03:48 | chaurasiagarima97@gmail.com | Cipla Unit 1 | TITU9230980 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | KEYPAD NOT WORKING | NEED SPARES | Refirgerant Gas - R134a, Brazing Set, Liquid Filter, GAUGE MANIFOLD & ADAPTOR, Daikin Inlet Sensor, Daikin Compressor Contactor 30A (PCC1-PCC2) |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG042 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | MUKESH
AUG043 | 2024-09-06 03:51 | chaurasiagarima97@gmail.com | North West logistic | MYRU4505847 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | ERROR FOUND AL E401, IN SUPPY SENSOR , HPT SESOR , SHEET KEY AND GAS REPLACEMENT | RETURN BACK TO US AFTER WARD WE WORK ON IT. | TK-4000 COMPRESSOR CONTACTOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG043 | Daikin | Daikin |  |  |  | Used |  | MUKESH
AUG044 | 2024-09-06 03:56 | chaurasiagarima97@gmail.com | North West logistic | TITU9928040 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | KEYPAD DEFECTIVE | RETURN BACK TO US AFTER WARD WE WORK ON IT. | Daikin Reefer Unit, Packing, Transport |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG044 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | MUKESH
AUG045 | 2024-09-06 03:58 | chaurasiagarima97@gmail.com | North West logistic | MYRU4513729 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | ERROR FOUND AL E401, IN SUPPY SENSOR , HPT SESOR , SHEET KEY AND GAS REPLACEMENT | NEED TO REFILL Refirgerant Gas - R134a | Refirgerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG045 | Daikin | Daikin |  |  |  | Refurbished |  | MUKESH
AUG046 | 2024-09-06 04:00 | chaurasiagarima97@gmail.com | North West logistic | MYRU4515188 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | PM SERVICES | NEED SPARES | Refirgerant Gas - R134a, MAK Process Oil - RL32H - Emkarte |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG046 | Daikin | Daikin |  |  |  | Used |  | MUKESH
AUG047 | 2024-09-06 04:04 | chaurasiagarima97@gmail.com | Cipla Unit 1 | TITU9231009 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | DISPLAY ISSUE | Spare Required | Display, Keypad, Carrier Thinline Ambient Sensor, Carrier Supply Sensor, Carrier Compressor Contactor 30A, Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG047 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | MUKESH
AUG048 | 2024-09-06 04:07 | chaurasiagarima97@gmail.com | Cipla Unit 1 | CXRU1033344 | NA | DAIKIN | SERVICE-AT SITE | LEASE | NA | SUPPLY TEMP SENSOR DEFECTED | NEED TO REPLACE TEMP SUPPLY SENSOR | Daikin Display, Liquid Filter, LED Light 20W, Curtain set for 40ft [Model - Frigus], L&T MCB 16 AMP X 2P, Polycab Flexible Cable 1.5 sq mm X 2 Core, Insulation Tape, RIVIT, CABLE TIE, 12INCH BLACK, RIVIT GUN, Drill Machine, CASING PATTI 1 INCH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG048 | DAikin | LXE10E147F2 | M001118 | K31411114078 | DECOS 3F 2609 / 1 | Used | JSGA622340264 | MUKESH
AUG049 | 2024-09-06 04:10 | chaurasiagarima97@gmail.com | Divis Lab | CONT-3 | NA | NA | SERVICE-AT SITE | LEASE | NA | COMPRESSOR TRIPPED | NEED TO REPLACE COMPRESSOR AND FILTER, NET BOLT | Carrier Supply Sensor |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG049 | [7 empty] | SHAHBUDDIN
AUG051 | 2024-09-06 04:16 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | CRLU6220410 | 40FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | NEED TO REPLACE BOTH DOOR GASLET | NEED TO REPLACE BOTH DOOR GASLET | Carrier Supply Sensor, Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG051 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA622170434 | VIRENDRA
AUG052 | 2024-09-06 04:19 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | MYRU4500552 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | NEED TO REPLACE SUPPLY SENSOR , ABINENT SESOR, CONDENSOR SENSOR,EVP SENSOR | Spare Required | Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG052 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | VIRENDRA
AUG053 | 2024-09-06 04:22 | chaurasiagarima97@gmail.com | DSV | TITU9930006 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | DIX40 TK MP4000 FOR INSTATTION , INTERNAL LIGHT NOT WORKING AND NEED TO INSTALL EXTERNAL LIGHTS | SPARES REQUIRED | Daikin HSV-DSV-BSV Solenoid Valve, MAK Process Oil - RL32H - Emkarte, Compressor Gasket - Suction & Discharge, Liquid Filter, Daikin Compressor Contactor 30A (PCC1-PCC2) Refirgerant Gas - R134a, Nitrogen, Oxygen, Brazing Set, Brazing Rod, Daikin Inlet Sensor, Daikin Return Temperature Sensor, Vaccume Pump |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG053 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | SHAHBUDDIN
AUG054 | 2024-09-06 04:26 | chaurasiagarima97@gmail.com | DSV | SJKU4000104 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | DIX40 TK MP4000 FOR INSTATTION, | AC INSTATTALLATION DONE WORKING WELL | Daikin LSV Coil, Daikin HSV-DSV-BSV Solenoid Valve, Daikin Expansion Valve, Daikin Compressor, Compressor Gasket - Suction & Discharge, Refirgerant Gas - R134a, Nitrogen Oxygen, Brazing Set, Brazing Rod, Vacuum Pump |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG054 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN
SEP001 | 2024-09-06 04:29 | chaurasiagarima97@gmail.com | Qwik Supply | CGHU2988654 | 20 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | WATER ENTERED IN ELECTRICAL PANEL, ENTERNAL LIGHT DAAMAGED , EVAPROTER MOTOR NOISY, MAIN POWER CABLE DAAMAGED WITH POWER PLUGIN , | DUE TO HEAVY RAIN NOT ABLE TO DO TEST. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP001 | [7 empty] | NA | No
SEP002 | 2024-09-06 04:31 | chaurasiagarima97@gmail.com | Qwik Supply | CGHU2989060 | 20 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | UNIT UNABLE TO RUN DUE TO HEAVY RAINFALL.INTERNAL LIGHT DAMAGED,MAIN POWER PLUGIN AND CABLE IS DAMAGED AND RUSTY, | DUE TO HEAVY RAIN NOT ABLEE TO DO TEST. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP002 | [7 empty] | NA | No
SEP003 | 2024-09-06 04:32 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | MYRU4517508 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Need replace Daikin keypad, display & display cover, CPU guard cover, internal cleaning,, lights , need togaslet fixed kick plate / baffle plates is damaged, door , PTI failed | SPARES REQUIRED | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP003 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | SHAHBUDDIN | No
SEP004 | 2024-09-06 04:34 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | CGMU2990461 | 20 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | PM services / Inspection / PTI | PM service done, convertor coil clean, Air pressure, sensor reading, gas level , Oil test, leakage test done. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP004 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | SHAHBUDDIN | No
SEP005 | 2024-10-02 23:25 | operation@crystalgroup.in | Shivamrut | CXRU1030854 | NA | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | LEAK IN CONTAINER | CUSTOMER WILL ARRANGE CONSUMABLES | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP005 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | Mukesh
SEP006 | 2024-10-02 23:28 | operation@crystalgroup.in | Dr Reddy CTO5 | GSOU6384153 | NA | NA | SERVICE-AT SITE | LEASE | FOC | EVP MOTOR NOISY | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP006 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN | Yes
SEP007 | 2024-10-02 23:30 | operation@crystalgroup.in | Dr Reddy CTO5 | CXRU1045896 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP007 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | SHAHBUDDIN | Yes
SEP008 | 2024-10-02 23:33 | operation@crystalgroup.in | Dr Reddy CTO5 | Dr Reddy CTO5 | GSOU6384240 | NA | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP008 | [7 empty] | SHAHBUDDIN | Yes
SEP009 | 2024-10-02 23:35 | operation@crystalgroup.in | Dr Reddy CTO5 | CXRU1032564 | CXRU1032564 | NA | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP009 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN | Yes
SEP010 | 2024-10-02 23:38 | operation@crystalgroup.in | DSV | SJKU4000104 | NA | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | POWER MODULE DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP010 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN | Yes
SEP011 | 2024-10-02 23:49 | operation@crystalgroup.in | Dr Reddy FTO-7 | CXRU1033616 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | INLET SENSOR DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP011 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | VIRENDRA | Yes
SEP012 | 2024-10-02 23:50 | operation@crystalgroup.in | Dr Reddy FTO-7 | KKFU6712802 | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | MOTOR NOISY | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP012 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | VIRENDRA | Yes
SEP013 | 2024-10-02 23:52 | operation@crystalgroup.in | Dr Reddy FTO-7 | TRIU6632949 | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | KING VALVE, KEYPAD & LEAK FOUND | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP013 | Carrier - Thinline | Thinline | 1808L295 | MS60317785 |  | Used |  | VIRENDRA | Yes
SEP014 | 2024-10-02 23:54 | operation@crystalgroup.in | Dr Reddy FTO-7 | TITU9930074 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMP CONTACTOR REQ | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP014 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes
SEP015 | 2024-10-02 23:57 | operation@crystalgroup.in | Tan90 | CICU3876523 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | NOT ACHEIVING TEMP | REARRANGE THE CARGO AND DEFROST SETTING CHANGE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No
SEP016 | 2024-10-03 00:01 | operation@crystalgroup.in | Gennova Biopharma | CICU1938565 | 20-REEFER | TK-MP4000 | SERVICE-ON CALL | SALE | FOC | WORKING WELL | ITS A SUPERFREEZER MACHINE HAVING 2 COMPRESSORES AND ITS QUIT LOUD IN NATURE COMPAIR TO OTHER SINGLE COMPRESSOR UNITS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP016 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | NA | No
SEP017 | 2024-10-03 00:02 | operation@crystalgroup.in | Crystal Yard-JNPT | CGMU2989060 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | STOCK | FOC | CABLE, PLUG, DISPLAY, KEYPAD, CONTACTOR REQUIRED | NEED PARTS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP017 | Carrier - Thinline | Thinline | LSM 60197754 | LSM60197754 |  |  | JSGA622180043 | NA | No
SEP018 | 2024-10-03 00:04 | operation@crystalgroup.in | Siemens | PRGU4958724 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | SALE | FOC | VOLTAGE ERROR | VOLTAGE GET CORRECTED FROM CLIENT AND WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP018 | Carrier - Thinline |  |  |  |  | Used |  | SHAHBUDDIN | No
SEP019 | 2024-10-03 00:06 | operation@crystalgroup.in | Qwik Supply | CGMU2988654 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | CONTAINER INSPECTION FOR OFF LEASING THE SAME | INSPECTION DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP019 | Carrier - Thinline | Thinline | 2907L50458 | LSM60197481 |  | Used |  | NA | Yes
SEP020 | 2024-10-03 00:08 | operation@crystalgroup.in | Divis Lab | CONT-3 | NA | CARRIER-THINLINE | SERVICE-AT SITE | SALE | FOC | LEAK IN TERMINAL BOX BECAUSE TERMINALS ARE TRIPPED WHILE TIGHTNING | NEED TO REPLACED TERMINAL | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP020 | [7 empty] | VIRENDRA | Yes
SEP021 | 2024-10-03 00:19 | operation@crystalgroup.in | DSV | TITU9930006 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | LED LIGHT NOT WORKING | CHANGED IN WIRING | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP021 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | VIRENDRA | Yes
SEP022 | 2024-10-03 00:21 | operation@crystalgroup.in | Qwik Supply | BMOU9782197 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EXPANSION VALVE AND COIL, LIQUID VALVE, BY PASS VALVE AND GAS REQ | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP022 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | NA | No
SEP023 | 2024-10-03 00:32 | operation@crystalgroup.in | Dr Reddy Biotechnology | TITU9930114 | NA | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | WORKING WELL | WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP023 | Thermoking | MP-4000 | 14E219055 | EOG1000667 |  |  | JSGA622180063 ¦ JSGA622180011 | VIRENDRA | Yes
SEP024 | 2024-10-03 00:33 | operation@crystalgroup.in | Dr Reddy Biotechnology | TITU9930074 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | SENSOR CONNECTION LOOSE | FIX PROPERLY AND WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP024 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes
SEP025 | 2024-10-03 00:35 | operation@crystalgroup.in | Chemplast Sanmar Limited | TITU9930222 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | NEED TO REPLACED COMPRESSOR | COMPRESSOR REPLACED BUT KEYPAD REQUIRED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP025 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | VIRENDRA | Yes
SEP026 | 2024-10-03 00:36 | operation@crystalgroup.in | ITC Ltd | PCIU6010243 | 40-REEFER | TK-MP3000 | SERVICE-AT SITE | LEASE | FOC | SETTINGS NOT PROPER | WORKING WELL CHANGED IN SETTING, BODY VALVE SUSPECTED MAY BE NEED TO CHANGE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP026 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | VIRENDRA | Yes
SEP027 | 2024-10-03 00:38 | operation@crystalgroup.in | Qwik Supply | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | FOUND VOLTAGE FLUCTUATION | GET CORRECTED FROM CLINET AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP027 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | SHAHBUDDIN | No
SEP028 | 2024-10-03 00:39 | operation@crystalgroup.in | Hetero Biopharma | CXRU1030387 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | MOTOR NOISY | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP028 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | SHAHBUDDIN | No
SEP029 | 2024-10-03 00:41 | operation@crystalgroup.in | Laurus Unit 3 | ARCU4530675 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | FUSE & HARNESS CABLE NOT CONNECTED WELL | FIX IT PRPERLY AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP029 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used |  | SHAHBUDDIN | No
SEP030 | 2024-10-03 00:43 | operation@crystalgroup.in | PI Industry | CXRU1035856 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | CONTACTOR & SENSOR DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP030 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used |  | NA | No
SEP031 | 2024-10-03 00:44 | operation@crystalgroup.in | Cipla Unit 3 | TITU9231009 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | COIL DIRTY, KEYPAD DEFECTIVE | KEYPAD CHANGED, CLEAN COIL & CHECKED PARAMAETERS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP031 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | NA | Yes
SEP032 | 2024-10-03 00:46 | operation@crystalgroup.in | Cipla Unit 3 | TITU9230980 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DISPLAY DEFECTIVE, AND GAS FOUND SHORT | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP032 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | NA | Yes
SEP033 | 2024-10-03 00:47 | operation@crystalgroup.in | UPS | SJKU4000110 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | INSTALLATION | DONE AND GIVEN TRAINIG | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP033 | Thermoking | MP-4000 |  |  |  | Brand New |  | SHAHBUDDIN | Yes
SEP034 | 2024-10-03 00:50 | operation@crystalgroup.in | Gennova Biopharma | CICU1937152 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | SALE | FOC | SET TEMP IS +5 & CONTAINER TEMP GOES TILL -13 | NEED TO UPGRADE SOFTWARE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP034 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New
SEP035 | 2024-10-03 00:51 | operation@crystalgroup.in | Hetero Plasma | CXRU1030387 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | MOTOR NOISY | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP035 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used
SEP036 | 2024-10-03 00:55 | operation@crystalgroup.in | Reliance Industries | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | GAS LEAK | NEED TO ATTEND PHYSICALLY | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP036 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289
SEP037 | 2024-10-03 00:56 | operation@crystalgroup.in | Crystal Yard-JNPT | HDMU5220720 | 40-REEFER | DAIKIN | SERVICE-AT SITE | STOCK | FOC | CONTACTOR DEFECTIVE | PCC1-PCC2 CONTACTOR CHANGED PTI PASS WORKING WELL | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP037 | Carrier Thineline |  |  |  |  | USed
SEP038 | 2024-10-03 00:58 | operation@crystalgroup.in | UPS | HDMU5221979 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | INSTALLATION | DONE AND GIVEN TRAINIG | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP038 | Daikin |  |  |  |  | USed
SEP039 | 2024-10-03 01:01 | operation@crystalgroup.in | Lupin Limited | CCLU1036859 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | MOTOR NOISY, NEED TO REPLACED | MOTOR REPLACED AND WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP039 | Carrier |  |  |  |  | Used | JSGA623040314
SEP040 | 2024-10-03 01:02 | operation@crystalgroup.in | Celon | TRIU6616871 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DISPLAY & SUPPLY SENSOR REQUIRED | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP040 | Carrier - Thinline | Thinline |  |  |  | Used
SEP041 | 2024-10-03 01:03 | operation@crystalgroup.in | Aurobindo Unit-4 | NA | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DISPLAY & DRAIN PIPE REQ | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP041
SEP042 | 2024-10-03 01:05 | operation@crystalgroup.in | Laurus Unit 4 | ARCU4530675 | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | GAS CONTAMINATED | NEED GAS TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP042 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used
SEP043 | 2024-10-03 01:07 | operation@crystalgroup.in | DSV | SJKU4000104 | NA | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | POWER MODULE DEFECTIVE | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP043 | Thermoking | MP-4000 |  |  |  | Refurbished
SEP044 | 2024-10-03 01:08 | operation@crystalgroup.in | Bharat Petroleum | CXRU1043337 | 40-REEFER | TK-MP4000 | SERVICE-ON CALL | LEASE | FOC | GAS LEAK | NEED PHYSICAL VISIT | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP044 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used
SEP046 | 2024-10-03 01:09 | operation@crystalgroup.in | Divis Lab | CONT-3 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | TERMINAL LEAK | NEED TO CHANGE TERMINAL | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP046
SEP047 | 2024-10-03 01:11 | operation@crystalgroup.in | Aspiro Pharma | CGMU2991560 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | UNIT 1 -EVP MOTOR & UNIT 2 - CONTROLLER DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP047 | Carrier - Thinline | Thinline |  |  |  | Used
SEP048 | 2024-10-03 01:12 | operation@crystalgroup.in | Qwik Supply | CXRU1042578 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | SUPPLY SENSOR REQ AND FILTER NEED TO CHANGE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP048 | Daikin | LXE10E147F2 | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032
SEP049 | 2024-10-03 01:14 | operation@crystalgroup.in | Qwik Supply | MYRU4500552 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | SUPPLY & RETURN SENSOR FAIL | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP049 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used
SEP050 | 2024-10-03 01:15 | operation@crystalgroup.in | Qwik Supply | TITU7263521 | 10-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR DEFECTIVE | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP050 | Daikin |  |  |  |  | brand New | JSGA622180055
SEP051 | 2024-10-03 01:59 | operation@crystalgroup.in | Qwik Supply | CICU1442240 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR DEFECTIVE | COMPRESSOR REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP051 | Thermoking | MP-4000 |  |  |  | Brand New
SEP052 | 2024-10-03 02:01 | operation@crystalgroup.in | Divis Lab | CONT-3 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | TERMINAL LEAK | TERMINAL REPLACED NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP052
SEP053 | 2024-10-03 02:03 | operation@crystalgroup.in | Qwik Supply | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | leak in condenser coil | NEED VISIT | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP053 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289
SEP054 | 2024-10-03 02:05 | operation@crystalgroup.in | Qwik Supply | CICU2779920 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP054 | Thermoking | Magnum Plus | E0GM030270 | ABC782800322010477 |  | BrandNew
SEP055 | 2024-10-03 02:06 | operation@crystalgroup.in | Softbox Systems | GRMU3707470 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Exv valve and body, Inlet sensor 1 & Temp sensor 2 required | required spares | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP055 | Daikin |  |  |  |  | used
SEP056 | 2024-10-03 02:07 | operation@crystalgroup.in | Softbox Systems | TITU8257288 | 20-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP056 | Thermoking | Thermoking MP4000 |  |  |  | Used
SEP057 | 2024-10-03 02:08 | operation@crystalgroup.in | Qwik Supply | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | LEAK IN DISCHARGE LINE | RESOLVED AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP057 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | RAMIZ | No
SEP058 | 2024-10-03 02:10 | operation@crystalgroup.in | Qwik Supply | MYRU4501435 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP058 | Daikin | Daikin |  | LXE10E136A |  | Refurbished
SEP059 | 2024-10-03 02:32 | operation@crystalgroup.in | Hetero Unit 5 | SUDU6218004 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | PM SERVICE AND GENRAL INSPECTION | SHORT PTI | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP059 | Carrier-Primeline | Primeline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished
SEP060 | 2024-10-03 02:35 | operation@crystalgroup.in | Hetero Unit 5 | CXRU1186425 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM SERVICE AND GENRAL INSPECTION | SHORT PTI | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP060 | DAikin | LXE10E136F2 | M002116 | K31511151600 | DECOS 3F 2557 / 1 | Used | JSGA621320194
SEP061 | 2024-10-03 02:36 | operation@crystalgroup.in | Hetero Unit 5 | CXRU1030746 | 40-REEFER | NA | SERVICE-AT SITE | LEASE | FOC | PM SERVICE AND GENRAL INSPECTION | SHORT PTI | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP061 | DAikin | LXE10E147F2 | M001536 | K31405122693 | DECOS 3F 2609 / 1 | Used
SEP062 | 2024-10-03 02:37 | operation@crystalgroup.in | Hetero Unit 5 | CXRU1186467 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM SERVICE AND GENRAL INSPECTION | SHORT PTI | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP062 | Daikin | LXE10E136F2 | M002118 | K31503145677 | DECOS 3F 2557 / 12 | Used | JSGA622180060
SEP063 | 2024-10-03 02:39 | operation@crystalgroup.in | Laurus Unit 3 | APRU5091340 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR DEFECTIVE | COMPRESSOR REPLACED BUT 1 MOTOR IS MISSING AND 1 IS NOISY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP063 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used
SEP064 | 2024-10-03 02:40 | operation@crystalgroup.in | Laurus Unit 3 | DFOU6120384 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | KEYPAD DEFECTIVE | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP064 | Daikin | Daikin | MOO4338 |  |  | Used
SEP065 | 2024-10-03 02:41 | operation@crystalgroup.in | Laurus Unit 3 | BMOU9784137 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | KEYPAD, OUTLET, SUPPLY & RETURN SENSOR REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP065 | Daikin |  |  |  |  | used
SEP066 | 2024-10-03 02:43 | operation@crystalgroup.in | Laurus Unit 3 | MYRU4519115 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | LP SWITCH, RETURN, AMBIENT & SUPPLY SENSOR REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP066 | Daikin | Daikin | 806162 | LXE10E136A2 |  | Refurbished
SEP067 | 2024-10-03 02:44 | operation@crystalgroup.in | Laurus Unit 3 | KKFU6710760 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | FILTER & SUPPLY SENSOR REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP067 | Carrier - Eliteline | Thinline |  | LSX60253959 | 5167 | Used
SEP068 | 2024-10-03 02:45 | operation@crystalgroup.in | Zenfold Sustainable | TRIU6618637 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DISPLAY & OIL REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP068 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040284
SEP069 | 2024-10-03 02:49 | operation@crystalgroup.in | Qwik Supply | TCLU1130265 | 40-REEFER | TK-MP3000 | SERVICE-AT SITE | LEASE | FOC | EVP, RETURN & SUPPLY SENSOR DEFECTIVE | EVP & RETURN REPLACED BUT SUPPLY NEED TO CHANGE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP069 | Thermoking | MP-4000 |  |  |  | Refurbished
SEP070 | 2024-10-03 02:50 | operation@crystalgroup.in | Softbox Systems | GRMU3707470 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EVP COIL SETTING NOT PROPER | CHANGE THE SETTING AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP070 | Daikin |  |  |  |  | used
SEP071 | 2024-10-03 03:12 | operation@crystalgroup.in | Navin Fluorine | CCLU1031878 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | EVP & CONDENSER MOTOR NOISY | EVP MOTOR CHANGED BUT CONDENSER MOTOR REQ | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP071 | Carrier - Thinline | Thinline |  |  |  | Used
SEP072 | 2024-10-03 03:14 | operation@crystalgroup.in | PI Industry | MYRU4502299 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CONTACTOR & DISPLAY DEFECTIVE | CONTACTOR REPLACED BUT DISPLAY REQ | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP072 | Daikin | Daikin | NOT AVAILABLE | LYE10E136A2 | NOT AVAILABLE | Refurbished
SEP073 | 2024-10-03 03:15 | operation@crystalgroup.in | Arkray Healthcare | APRU5066497 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | NA | ONLY BODY INSPECTION DONE MACHINE IS DISCONNECTED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP073 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040296
SEP074 | 2024-10-03 03:16 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EVP COIL LEAK | NEED TO REPLACED EVP COIL | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP074 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used
SEP075 | 2024-10-03 03:17 | operation@crystalgroup.in | Hetero - 3 | CXRU1030387 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP075 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used
SEP076 | 2024-10-03 03:18 | operation@crystalgroup.in | Reliance Industries | CXRU1042578 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | FILTER & SUPPLY, INLET SENSOR REQ | FILTER REPLACED BUT SENSORES REQ | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP076 | Daikin | LXE10E147F2 | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032
SEP077 | 2024-10-03 03:20 | operation@crystalgroup.in | Reliance Industries | MWCU6776506 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | GAS TOP UP REQ AND SUPPLY SENSOR REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP077 | Carrier - Thinline | Thinline |  |  |  |  | JSGA622180072
SEP078 | 2024-10-03 03:21 | operation@crystalgroup.in | Hetero - 3 | CXRU1030427 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | SHEET PANEL & KEYPAD REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP078 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186
SEP079 | 2024-10-03 03:22 | operation@crystalgroup.in | Hetero - 3 | APRU5091041 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DEFROST SENSOR REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP079 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287
SEP080 | 2024-10-03 03:24 | operation@crystalgroup.in | Hetero - 3 | PCIU6016370 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP080 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188
SEP081 | 2024-10-03 03:25 | operation@crystalgroup.in | Hetero - 3 | CXRU1026520 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | SHEET PANEL REQ | NEED PARTS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP081 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278
SEP082 | 2024-10-03 03:26 | operation@crystalgroup.in | Gennova Biopharma | CICU1938565 | 20-REEFER | TK-MP4000 | SERVICE-AT SITE | SALE | CHARGEABLE | NORMAL EXTRA NOISE IN COMPRESSOR | SALE UNIT NEED TO CALL TK-MECHANIC | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP082 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New
OCT001 | 2024-10-04 00:44 | operation@crystalgroup.in | CRYSTAL | TITU9928040 | 40-REEFER | THERMOKING MP4000 | REPAIR | STOCK | FOC | POWER MODULE FAIL | NEED TO CHANGE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT001 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | VIRENDRA
OCT002 | 2024-10-04 01:03 | operation@crystalgroup.in | HETERO | APRU5091041 | 40-REEFER | NA | PREVENTIVE MAINTENANCE | LEASE | FOC | AL60 DEFROST SENSOR | DEFROST SENSOR REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT002 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | MUKESH
OCT003 | 2024-10-04 02:01 | operation@crystalgroup.in | HETERO | PCIU6016370 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CONTROLLER D/F | CONTROLLER REPLACE AND CONTAINER RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT003 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | MUKESH
OCT004 | 2024-10-04 02:11 | operation@crystalgroup.in | HETERO | CXRU1030427 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | ALE607 KEYPAD/SHEET KET D/F | SHEET KEY AND DISPLAY COVER REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT004 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | MUKESH
OCT005 | 2024-10-04 02:20 | operation@crystalgroup.in | HETERO | CXRU1026520 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED AND FOUNF CONTAINER | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT005 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | MUKESH
OCT006 | 2024-10-04 02:27 | operation@crystalgroup.in | CIPLA | TITU9230980 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | REFILL R-134a 1800g | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT006 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | VIRENDRA
OCT007 | 2024-10-04 04:49 | operation@crystalgroup.in | TIPTOP PLAZA | SITE INSPECTION | NA | NA | NA | NA | NA | THERE IS NO SUFFICIENT SPACE FOR TRAILER AND HYDRA SO DISCUSSED WITH PRASHANT SIR SAME | THE CONTAINER IN BASEMENT IS FULLY SECURE AND CLEANED AREA NO ISSUE FOR CONDENSATION , NEED TOMAKE SURE WHILE UNLOADING OF CONTAINER SINCE THE SPACE OF TOP IS LESS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT007 | [7 empty] | UMESH
OCT008 | 2024-10-04 05:13 | operation@crystalgroup.in | Shri. SWAMI NARAYAN TEMPLE | TCTU1911479 | 20-REFEER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION | NEED WASH ONLY RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT008 | [7 empty] | UMESH
OCT010 | 2024-10-05 00:02 | operation@crystalgroup.in | SOFTBOX PVT LTD | GRMU3703470 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | PM DONE AND SHORT PTI PASS CONTAINER IS RUNNING GOOD IOT INSTALLED | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT010 | [7 empty] | MUKESH
OCT012 | 2024-10-06 22:13 | operation@crystalgroup.in | JUBILANT | TRIU6687350 | 20-REFEER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONDENSOR COIL VERY DIRTY SO CLEANEDD IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENT ALL WORKING GOOD TEMPERATURE COOLING -25 IN RANGE | container running good need to clean condenser coil every 10 days | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT012 | Carrier |  |  |  |  | USed |  | UMESH
OCT013 | 2024-10-06 22:22 | operation@crystalgroup.in | JUBILANT | GRMU3607418 | 20-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED & FOUND CONTAINER BREAKDOWN DUE TO HEAVVY SOUND IN COMPRESSOR SO CHECKED & FOUND EV COIL NOT OPEN PROPERLY | SO FIX THE EV COIL AND CONTAINER RUNNING OK | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT013 | Daikin |  |  |  |  | Used |  | VIRENDRA | Yes
OCT014 | 2024-10-06 22:25 | operation@crystalgroup.in | GMR AIR CARGO | MYRU4517508 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING GOOD , DISPLAY FADED | PM , SHORT PTI PASS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT014 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | MUKESH
OCT015 | 2024-10-06 22:29 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND NO GAS IN SYSTEM HPT AND LPT GOES TO MINUS AND EXPENSION OPEN 100% | WE HAVE REFILL R-134a 5kg NOW CONTAINER RUNNING IN RANGE TEMP PRESENT TEMP +14.2 C AND SENSOR VALVE Ab 30.6C ,EI 12.1C ,EO 13.2C, dC 87.0C , SGS 22.9C, SMV 21%, EV 47% | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT015 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | VIRENDRA
OCT015 ( DAY 2) | 2024-10-06 22:32 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WE HAV FOUND CONTAINER WORKING SOUND CONDITION WITHOUT ANY ALARM EV 53% , SMV 14%, DC 85C PRESENT TEMP +15 C | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT015%20(%20DAY%202) | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used
OCT016 | 2024-10-06 22:37 | operation@crystalgroup.in | GMR AIR CARGO | CGMU2990462 | 20-REFEER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKD AND FOUND DEFROST SENSOR DEFECTIVE NEED TO REPLACE | PM DONE AND SHORT PTI FAIL PS CONTAINER RUNNING GOOD CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT016 | [7 empty] | SHAHBUDDIN | No
OCT009 | 2024-10-07 05:02 | operation@crystalgroup.in | SYMBIOTEC | CRIU6617292 | 20-REFEER | CARRIER | SERVICE-ON CALL | SALE | FOC | ALARM 22 EVAPORATOR MOTOR 1PH , ALARM 72 LESS GASS | NEED TO LEAK TEST, AND REPLACE MOTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT009 | [7 empty] | SHAHBUDDIN | No
OCT011 | 2024-10-07 05:43 | operation@crystalgroup.in | PARLE | CXRU1186404 | 40-REFEER | DAIKIN | SERVICE-ON CALL | SALE | FOC | COMPRESSOR NOISY | NEED TO REPLACE COMPRESSOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT011 | DAikin | LXE10E136F2 | M002106 | K11910045666 | DECOS 3F 2551 / 1 | used |  | UMESH
OCT018 | 2024-10-09 03:14 | operation@crystalgroup.in | RELIANCE | CICU2094089 | 10-REFEER | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND COMPRESSOR CONTACTOR BURN AND TRANSFORMER NOISY. COMPRESSOR CREATE NOISE ALARM BUZER NOT CREATE SOUND | WE HAVE REPLACE CONTACTOR BUT NOT SUPPORTED NEED CONTACTOR 1NOS PRESENT CONTAINER RUN IN BURN CONTACTOR SO NEED CONTACTOR ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT018 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 |  | BrandNew |  | VIRENDRA
OCT020 | 2024-10-14 10:42 | operation@crystalgroup.in | AAK LIMITED | SJKU4000038 | 40-REFEER | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT020 | Carrier-Primeline | Primeline |  |  |  |  | JSGA623040167 | VIRENDRA
OCT021 | 2024-10-14 10:52 | operation@crystalgroup.in | AAK LIMITED | CICU8118070 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT021 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA
OCT022 | 2024-10-14 11:01 | operation@crystalgroup.in | AAK LIMITED | CICU8118130 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT022 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA
OCT023 | 2024-10-14 11:07 | operation@crystalgroup.in | AAK LIMITED | CICU8118167 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT023 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA
OCT024 | 2024-10-14 11:18 | operation@crystalgroup.in | RELIANCE | CXRU1040322 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT024 | [7 empty] | UMESH
OCT025 | 2024-10-14 12:12 | operation@crystalgroup.in | RELIANCE | CXRU1043912 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT025 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH
OCT026 | 2024-10-14 12:24 | operation@crystalgroup.in | RELIANCE | TITU7263521 | 10-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | BREAKDOWN | NEED TO REPLACE ALL VALVE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT026 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH
OCT027 | 2024-10-14 12:39 | operation@crystalgroup.in | RELIANCE | TCLU1130265 | 40-REFEER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT027 | Thermoking | MP-4000 |  |  |  | Refurbished |  | UMESH
OCT028 | 2024-10-14 12:48 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-REFEER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | EVP SENSOR NOT WORKING PROPERLY DUE TO ICE FORMATION INSIDE THE CONTAINER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT028 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH
OCT029 | 2024-10-14 12:56 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT029 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | UMESH
OCT030 | 2024-10-14 16:51 | operation@crystalgroup.in | SWADESH MILK | GESU9290991 | 40-REFEER | NA | INSTALLATION | SALE | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT030 | Carrier | Thineline |  |  |  | Used |  | UMESH
OCT031 | 2024-10-14 16:55 | operation@crystalgroup.in | SWADESH MILK | NYKU7932356 | 40-REFEER | NA | INSTALLATION | SALE | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT031 | Carrier | Thineline |  |  |  | Used |  | UMESH
OCT032 | 2024-10-15 13:24 | operation@crystalgroup.in | CRYSTAL YARD | MYRU4505847 | 40-REEFER | DAIKIN | REPAIR | STOCK | FOC | REQUIRED THESE PART FOR THIS CONTAINER | SPARE REQUEST | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT032 | Daikin | Daikin |  |  |  | Used |  | VIRENDRA
OCT033 | 2024-10-15 13:26 | operation@crystalgroup.in | CRYSTAL YARD | MYRU4513729 | 40-REEFER | DAIKIN | REPAIR | STOCK | FOC | REQUIED THESE PART FOR THIS CONTAINER | REQUEST FOR SPARE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT033 | Daikin | Daikin |  |  |  | Refurbished |  | VIRENDRA
OCT034 | 2024-10-16 11:06 | operation@crystalgroup.in | AMUL | CXRU1056669 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION | SHORT PTI PASS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT034 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | MUKESH
OCT035 | 2024-10-16 11:08 | operation@crystalgroup.in | AMUL | GESU9440129 | 40-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTROLLER D/F NEED TO REPLACE REVERSE PHASE CONNECTION DUE TO THE REVERSE PHASE CONNECTION THE CONTAINER CONTROLLER IS DAMAGED AND NOT WORKING | NEED TO REPLACE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT035 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | MUKESH
OCT036 | 2024-10-16 15:17 | operation@crystalgroup.in | RELIANCE | TRIU6618391 | 20-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER BREAKDOWN AL26 GAS PRESSURE 16 THEN CHECKED AND FOUND FILTER CHOKE AND SENSOR FAULTY | NEED TO REPLACE/REPAIR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT036 | Carrier - Thinline | Thinline |  |  |  | Used |  | UMESH
OCT037 | 2024-10-16 15:32 | operation@crystalgroup.in | RELIANCE | CICU2779914 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED & FOUND CONDENSOR COIL VERY DIRTY SO CLEANED IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENTS ALL WORKING GOOD | CONTAINER IS RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT037 | Thermoking | Magnum Plus | E0GM030254 | ABC782800322010282 |  | BrandNew |  | RAMIZ
OCT039 | 2024-10-18 17:21 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DAY 1 TEMP ISSUE & EVP LEAK- UNIT REPLACE DAY 2 CONTAINER HOLE UNIT REPLACED | UNIT REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT039 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | SHAHBUDDIN
OCT040 | 2024-10-21 11:13 | operation@crystalgroup.in | UCT | TRIU6617353 | 20-REEFER | CARRIER | SERVICE-AT SITE | STOCK | FOC | NA | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT040 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | VIRENDRA
OCT041 | 2024-10-21 11:31 | operation@crystalgroup.in | UCT | MWCU5709930 | 20-REEFER | CARRIER | SERVICE-AT SITE | STOCK | FOC | CONTROLLER NEED CONFIGER THREW SOFTWARE CONDENSOR MOTOR NOT REPLACE DUE TO BLADE NOT OPENING | WE HAVE REPLACE LIS EVP MOTOR CONTROLLER , DISPLAY AND HUMIDITY SENSOR FIX DUE TO MISSING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT041 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA
OCT042 | 2024-10-22 09:54 | operation@crystalgroup.in | APL HEALTH CARE | TITU9230954 | 40-REEFER | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | COMPRESSOR REPLACE REQUEST | COMPRESSOR REPLACED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT042 | [7 empty] | VIRENDRA
OCT043 | 2024-10-23 16:07 | operation@crystalgroup.in | ITC | MYRU4519748 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | WE HAVE REPLACE R/S EVP MOTOR, FILTER DRIER, R134a REFULL 900gm AND DAMPER SHEET APPLY 3MTR IN TOP ROOF CONTAINER RUNNING IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT043 | Daikin | Daikin | M003143 | LXE10E136A |  | Used | JSGA623040176 | VIRENDRA
OCT044 | 2024-10-23 16:09 | operation@crystalgroup.in | ITC | PCIU6003244 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | WE HAVE REPLACE R/S EVP MOTOR AND FILTER DRIER REPLACE CONTAINER RUNNING IN SOUND CONDITION WITHOUT ANY ALARM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT044 | Daikin |  |  |  |  | used |  | VIRENDRA
OCT045 | 2024-10-23 17:50 | operation@crystalgroup.in | TIPTOP PLAZA | CICU3876570 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER PLACED IN LOCATION SO DONE THE INSTALLATION AND CHECKED AFTER EQUIPMENTS ALL WORKING GOOD THEN CHECKED GAS MOTOR & COMPRESSOR ALLL WORKING GOOD | CONTAINER WORKING IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT045 | Thermoking | Magnum + | 22A8578JT | ABC782800322010281 | ABC782900321510326 | Brand New |  | UMESH
OCT046 | 2024-10-23 17:53 | operation@crystalgroup.in | TIPTOP PLAZA | CICU3876565 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER PLACED IN LOCATION AND INSTALLATION & CHECKED ALL EQUIPMENTS THEN CHECKED MOTOR AND COMPRESSOR ALL WORKING GOOD | CONTAINER RUNNING IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT046 | Thermoking | Magnum + | 22A4218AT | ABC782800322010051 | ABC782900321510023 | Brand New |  | UMESH
OCT047 | 2024-10-24 15:26 | operation@crystalgroup.in | CRYSTAL | CGMU2988654 | 10-REEFER | CARRIER THINLINE | MACHINE INSPECTION | STOCK | FOC | CARRIER THINLINE UNIT CHECKED & FOUND COMPRESSOR INTERNAL NOISY & HOW PUMPING NOT FIT FOR -20 DEGREE C TO -25 DEGREE C COMPRESSOR OIL BLACK & DIRTY. NEED TO FLASH OUT SYSTEM WITH NITROGEN | IF RELEASE FOR MINUS CARGO NOT FIT -20. WE USED ONLY CHILLED PLUSE CARGO | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT047 | Carrier - Thinline | Thinline | 2907L50458 | LSM60197481 |  | Used |  | SHAHBUDDIN
OCT048 | 2024-10-29 10:09 | operation@crystalgroup.in | GCMMF | CXRU1056669 | 40-REEFER | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | MAIN MCB IS 32A AND ITS TRIPPED | NEED TO CHANGE MAIN CONTACTOR. CURRENT COMPONENT IS 32A AND WE REQUIRED MINIMUM 50A . NOT ABLE TO CHECK IN DETAIL BECAUSE NO POWER CONNECTION SUPPLY PROPER | -NA- |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT048 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | PRAVIN, UMESH
OCT049 | 2024-10-29 10:15 | operation@crystalgroup.in | GCMMF | GESU9440129 | 40-REEFER | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | MAIN MCB IS 32A | WE FOUND THAT MAIN POWER SUPPLY CONNECTION IS WRONG PHASE CONNECTION IS NEUTRAL BECAUSE OF THIS CONNECTION MACHINES CONTROLLER IS DAMAGED & NOT WORKING NEED TO CHANGE MAIN CONTACTOR ALSO EXISTING IS 32A WE REQUIRED 50 A MINIMUM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT049 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ | No
OCT050 | 2024-10-29 12:07 | operation@crystalgroup.in | LANDS FLAVOUR | TIRU6616594 | 40-REEFER | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLDOWN | NEED TO REPLACE SUPPLY SENSOR AND DEFROST SENSOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT050 | [7 empty] | NA | No
OCT051 | 2024-10-30 10:02 | operation@crystalgroup.in | LAURUS UNIT 3 | APRU5091340 | 40-REEFER | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND COMPRESSOR HEAVY BUBBLING DUE TO COMPRESSOR CONTACTING ROD BROKEN NEED TO REPLACE | WE SUGGEST TO REPLACE CONTAINER IN THIS SITE CONDENSOR COIL LEAKKEGE DUE TO COMPRESSOR BUBBLING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT051 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA
NOV001 | 2024-11-04 15:34 | operation@crystalgroup.in | DSV | TITU8258978 | 20-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | COMPRESSOR CONTACTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV001 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN
NOV002 | 2024-11-04 15:39 | operation@crystalgroup.in | QUICK SUPPLY RELIANCE | CICU2779920 | 10-REFEER | THERMOKING MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENRAL CHECKUP | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV002 | Thermoking | Magnum Plus | E0GM030270 | ABC782800322010477 |  | BrandNew |  | SHAHBUDDIN
NOV003 | 2024-11-04 15:46 | operation@crystalgroup.in | ZENFOLD PHARMA | TRIU6618637 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM / REPLACEMENT PARTS | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV003 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040284 | SHAHBUDDIN
NOV004 | 2024-11-04 15:48 | operation@crystalgroup.in | BIOCON | TDRU5800414 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM / GENRAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV004 | Daikin | Daikin | A001807 | LVE10EA36A |  | Refurbished | JSGA623040182 | SHAHBUDDIN
NOV006 | 2024-11-05 14:16 | operation@crystalgroup.in | SOFTBOX | GRMU3707470 | 20-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | IOT INSTALLATION DONE, DISPLAY PATCH/BLUR | NEED TO REPLACE DISPLAY | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV006 | Daikin |  |  |  |  | used |  | SHAHBUDDIN
NOV007 | 2024-11-05 14:18 | operation@crystalgroup.in | SOFTBOX | TITU8257288 | 20-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | IOT INSTALLATION DONE, DISPLAY PATCH/BLUR | NEED TO REPLACE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV007 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | SHAHBUDDIN
NOV008 | 2024-11-06 09:47 | operation@crystalgroup.in | DSV | TITU8258978 | 20-REEFER | THERMOKING MP4000 | REPAIR | LEASE | FOC | UNIT NOT WORKING | REPLACED COMPRESSOR CONTACTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV008 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN
NOV009 | 2024-11-06 09:49 | operation@crystalgroup.in | DHL | DFOU6120281 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM & GENERAL MAINTENANCE | DRY SERVICE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV009 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | SHAHBUDDIN
NOV005 | 2024-11-06 18:33 | operation@crystalgroup.in | NAVIN FLORINE | CCLU1031878 | 20-REEFER | CARRIER THINELINE | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTAND THIS UNIT AND FOUND FILTER DRIER CHOWK COMPRESSOR OVERHEATING AND CONDENSOR COIL HEAVY DIRTY TO WORK R/S EVP MOTOR HEAVY NOISE | WE HAVE REPLACE FILTER DRIER GAS REFILL 3KG CONDENSOR MOTOR REPLACE R/S EVP MOTOR REPLACE CONDENSOR COIL WASH WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV005 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA
NOV011 | 2024-11-07 11:02 | operation@crystalgroup.in | BEJAPURI DAIRY PVT LTD | MYRU4503459 | 40-REFEER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | RUN AND CHECKED OPERATION MAINTAINANCE VOLTAGE ALL MOTOR AMP & ROTATION ELECTRICAL PANEL WIRING & HARNESS CHECKED GAS LEVEL % PRESSURE & PARAMETERS CLEAN UNIT & CONDENSOR COIL UNIT PERFORM AND PASS SHORT PTI UNIT WORKING GOOD CONDITION NOTE:- INSIDE HOUSE KEEPING NOT GOOD NEED TO CELAN MONTHLY UNIT FRONT SIDE ( MACHINE SIDE) TREE BRANCHE NEED TO CUT | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV011 | Daikin | Daikin |  |  |  | Refurbished |  | SHAHBUDDIN
NOV012 | 2024-11-07 11:12 | operation@crystalgroup.in | ITC AQUEA | MYRU4517508 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | UNIT NOT WORKING | NEED TO REPLACE PHASE CONTACTOR BOTH CONTACTOR DEFECTIVE UNIT NOT WORKING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV012 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | RAMIZ
NOV010 | 2024-11-07 15:17 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN LAST TEMPERATURE -14.3 FOUND ICE FOUNDATION ON EVAPORATOR COIL BLOCK SUPPLY AIR FLOW | NEED TO CLEAN EVP COIL AND BUFFET PLATE ARM + BAR FLOOR DUE TO CARGO LOADED NO POSSIBLE CLEAN THIS ARE REEFER UNIT RUNNNING NORMAL TEMPERATURE ISSUE STILL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV010 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ
NOV015 | 2024-11-07 15:48 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-BLAST REEFER | TK MP4000 | SERVICE-ON CALL | LEASE | FOC | ALARM FOR RETURN SENSOR, TEMP NOT PULL DOWN | NEED TO REPLACE RETURN SENSOR THE REEFER UNIT IN NORMAL CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV015 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH
NOV013 | 2024-11-08 10:20 | operation@crystalgroup.in | PRAYAGH COSUMER | MYRU4500552 | 40-REEFER | TK MP-3000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE AND GENERAL INSPECTION DOOR OPEN AND CLOSING ISSUE COMPRESSOR CONTACTOR & LIGHTING C.B FELT DOWN CONTR DOOR HINGES POINT GREECING & OILING DOOR OPEN & CLOSING SMOOTH RUNN UNIT CHECK OPERATION MAIN VOLTAGE ALL MOTOR AMP & ROTATION ALL SENSOR READING & PARAMETER GAS LEVEL AND PRESSURE UNIT ALL OVER WORKING AS SATISFACTORY. UNIT PASS TEST PTI FULL | SECURED MRB WIRING AND COMPRESSOR CONTOR & LIGHT C.B. CLEAN UNIT & CONDENSOR COIL WITH FRESH NORMAL WATER UNIT WORKING FINE & MAINTAIN SET TEMP WITH NO ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV013 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | SHAHBUDDIN
NOV014 | 2024-11-08 10:39 | operation@crystalgroup.in | DSV | TITU8259260 | 20-REEFER | THERMOKING MP4000 | SERVICE-AT SITE | SALE | CHARGEABLE | CUSTOMER REQUEST REPAIR AND QUOTATION UNIT MP4000 PM SERVICE | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV014 | [7 empty] | SHAHBUDDIN | Yes
NOV016 | 2024-11-08 10:55 | operation@crystalgroup.in | RELIANCE | TRIU6618663 | 20-REEFER | CARRIER | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPING OFF DISPLAY FADED | CHECKED AND FOUND EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERATURE DISCONNECTED GR COIL WIRING NEED REPLACED DISPLAY ( CARRIER ) FADED UNIT RUN & MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV016 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN | Yes
NOV017 | 2024-11-08 10:57 | operation@crystalgroup.in | RELIANCE | CCLU1031918 | 20-REEFER | CARRIER | SERVICE-ON CALL | LEASE | FOC | UNIT CARRIER THINLINE UNIT TRIPPING OFF | CHECKED EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERLY DISCONECTED WIRING & MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV017 | Carrier - Thinline | Thinline |  |  |  | brand New |  | SHAHBUDDIN | Yes
NOV018 | 2024-11-08 10:59 | operation@crystalgroup.in | NEWLY WEDS FOODS PVT LTD | MYRU4512527 | 40-REFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | TEMP SENSOR OUT OFF RANGE SET TEMP ISSUE DISPLAY COVER BROKEN | REQUIRED VISIT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV018 | [7 empty] | VIRENDRA | Yes
NOV021 | 2024-11-09 14:43 | pravin.shinde@crystalgroup.in | Hetero 3 | APRU5091041 | 40ft | carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | pm | na | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV021 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | SHAHBUDDIN
NOV019 | 2024-11-09 14:46 | operation@crystalgroup.in | HETERO UNIT 3 | CXRU1026520 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV019 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | SHAHBUDDIN
NOV020 | 2024-11-09 14:47 | operation@crystalgroup.in | HETERO UNIT 3 | CXRU1030427 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV020 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | SHAHBUDDIN
NOV022 | 2024-11-09 14:50 | operation@crystalgroup.in | HETERO UNIT 3 | PCIU6016370 | 10-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | pm | na | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV022 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | SHAHBUDDIN
NOV023 | 2024-11-09 14:52 | operation@crystalgroup.in | CELON LAB | TRIU6616871 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV023 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN
NOV024 | 2024-11-11 12:01 | operation@crystalgroup.in | RELIANCE | CICU1799177 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV024 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 |  | BRand NEW | JSGA622180057 | SHAHBUDDIN
NOV026 | 2024-11-11 15:40 | operation@crystalgroup.in | DSV | TITU9930006 | 40-REEFER | THERMOKING MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM AND GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV026 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | SHAHBUDDIN
NOV025 | 2024-11-12 11:58 | operation@crystalgroup.in | DSV | SJKU4000104 | 40-REEFER | TK MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV025 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN
NOV028 | 2024-11-12 12:29 | operation@crystalgroup.in | Dr. REDDY FTO-9 | CICU1920740 | 40-REEFER | TK MP4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | NA | NO` |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV028 | Thermoking | Magnum Plus | E0GM018643 | ABC782800320490059 |  | BrandNew |  | RAMIZ
NOV027 | 2024-11-13 09:55 | operation@crystalgroup.in | TGF TRANSYS GLOBAL | TITU8259378 | 20-REEFER | TK MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV027 | Thermo King MP-4000 | MP 4000 |  |  |  | Used |  | SHAHBUDDIN
NOV030 | 2024-11-13 18:42 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | NEED TO REPLACE EVAPORATOR MOTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV030 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ
NOV029 | 2024-11-14 10:51 | operation@crystalgroup.in | VIMAL FEEDS | CICU1442256 | 40-REEFER BLAST 5 UNIT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV029 | Thermoking | EOG5003933 | EOG5003933 | 220916, 3.29.00 |  | brand New |  | SHAHBUDDIN
NOV031 | 2024-11-15 12:58 | operation@crystalgroup.in | DR REDDY CTO 5 | CXRU1045896 | 40-REEFER | DAAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV031 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | SHAHBUDDIN
NOV032 | 2024-11-15 13:22 | operation@crystalgroup.in | DR REDDY CTO 05 | CXRU1032564 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV032 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN
NOV033 | 2024-11-15 13:24 | operation@crystalgroup.in | DR REDDY CTO 05 | GSOU6384153 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV033 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN
NOV035 | 2024-11-16 22:42 | operation@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV035 | DAikin |  |  |  |  | Used | JSGA622340482 | SHAHBUDDIN
NOV036 | 2024-11-16 22:44 | operation@crystalgroup.in | ASPIRO PHARMA | CGMU2991560 | 20-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV036 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN
NOV037 | 2024-11-16 23:24 | operation@crystalgroup.in | DR REDDY CTO3 | GSOU6384240 | 40-REEFER | CARRIER THINLINE | INSTALLATION | LEASE | FOC | INSTALLATION | NO | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV037 | Carrier | Carrier Thinline | SSB60749120 |  | ML-3 | used | JSGA622340472 | SHAHBUDDIN
NOV034 | 2024-11-19 16:51 | operation@crystalgroup.in | ZEPTO | GESU9460634 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | DOOR NOT CLOING DUE TO CONTAINER ALIGNMENT WRONG , IMPROPER GROUND LEVEL | NEED TO LIFT THE CONTAINER AND KEEP IN PROPER GROUND LEVEL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV034 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ | No
NOV061 | 2024-11-19 16:57 | operation@crystalgroup.in | RELIANCE | MYRU451588 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULL DOWN ,COPRESSOR CONTACTOR TERMINAL SHORT CIRCUIT | TERMINAL BURNT HAS REPLACED AND FIXED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV061 | [7 empty] | RAMIZ
NOV038 | 2024-11-19 18:13 | operation@crystalgroup.in | jublient | GRMU3607418 | 20-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | E109, E607, TEMPERATURE NOT PULLDOWN | FILTER DRIER CHOKE, REPLACE IT ,& CHARGE GAS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV038 | Daikin |  |  |  |  | Used |  | RAMIZ& ON SITE TECH
NOV039 | 2024-11-19 18:21 | operation@crystalgroup.in | SYMBIOTEC | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | UNIT LOW PRESSURE TRIPPING ALARM E109, | SUSPECTED LEAK | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV039 | Daikin | Daikin |  |  |  | Used
OCT052 | 2024-11-20 16:13 | operation@crystalgroup.in | PARLE | MYRU4506735 | 40-REEFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | TEMPERATURE NOT PULL DOWN | HOT WATER WASHING EVP COIL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT052 | [7 empty] | RAMIZ
OCT017 | 2024-11-20 17:41 | service@crystalgroup.in | DIVIS LAB | DC-UNIT-09 | 40 FT | CARRIER | SERVICE-ON CALL | LEASE | CHARGEABLE | COMPRESSOR CUT OUT & SUPPLY AIR FLOW BLOCK | T BAR FLOOR CLEAN WITH HOT WATER . | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT017 | [7 empty] | RAMIZ
JUL050 | 2024-11-20 23:52 | operation@crystalgroup.in | Crystal Yard-JNPT | GESU9469328 | 40-REEFER | CARRIER-ELITLINE | REPAIR | NA | FOC | COMPRESSOR DEFECTIVE | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL050 | Carrier - Thinline | Elite line |  |  |  | Used |  | NA
JUL051 | 2024-11-20 23:57 | operation@crystalgroup.in | Qwik Supply | TITU7263521 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR DEFECTIVE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL051 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH
JUL052 | 2024-11-21 00:06 | operation@crystalgroup.in | Crystal Yard-Vizag | TRIU6680994 | 20-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | PAINTING REQ | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL052 | Carrier - Thinline | Thinline |  | NSG60383780 |  | Used | JSGA623040285 | THIRD PARTY LOCAL
OCT038 | 2024-11-21 11:42 | service@crystalgroup.in | CSIRPILANI | MORU0322200 | 20FT | CARRIER | SERVICE-ON CALL | SALE | FOC | EVP FAN MOTOR DEFECTIVE | REPLACED EVP FAM MOTOR | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT038 | Thermoking MP-3000 | MP 3000 |  |  |  | Used | JSGA623040313 | VIRENDRA | No
NOV062 | 2024-11-25 16:56 | service@crystalgroup.in | Lupin Ltd | TRIU6681882 | 20FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | ALARM 22 & 53 , FOUND R/ S EVAPROTER MOTOR DEFECTIVE | NEED TO REPLACED R/S EVAPROTER MOTOR. | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV062 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040302 | SHAHBUDDIN
NOV040 | 2024-11-26 11:57 | operation@crystalgroup.in | ITC | MYRU4517508 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PREVENTIVE MAINTENANCE & SPARES INSTALLATON | SPARES REQUIRED IN NEXT VISIT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV040 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | VIRENDRA | Yes
NOV041 | 2024-11-26 12:38 | operation@crystalgroup.in | NSR TRADERS | TCLU1112683 | 40-REEFER | TK MP3000 | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | WE HAVE ATTENDED THE UNIT AND FOUND DISPLAY NOT SHOWING SET POINT HEATER RELAY AND SOCKET BURNT KEYPAD DAMAGER FILTER DRIER RUSTED | WE HAVE CLEAN CONDENSOR COIL WITH NORMA WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM ALL WORK NEED TO DONE ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV041 | [7 empty] | VIRENDRA | Yes
NOV042 | 2024-11-26 14:44 | operation@crystalgroup.in | LAURUS UNIT 3 | MYRU4519115 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAEV REPLACED AMBIENT SNESOR 2 NOS SAS SENSOR 1 NOS AND CLEAAN CONDENSOR WITH NORMAL WATER CONTAINER RUNNING SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV042 | Daikin | Daikin | 806162 | LXE10E136A2 |  | Refurbished |  | VIRENDRA
NOV043 | 2024-11-26 15:12 | operation@crystalgroup.in | LAURUS UNIT 3 | KKFU6711724 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER AND CLEAR ALARM AA54. CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV043 | Carrier - Thinline | Thinline | 4515UD3741 | LSX60253415 |  | used |  | VIRENDRA | Yes
NOV044 | 2024-11-26 15:42 | operation@crystalgroup.in | LAURUS UNIT 3 | KKFU6710768 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSER COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONSDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV044 | [7 empty] | VIRENDRA
NOV045 | 2024-11-26 15:46 | operation@crystalgroup.in | LAURUS UNIT 3 | TDRU7153256 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALALRM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV045 | Daikin | Daikin |  |  |  | used | JSGA623040290 | VIRENDRA
NOV046 | 2024-11-26 15:49 | operation@crystalgroup.in | LAURUS UNIT 3 | BMOU9784137 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HACE REPLACED SUPPLY SENSOR 2 NOS OUTLET SENSOR 1 NOS RETURN SENSOR 1 NOS CONDNSOR COIL WARN WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV046 | Daikin |  |  |  |  | used |  | VIRENDRA
NOV047 | 2024-11-26 15:54 | operation@crystalgroup.in | LAURUS UNIT 3 | APRU5091340 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | UNIT INSTALLATION | WE HAVE REPLACED MAIN UNIT WITH NEW ONE AND RUN CONTIANER , CONTAINER RUNNING IN GOOD CONDITION WITHOUT ANY ALARM PRESENT TEMP 15 TO 25 C THIS UNIT IS MAINTAINING TEMP | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV047 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA
NOV048 | 2024-11-26 16:02 | operation@crystalgroup.in | LAURUS UNIT 3 | MYRU4505847 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE INSPECTION THIS UNIT AND FOUND CONTAINER WITHOUT ANY ALARM ANY ALARM AND MAITAIN TEMP +20.7C | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV048 | Daikin | Daikin |  |  |  | Used |  | VIRENDRA
NOV049 | 2024-11-26 16:09 | operation@crystalgroup.in | LAURUS UNIT 3 | TCLU1912290 | 20-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THE UNIT AND FOUND CONATAINER SHOWING ALARM E406 SG SENSOR FAILURE | WE HAVE REPLACED SGS SENSOR CLEAN CODENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV049 | Daikin |  |  |  |  | used |  | VIRENDRA
NOV050 | 2024-11-26 16:14 | operation@crystalgroup.in | LAURUS UNIT 3 | DFOU120384 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PEVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER AND SHEET KEY JACK PROPER FILTER NOW CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV050 | [7 empty] | VIRENDRA
NOV051 | 2024-11-26 16:18 | operation@crystalgroup.in | LAURUS UNIT 3 | SUDU6257274 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE REPLACE HUMIDITY SENSOR AND CONDENSOR COIL WASH WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV051 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA | Yes
NOV052 | 2024-11-26 16:37 | operation@crystalgroup.in | LAURUS UNIT 3 | TITU9930011 | 40-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | WE ATTENDED THIS CONTAINER AND FOUND CONDENSOR COIL NORMAL DIRTY TO WARN AND SOFTWARE NEED TO UPDATE | WE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV052 | Thermoking MP-4000 | MP 4000 | 14D8568HT | EOG1000566 |  | Used |  | VIRENDRA | Yes
NOV053 | 2024-11-26 16:45 | operation@crystalgroup.in | LAURUS UNIT 6 | MYRU4509035 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV053 | Daikin | Daikin | 802602 | LXE10E136A |  | Used |  | VIRENDRA
NOV054 | 2024-11-26 16:50 | operation@crystalgroup.in | LAURUS UNIT 6 | ARCU4530675 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH CONDENSOR MOTOR CREATE SOUND SOMETIMES IN RUNNING CONDITION | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SUND CONDITION WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV054 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used |  | VIRENDRA | Yes
NOV055 | 2024-11-26 17:10 | operation@crystalgroup.in | LAURUS UNIT 4 | MYRU4500613 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE ATTEND THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HAVE CLEAN COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV055 | Daikin | Daikin | M005107 | LXE10E136A2 | 24C1 | Used |  | VIRENDRA
NOV056 | 2024-11-26 17:14 | operation@crystalgroup.in | LAURUS SYNTHESIS UNIT 2 | TRIU6680994 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND CONTAINER SHOWING AL57 AMBIENT SENSOR DIF TO REPLACE FILTER DRIER RUSTED TO REPLACE AND CONDENSOR COIL HEAVY DIRTY | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV056 | Carrier - Thinline | Thinline |  | NSG60383780 |  | Used | JSGA623040285 | VIRENDRA | Yes
NOV063 | 2024-11-26 17:35 | operation@crystalgroup.in | ALPHA DAIRY | CXRU1042080 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | CHECKED AND FOUND CONTAINER BREAKDOWN THEN CHECKED OTHER EQUIPMENTS AND FOUND 3 NOS SENSOR ARE FAULTY NEED TO REPLACE BETTER TO CHANGE ALL SENSOR | CONTAINER RUNNING IN GOOD CONDITION BUT NEED TO REPLACE SS, DSS , EOS FOR STARTING THE CONTAINER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV063 | [7 empty] | SHAHBUDDIN | Yes
NOV064 | 2024-11-26 18:12 | operation@crystalgroup.in | ALPHA DAIRY | APRU5094288 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION THEN CHECKED OTHER EQUIPMENTS LIKE ELECTRICAL & MECHANICAL PARTS ALL PAPRTS ARE WORKING IN GOOD CONDITION | CONTAINER RUNNING IN GOOD CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV064 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | Ninad | No
NOV068 | 2024-11-27 11:01 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKEDD AND FOUND CONTAINER WORKING GOOD BUT TEMPERATURE COMING SLOW SO REAYIFY THE PROBLEM & FOUND (EVP MOTOR) L/S NOT WORKING IN LOW SPEED SO TEMPERATURE GO DOWN SLOWLY AFTR -5C | CONTAINER RUNNING GOOD BUT THEY OPEN DOOR EVERY 40 TO 45 MIN NEED TO NOT OPEN DOOR FOR ATLEAST 4 HOURS IN CONTINOUS RUNNING NEED TO CHANGE EVP MOTOR ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV068 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | UMESH
NOV066 | 2024-11-27 13:37 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | SENSORS NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV066 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH
NOV067 | 2024-11-27 14:22 | operation@crystalgroup.in | RELIANCE | TCLU1130265 | 40-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | CONTAINER RUNN IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV067 | Thermoking | MP-4000 |  |  |  | Refurbished |  | UMESH
NOV065 | 2024-11-27 15:07 | service@crystalgroup.in | RELIANCE | CICU2094089 | 10 FT BLAST | THERMOKING | SERVICE-ON CALL | LEASE | FOC | TEMPERSTURE NOT PULL DOWN /ICE FORMATION | Internal hot water wash done . | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV065 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 |  | BrandNew |  | SHAHBUDDIN | Yes
NOV069 | 2024-11-27 15:34 | operation@crystalgroup.in | ZEPTO | GESU9460634 | 40-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE DOOR NOT CLOSING | NEEED TO CORRECT WIRING | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV069 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH
NOV070 | 2024-11-28 13:02 | crm@crystalgroup.in | RELINACE | CICU3876586 | 10FT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | "CHECKED AND FOUND CONTAINER RUNNING GOOD CONDENSOR COIL CLEANED, COMPRESSOR MOTORS AND VALVES SENSORS WORKING IN GOOD CONDITION AND TAINING PROVIDED TO MR.PRAMOD RANA." | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV070 | Thermoking | Magnum + | 22A4227AT | ABC782800322010496 | ABC782900321510417 | Brand New |  | UMESH
NOV071 | 2024-11-28 13:10 | crm@crystalgroup.in | RELIANCE | CXRU1043912 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MEASURE | CONDENSOR CLEANED PROPERLY ,NO FAULT IN SYSTEM. CONATINER RUNNING IN GOOD CONDITION. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV071 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH
NOV072 | 2024-11-28 13:31 | crm@crystalgroup.in | RELIANCE | CXRU1040322 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PRENVENTIVE MEASURE | CONTAINER IN GOOD CONDITION, CONDENSER COIL CLEANED, ALL EQUIPMENTS (ELECTRICAL MECHENICAL ARE WORKING | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV072 | [7 empty] | UMESH
NOV057 | 2024-11-28 16:45 | crm@crystalgroup.in | LAURUS UNIT-1 | APRU5000210 | 40 FT | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE | LEASE | FOC | ATTEND THE SITE AND FOUND , CONDENSOR COIL NORMAL, DIRTY TO WASH, KEYPAD NOT WORKING NEED TO REPLACE WITH DISPLAY | CONDESOR COIL WASHED WITH NORMAL WATER, CONTAINER RUN A SOUND WITHOUT ANY ALRAM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV057 | Carrier - Thinline | Thinline | 2594J02559 | GGCR80067211 |  | Refurbished |  | VIRENDRA | Yes
NOV058 | 2024-11-28 17:00 | crm@crystalgroup.in | LAURUS UNIT - 1 | CXRU1037308 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE,CONTAINER SHOWING ALRAM E401 A | WASHED CONDENSOR COIL WITH NORMAL WATER REPACED SUPPLY SENSOR 2 NOS , CONTAINER RUNNING SOUND CONDITION WITHOUT ANY ALRAM. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV058 | Daikin | LXE10E147F2 | M000334 | K31505146690 | DECOS 3F 2553 / 1 | Used |  | VIRENDRA
NOV059 | 2024-11-28 17:14 | crm@crystalgroup.in | LAURUS UNIT 1 | PCIU6006639 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE , DISPLAY NOT SHOWING SET POINT , CONDENSOR COIL DIRTY | CONDENSOR COIL WITH NORMAL WATER, CONTAINER RUNINING SOUND CONDITION WITHOUT ANY ALRAM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV059 | Daikin |  |  |  |  | used |  | VIRENDRA | Yes
NOV073 | 2024-11-28 17:41 | crm@crystalgroup.in | LUPIN -THANE | CCLU1036859 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE | PAY SERVICE DONE CHECKED UNIT OPERATION MAIN UINT , ALL MOTOR ,GAS LEVEL, PRESSURE UNIT CLEAN CONDENSOR COIL, CHILLED ALL SENSOR READING , WORKING AS FINE , | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV073 | Carrier |  |  |  |  | Used | JSGA623040314 | SHAHBUDDIN
NOV060 | 2024-11-30 12:59 | crm@crystalgroup.in | AJINOMOTO BIO | KKFU6706142 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE, | REPLACED SENSOR | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV060 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040294 | VIRENDRA | Yes
NOV082 | 2024-11-30 15:28 | crm@crystalgroup.in | AJINOMOTO BIO | KKFU6712079 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | REPLACED SENSOR FULLTER DUTER REPLACE AND CONDENSOR COIL WASHED WITH NORMAL WAATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV082 | Carrier - Thinline | Thinline |  | 69NT40541321 |  | brand New | JSGA623040320 | VIRENDRA
NOV084 | 2024-11-30 15:44 | crm@crystalgroup.in | AJINOMOTO BIO | BMOU9766180 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | REPLACED SUPPLY SENSOR WASHED CONDENSOR WITH CLEAN WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV084 | Daikin |  |  |  |  | used |  | VIRENDRA
OCT019 | 2024-12-02 14:31 | service@crystalgroup.in | RENEW POWER | CICU2782230 | 40HQ | MP4000 | SERVICE-ON CALL | SALE | FOC | TEMPERATURE NOT POLL DOWN, CONDENSOR COIL HEAVY DIRTY | CONDENSOR COIL CLEANED WITH FRESH WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT019 | Thermoking | Magnum Plus | E0GM030246 | ABC782800322010263 |  | BrandNew |  | SHAHBUDDIN
DEC001 | 2024-12-03 15:10 | crm@crystalgroup.in | TANISH LAB | CXRU1040451 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | SHEET KEY REPLACED CONDENSOR COIL WASHED WITH NORMAL WATER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC001 | DAikin | LXE10E147F2 | M001991 | K31408134485 | DECOS 3F 2551 / 1 | Used |  | VIRENDRA | Yes
DEC002 | 2024-12-03 15:14 | crm@crystalgroup.in | TANISH LAB | TRLU1741601 | 40FT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | CLEAN CONDENSOR COIL WITH NORMAL WATER CONATINER RUN IN SOUND CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC002 | Thermoking | Thermoking |  |  |  | used |  | VIRENDRA
DEC003 | 2024-12-03 15:24 | crm@crystalgroup.in | APITARLO PHARMA | TITU725080 | 40FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | REPLACED DISPLAY COMPRESSOR PAINT WITH SPRAY AND CONDENSOR COIL WASL WITH NORMAL WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC003 | [7 empty] | VIRENDRA
NOV075 | 2024-12-03 16:16 | crm@crystalgroup.in | AJINOMOTO BIO | KKFU6994964 | 40FT | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | REPLACE SUPPLY SENSOR , FULLTER REPLACE AND CONDENSOR COIL WASH WITH NORMAL WATER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV075 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | VIRENDRA | Yes
NOV083 | 2024-12-03 16:19 | crm@crystalgroup.in | AJINOMOTO BIO | TITU9930069 | 40 FT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | CLEANED CONDENSOR COIL WITH NORMAL WATER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV083 | Thermoking | MP-4000 | NA | NA | NA | USED
NOV085 | 2024-12-03 16:23 | crm@crystalgroup.in | AJINOMOTO BIO | HDMU5537036 | 40FT | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | FIRST NEED TO TEST THEN TOPUP GAS THEN SECOND TEST | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV085 | Carrier | Thineline |  |  |  | Used
NOV074 | 2024-12-05 12:40 | operation@crystalgroup.in | RELIANCE | CICU3896586 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED & FOUND TEMPERATURE ISSUE TEMPERATURE NOT PULLING DOWN BELOW -11C SO CHECKED & FOUND SOME SENSOR ARE NOT WORKING SO REMOVE SENSOR AND REFIX | CONTAINER RUNNING IN GOOD CONDITION | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV074 | [7 empty] | UMESH
NOV081 | 2024-12-05 13:04 | operation@crystalgroup.in | SYMBIOTEC | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-AT SITE | SALE | FOC | BREAKDWN | REAPAIR WORK | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV081 | Daikin | Daikin |  |  |  | Used
DEC004 | 2024-12-05 13:24 | operation@crystalgroup.in | DR REDDY CTO 6 | CXRU1033616 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | ONE SENSOR REPLACED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC004 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | VIRENDRA
DEC007 | 2024-12-05 14:52 | operation@crystalgroup.in | SYMBIOTEC | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | BREAKDOWN | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC007 | Daikin | Daikin |  |  |  | Used
DEC008 | 2024-12-05 15:07 | operation@crystalgroup.in | JUBLIENT | GRMU3607418 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC008 | Daikin |  |  |  |  | Used |  | VIRENDRA | Yes
DEC009 | 2024-12-06 17:58 | service@crystalgroup.in | RELIANCE | CICU2779935 | 10FT | MP4000 | SERVICE-ON CALL | LEASE | FOC | FLUCTUATIONS IN TEMEPRATURE, PCM IS NOT FREEZIN. WRONG STACK PCM FRO BLAST | GIDE TO KEEP RIGHTLY PCM STACK . UNDER OVSERVATION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC009 | Thermoking | Magnum Plus | E0GM030274 | ABC782800322010476 |  | BrandNew |  | RAMIZ | No
DEC010 | 2024-12-06 18:00 | service@crystalgroup.in | RELIANCE | CICU2779909 | 10 FT | MP4000 | SERVICE-ON CALL | LEASE | FOC | FLUCTUATIONS IN TEMEPRATURE, PCM IS NOT FREEZIN. WRONG STACK PCM FRO BLAST | GIDE TO KEEP RIGHTLY PCM STACK . UNDER OVSERVATION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC010 | Thermoking | Magnum Plus | E0GM030263 | ABC782800322010201 |  | BrandNew |  | RAMIZ | No
DEC012 | 2024-12-07 17:51 | service@crystalgroup.in | RELIANCE DC | TRIU8850831 | 40FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | Frequent power ON/OFF & AL27, 22, 63,15,52 TEMPERATURE NOT PULL DOWN | NEED REPLACED CONTROLLER L3i C/R 12-5501 , SUSPECTED Carrier Contactor 12A, Carrier supply sensor , Carrier Return Sensor, Carrier Contactor 30A Carrier Defrost Sensor TRANSFORMER, SERVICE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC012 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA622180048 | RAMIZ
DEC013 | 2024-12-09 13:07 | operation@crystalgroup.in | Crystal Yard | Site Cabine | NA | NA | NA | NA | NA | NA | NA | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC013 | [7 empty] | NA
DEC014 | 2024-12-09 15:27 | service@crystalgroup.in | OLA | TCLU1906493 | 20 FT | DAIKIN | SERVICE-ON CALL | LEASE | FOC | COMPRESSOR RISTED & CONDENSER COIL NORMAL DIRTY | NEED TO PAINT COMPRESSOR BOTTOM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC014 | Daikin | Daikin |  |  |  | Used | JSGA623040305 | RAMIZ | No
DEC015 | 2024-12-09 16:40 | operation@crystalgroup.in |  | NA | NA | NA | NA | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC015 | [7 empty] | NA
DEC016 | 2024-12-09 20:15 | service@crystalgroup.in | ZEPTO | TITU9928040 | 40 FT | THERMOKING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERSTURE NOT PULL DOWN | SUSPECTED TO LESS GAS OR COMPRESSOR CONTACTOR DEFECTIVE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC016 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | SHUBHAM
NOV006 | 2024-12-10 14:29 | service@crystalgroup.in | SOFT BOX | GRMU3707470 | 20FT | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE/ PULL DOWN SLOWLY | NEED TO REPLACED EXPNTION VALVE & EXPANTION COIL & TEMPERATURE SENSOR SUPPLY 2 NOS & EVAPROTER INLET SENSOR . | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV006 | Daikin |  |  |  |  | used |  | SHAHBUDDIN
DEC017 | 2024-12-11 10:32 | service@crystalgroup.in | soft box | GRMU3707470 | 20 FT | DAIKIN OLD | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NEED TO REPLACED EXPANCTION VALVE & COIL | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC017 | Daikin |  |  |  |  | used |  | RAMIZ | Yes
DEC018 | 2024-12-11 10:35 | service@crystalgroup.in | RELIANCE | TRIU6618663 | 20 FT | CARRIER | SERVICE-ON CALL | LEASE | AMC | UNIT TRIPPED DURING DEFROST PROCRESS | Possible defect in coil heater, dts sensor and Disply NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC018 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN | Yes
DEC019 | 2024-12-11 10:38 | service@crystalgroup.in | RELIANCE | CCLU1031918 | 20 FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPPED DURING DEFROST OPRATION | Defect in heater coil. NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC019 | Carrier - Thinline | Thinline |  |  |  | brand New |  | SHAHBUDDIN | Yes
DEC020 | 2024-12-11 15:03 | service@crystalgroup.in | Aspiro Pharma | CXRU1030387 | 20 FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | MOTOR MAKING NOISE, Controller ISSUE | NEED TO FIX Evaporator Motor single ph & Controller ML 3 | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC020 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | RAMIZ | No
DEC011 | 2024-12-12 10:26 | service@crystalgroup.in | GENNOVA BIOPHARMA | CICU1938565 | 20FT | THERMOKING | INSTALLATION | LEASE | FOC | OQ (DOCUMENTATION) | OQ (DOCUMENTATION) DONE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC011 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | SHAHBUDDIN
NOV076 | 2024-12-12 10:58 | service@crystalgroup.in | AJINOMOTO BIO | KKFU6712079 | 40 FT | carrier thine line | SERVICE-AT SITE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV076 | Carrier - Thinline | Thinline |  | 69NT40541321 |  | brand New | JSGA623040320 | VIRENDRA | Yes
NOV077 | 2024-12-12 11:03 | service@crystalgroup.in | AJINOMOTO BIO | TITU9930069 | 40 FT | THERMOKING | SERVICE-AT SITE | LEASE | FOC | FOUND CONDENSER COIL DIRTY | CLEAN CONDENSER WIT FRESH WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV077 | Thermoking | MP-4000 | NA | NA | NA | USED |  | VIRENDRA | Yes
NOV078 | 2024-12-12 11:12 | service@crystalgroup.in | AJINOMOTO BIO | BMOU9766180 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | FOUND SUPPLY SENSOR 2 NOS DEFECTIVE E401 & E402 | Replaced supply sensor with new 2 nos & clean condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV078 | Daikin |  |  |  |  | used |  | VIRENDRA | Yes
NOV079 | 2024-12-12 11:20 | service@crystalgroup.in | AJNOMOTO BIO | HDMU5537036 | 40 ft | carrier thine line | SERVICE-AT SITE | LEASE | FOC | found less gas in system due to that compress or run continuously. | clean condenser coil with fresh water | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV079 | Carrier | Thineline |  |  |  | Used |  | VIRENDRA | Yes
DEC021 | 2024-12-12 12:43 | service@crystalgroup.in | crystal yard | GESU9440432 | 40 FT | CARRIER THINE LINE | REPAIR | NA | NA | COMPRESSOR & CONTROLLER & DISPLY & ISOPLUG | COMPRESSOR & CONTROLLER & DISPLY & ISOPLUG NEED TO FIX FOR REPAIR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC021 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | RAMIZ | No
DEC023 | 2024-12-12 16:53 | service@crystalgroup.in | Devis Lab-Hyderabad | DCUNIT09 | 40 FT | Carrier Thine | SERVICE-ON CALL | SALE | FOC | Internal T Floor Ice Formation | Internal T Floor Ice Formation & temperature issue | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC023 | [7 empty] | RAMIZ | Yes
DEC022 | 2024-12-12 18:32 | service@crystalgroup.in | CRYSTAL YARD | CRYSTAL YARD | 40 FT | DAIKIN | REPAIR | STOCK | FOC | COMPRESSEO NO WORKING | COMPRESSOR DEFECTICE & EXPANCATION VALVE & STAINER & FILTER DRIER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC022 | [7 empty] | UMESH | Yes
SEP005 | 2024-12-13 11:52 | service@crystalgroup.in | shivamrut | CXRU1030854 | 40 FT | Daikin | SERVICE-AT SITE | LEASE | FOC | temperature not pull down | found leakage | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP005 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | Mukesh
JUL055 | 2024-12-13 14:58 | service@crystalgroup.in | MOCHAN FOODS | MYRU4500552 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | compressor tripped due to low voltage | need to replaced MP 3000 relay board | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL055 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | RAMIZ
DEC024 | 2024-12-14 14:24 | service@crystalgroup.in | Lauruslabs unit-2 | PRGU4958724 | 40 FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | AL 06 KEY PAD NOT WORKING | NEED TO CHANGE SET POINT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC024 | Carrier - Thinline |  |  |  |  | Used |  | VIRENDRA | No
DEC025 | 2024-12-14 17:13 | service@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd, | CXRU1030387 | 40 FT | DAIKIN | SERVICE-ON CALL | LEASE | FOC | REVENTIVE MAINTENANCE Required | NA | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC025 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | RAMIZ
DEC029 | 2024-12-18 17:29 | pravin.shinde@crystalgroup.in | Crystal Yard | Site Cabin 79 | Modified Cargo Shipping Container 20'X8'X12' | Porta Cabin | NA | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC029 | [7 empty] | RAMIZ | No
DEC026 | 2024-12-18 18:26 | mum.depot@crystalgroup.in | CRYSTAL | CGMU2990461 | 20 FT | CARRIER | REPAIR | STOCK | FOC | CONDENSER LEAKED/ STS SENSOR FOUND FAULTY AND EVP MOTOR NOISY | UNDER REPAIR | EVP MOTOR BEARING, ISO PLUG, STS SENSOR, BRAZING ROD, R134a GAS, FILTER DRIER, N2, BRAZING SET, VACCUM PUMP |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC026 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | RAMIZ | Yes
DEC030 | 2024-12-19 00:18 | service@crystalgroup.in | SOFTBOX | GRMU3707470 | 20 FT | DAIKIN (DECOSE D III) | SERVICE-AT SITE | LEASE | FOC | TEMPERATURENOT PULL DOWN | EXP VALVE & COIL NEED TO REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC030 | Daikin |  |  |  |  | used |  | RAMIZ
DEC031 | 2024-12-19 00:47 | service@crystalgroup.in | DIVIS LAB | SEZDC04 | 40 FT | CARRER THINE LINE | SERVICE-AT SITE | SALE | CHARGEABLE | Both evaporator motor heavy noise & al 56 supply temperature sensor defective & condenser coil dirty | cleaned condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC031 | [7 empty] | RAMIZ
DEC032 | 2024-12-19 01:10 | service@crystalgroup.in | DIVIS LAB | SEZDC06 | 40 FT | CSRRIER THINE LINE | SERVICE-AT SITE | SALE | CHARGEABLE | EVP DRAIN CLOGGED & DOOR GASKET HANGING (int) | Clean Evaporator drain & cut removed damaged gasket | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC032 | [7 empty] | RAMIZ
DEC027 | 2024-12-19 13:05 | mum.depot@crystalgroup.in | Dr Reddy- CTO 6 | CXRU1033616 | 40 | Daikin | SERVICE-ON CALL | LEASE | FOC | water leaking | advice to client for house keeping/ need to clean with normal hot water inside and evaporator section | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC027 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | UMESH | Yes
DEC028 | 2024-12-19 13:08 | mum.depot@crystalgroup.in | Dr Reddy- CTO6 | KKFU6712802 | 40 | CARRIER | SERVICE-ON CALL | LEASE | FOC | Water leaking issue | Advice for house keeping, need to clean inside and evaporator section with normal hot water | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC028 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | UMESH | No
DEC033 | 2024-12-19 13:11 | rahul.gawade@crystalgroup.in | Crystal Yard | TRLU8727441 - Site Cabin 77 | 20ft | NA | NA | NA | NA | NA | NA | Crystal Logo 10'X3' |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC033 | [7 empty] | NA
DEC034 | 2024-12-20 16:35 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1030854 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC034 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | NA
DEC037 | 2024-12-21 11:55 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1030854 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC037 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | NA
DEC038 | 2024-12-21 12:07 | rahul.gawade@crystalgroup.in | Crystal Yard | ARCU4530736 | 40RF | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC038 | Carrier - Thinline | Thinline |  | JSL90656195 |  | used |  | NA
DEC039 | 2024-12-21 12:09 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1036533 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC039 | [7 empty] | NA
DEC041 | 2024-12-21 15:38 | rahul.gawade@crystalgroup.in | Crystal Yard | WHLU4283466 | 40ft Dry | NA | REPAIR | STOCK | FOC | NA | Na | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC041 | [7 empty] | NA
DEC042 | 2024-12-21 16:26 | rahul.gawade@crystalgroup.in | Crystal Yard | JWWU5090354 | 20ft Dry | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC042 | [7 empty] | NA
DEC043 | 2024-12-21 16:37 | rahul.gawade@crystalgroup.in | Crystal Yard | JWWU5090518 | 20ft Dry | NA | REPAIR | STOCK | FOC | NA | Na | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC043 | [7 empty] | NA
DEC044 | 2024-12-21 17:15 | rahul.gawade@crystalgroup.in | Crystal Yard | MSCU5735843 | 40ft Dry | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC044 | [7 empty] | NA
DEC046 | 2024-12-21 21:13 | service@crystalgroup.in | Dr Reddy CTO 06 | TRIU6632949 | 20 FT | CARRIER THINE LINE | SERVICE-AT SITE | LEASE | FOC | found condenser coil normal dirty & evaporator Drin pipe clogged , less gas | cleaned condenser coil with fresh water & cleaned evp drin pipe with water presser | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC046 | Carrier - Thinline | Thinline | 1808L295 | MS60317785 |  | Used |  | RAMIZ | Yes
DEC047 | 2024-12-21 22:35 | service@crystalgroup.in | Dr Reddy CTO 06 | CXRU1033616 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | AMC | WATER STATEMENT IN SIDE THE DUE TO DRAIN CLOGGED & CONDENSER COIL NORMAL DIETY | Cleaned condenser coil with fresh water & cleaned evp drain pipe with water presser | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC047 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | RAMIZ | Yes
DEC050 | 2024-12-27 12:25 | rahul.gawade@crystalgroup.in | Indian Navy | HNKU6172760 | 40ft HQ DV | NA | REPAIR | STOCK | FOC | Site Installation | NA | Installtion Material and service |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC050 | [7 empty] | NA
DEC051 | 2024-12-27 12:27 | rahul.gawade@crystalgroup.in | Indian Navy | LYGU4092923 | 40ft HQ DV | NA | REPAIR | STOCK | FOC | Site Installation | NA | Installtion Material and service |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC051 | [7 empty] | NA
DEC049 | 2024-12-27 15:52 | mum.depot@crystalgroup.in | LUPIN | CCLU1036859 | 20FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | NEED TO VISIT | SUPPLY SENSOR & DISPLAY |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC049 | Carrier |  |  |  |  | Used | JSGA623040314 | UMESH
DEC054 | 2024-12-29 11:35 | operation@crystalgroup.in | CRYSTAL YARD | PORTA CABIN | - | - | READINESS OF CONTAINER | NA | NA | FOR PORTA CABIN READINESS | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC054 | [7 empty] | RAMIZ | No
DEC055 | 2024-12-29 12:27 | operation@crystalgroup.in | CRYSTAL YARD | CLHU8437426 | 40FT | DRY | READINESS OF CONTAINER | STOCK | FOC | DENTING AND PATCH WORK | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC055 | [7 empty] | RAMIZ | No
DEC056 | 2024-12-29 12:54 | operation@crystalgroup.in | CRYSTAL YARD | MANY | NA | NA | MACHINE INSPECTION | STOCK | FOC | CONTAINER SURVEY | 3RD PARTY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC056 | [7 empty] | RAMIZ | No
DEC057 | 2024-12-29 13:16 | operation@crystalgroup.in | CRYSTAL YARD | MSCU5735843 | 40FT | DRY | REFURBISHMENT OF CONTAINER | STOCK | FOC | LIGHT FITTING | 3RD PARTY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC057
DEC058 | 2024-12-30 11:20 | crm@crystalgroup.in | Lupin Ltd | TRIU6681882 | 20 STD RF | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | None | Container is working well | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC058 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040302 | UMESH
DEC059 | 2024-12-30 11:53 | operation@crystalgroup.in | CRYSTAL YARD | HDMU5542110 | 40FT | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | FLOOR NEED TO REPAIR | 3RD PARTY VENDOR REPARI FLOOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC059 | [7 empty] | RAMIZ | No
DEC060 | 2024-12-30 13:10 | mum.depot@crystalgroup.in | Tan90 Thermal Solutions Private Limited - PUNE | CICU3876523 | 10FT | TK MP-4000 | SERVICE-AT SITE | LEASE | FOC | UNIT TEMPERATURE NOT REACHED AT SET TEMPERATURE | UNDER PROCESS | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC060 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No
DEC052 | 2024-12-30 13:21 | mum.depot@crystalgroup.in | AJINOMOTO BIO | HDMU5537036 | 40FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | LOW GAS IN SYSTEM | NEED TO ADD GAS AND PM SERVICE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC052 | Carrier | Thineline |  |  |  | Used |  | RAMIZ | Yes
DEC053 | 2024-12-30 13:24 | mum.depot@crystalgroup.in | AJNOMOTO BIO | KKFU6994964 | 40FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | LOW GAS IN SYSTEM AND PM REQUIRED | NEED TO ADD GAS AND PM SERVICES AT SITE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC053 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | RAMIZ | Yes
DEC061 | 2024-12-30 15:05 | mum.depot@crystalgroup.in | SOFTBOX | TITU8257288 | 20FT | TK MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | DISPLAY FOUND BLUR | NEED TO CHANGE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC061 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | RAMIZ | Yes
DEC040 | 2024-12-30 16:14 | rahul.gawade@crystalgroup.in | Cipla | CRIU4024012, CRIU4024028 | 40FT Refer (Super Store 2 Bay) | Thermoking MP4000 | INSTALLATION | SALE | NA | Installation | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC040 | [7 empty] | SHAHBUDDIN, Harish , Akshay
DEC075 | 2024-12-30 16:26 | operation@crystalgroup.in | CRYSTAL | QNLU1018110 | 20GP | DRY | READINESS OF CONTAINER | STOCK | FOC | CUSTOMIZE CONTAINER | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC075 | [7 empty] | RAMIZ | No
DEC077 | 2024-12-30 16:30 | operation@crystalgroup.in | CRYSTAL (AMEY HYDRO ENGINEERING) | GESU2720771 | 20GP | DRY | READINESS OF CONTAINER | STOCK | FOC | CUSTOMIZE CABIN | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC077 | [7 empty] | RAMIZ | No
DEC048 | 2024-12-30 17:34 | rahul.gawade@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40FT Reefer - Dual Machine | Thermoking MP4000 | PREVENTIVE MAINTENANCE | SALE | FOC | Issue in Display, having damaged pixel. | Need to Replace | VGA display |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC048 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes
DEC072 | 2024-12-30 18:03 | rahul.gawade@crystalgroup.in | Crystal Yard | CRLU3181686 | 20FT Reefer | NA | READINESS OF CONTAINER | STOCK | NA | No Refer Machine | Refer Machine Required | Refer Machine Required |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC072 | Daikin | Daikin |  |  |  | Used |  | RAMIZ | No
DEC083 | 2024-12-31 14:55 | service@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | GESU9568130 | 40 FT | NA | SERVICE-ON CALL | SALE | NA | UN ABALE TO CLOSE THE DOOR BOTH | NEED TO CHECK DOOR ALIMENT & GROUND LEVEL ISSUE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC083 | [7 empty] | UMESH
DEC082 | 2024-12-31 15:55 | service@crystalgroup.in | Cipla | CRIU4024028 | 40 ft 2 bay | tk mp 4000 | INSTALLATION | SALE | CHARGEABLE | installation | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC082 | Thermoking | TK MP 4000 |  |  |  | New |  | SHAHBUDDIN, Harish , Akshay
DEC087 | 2024-12-31 17:00 | service@crystalgroup.in | Qwik supply chain Pvt Ltd | APRU5066497 | 40 ft | carrier tine line | SERVICE-ON CALL | LEASE | FOC | condense coil heavy dirty,( suspected = filter drier & less gas & defrost sensor ) | clean condenser coil with fresh water , under observation nest 24 hrs | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC087 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040296 | RAMIZ
DEC044 | 2024-12-31 17:22 | service@crystalgroup.in | Crystal | MSCU5735843 | 40 ft | na | NA | NA | NA | ready for dispatch | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC044 | [7 empty] | NA
DEC041 | 2024-12-31 17:24 | service@crystalgroup.in | Crystal | WHLU4283466 | 40 FT | NA | NA | NA | NA | READY FOR dispatch | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC041 | [7 empty] | NA
DEC076 | 2024-12-31 17:33 | service@crystalgroup.in | Crystal | TRLU8190780 | na | na | NA | NA | NA | already dispatched | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC076 | [7 empty] | RAMIZ | No
DEC074 | 2024-12-31 17:37 | service@crystalgroup.in | Crystal | GLDU0894019 | 40 ft | na | NA | NA | NA | Ready for dispatch | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC074 | [7 empty] | RAMIZ | No
DEC079 | 2024-12-31 17:41 | service@crystalgroup.in | Crystal | HNKU5111970 | 40 ft | na | NA | NA | NA | panting & logo balance | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC079 | [7 empty] | RAMIZ | No
DEC080 | 2024-12-31 17:45 | service@crystalgroup.in | Crystal | HNKU5113762 | 40 FT | NA | NA | NA | NA | Already dispatched | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC080 | [7 empty] | RAMIZ | No
DEC086 | 2024-12-31 17:51 | service@crystalgroup.in | Divis Labs | DCUNIT09 | 40 ft | carrier thine line | SERVICE-ON CALL | SALE | CHARGEABLE | evaporator fan motor noise both | need to replace both evaporator fan motors . | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC086 | [7 empty] | RAMIZ | No
DEC062 | 2024-12-31 18:24 | service@crystalgroup.in | Crystal | CGMU2989060 | 20 ft | carrier thine line | REPAIR | STOCK | NA | Controller, Contactor, Key Pad, Power Plug, Curtains, EVP motor defectives | na | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC062 | Carrier - Thinline | Thinline | LSM 60197754 | LSM60197754 |  |  | JSGA622180043 | RAMIZ | No
DEC078 | 2024-12-31 18:28 | service@crystalgroup.in | Crystal | GESU9440432 | 40 ft | carrier elight line | REPAIR | STOCK | FOC | ISO Plug,compressor elight line , controller ,disply , filter drier, gas r134a 5 kgs n2 | na | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC078 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | RAMIZ | No
DEC065 | 2024-12-31 18:32 | service@crystalgroup.in | Crystal | CICU3876591 | 10 ft blast | thermoking mp 4000 | REPAIR | STOCK | FOC | ISO plug | need to fix iso plug | YES | yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC065 | Thermoking | Magnum + | E0GM030860 | ABC782800322010299 | ABC782900321510393 | Brand New |  | RAMIZ | No
DEC081 | 2024-12-31 18:37 | service@crystalgroup.in | Crystal | Painting touch up and cleaning | 20 FT | NA | REPAIR | STOCK | NA | Painting touch up and cleaning | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC081 | [7 empty] | RAMIZ | No
DEC067 | 2024-12-31 18:41 | service@crystalgroup.in | Crystal | GRMU3707485 | 20 ft blast | daikin | REPAIR | STOCK | FOC | Power plug required for unit 1 & unit 3 and curtain missing / ONE UNIT REMOVED & FIX NEPAL | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC067 | Daikin |  |  |  |  | used |  | RAMIZ | No
DEC070 | 2024-12-31 18:44 | service@crystalgroup.in | Crystal | TITU7263521 | 10 ft | daikin | REPAIR | STOCK | FOC | battery missing, keypad damage, leakage found, cable missing, ISO plug is rusted, Complete unit need to be replace | need to replaced full unit | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC070 | Daikin |  |  |  |  | brand New | JSGA622180055 | RAMIZ | No
DEC084 | 2024-12-31 18:49 | service@crystalgroup.in | RELIANCE | CICU2779909 | 10 ft blast | thermoking mp 4000 | SERVICE-ON CALL | LEASE | FOC | PCM not freeze in expected time . | the reefer unit working sound & good condition . Need a heat lode calculation & explanation | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC084 | Thermoking | Magnum Plus | E0GM030263 | ABC782800322010201 |  | BrandNew |  | RAMIZ | No
DEC073 | 2025-01-04 15:17 | mum.depot@crystalgroup.in | Crystal | TRIU8836134 | 40FT | NA | REPAIR | STOCK | FOC | MAIN UNIT MISSING, OUTSIDE L/R PANEL PUSHED OUT | UNIT REQUIRED, NEED TO REPAIR SIDE PANELS | UNIT | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC073 | Carrier |  |  |  |  | Used |  | RAMIZ | No
DEC071 | 2025-01-04 15:21 | mum.depot@crystalgroup.in | Crystal | HDMU5542114 | 40FT | CARRIER THINLINE | REPAIR | STOCK | FOC | FLOOR REPAIRING DONE, PTI DONE BY RAMEZ, PAINTING BALANCE | NEED TO PAINT | NA | No |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC071 | Carrier | Thineline | [5 empty] | YARD TECHNICIAN | No
DEC069 | 2025-01-04 15:34 | mum.depot@crystalgroup.in | Crystal | TCLU1911479 | 20FT | DAIKIN | REPAIR | STOCK | FOC | SHEET KEY DAMAGE, ISO PLUG MISSING, | SHEET KEY AND ISO NEED TO CHANGE | SHEET KEY AND ISO PLUG | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC069 | DAIKIN LXE |  |  |  |  | USed |  | RAMIZ | No
DEC066 | 2025-01-04 15:39 | mum.depot@crystalgroup.in | Crystal | CICU1938924 | 20FT | THERMOKING MP4000 | REPAIR | STOCK | FOC | ISO PLUG MISSING | NEED TO FIX ISO PLUG | ISO PLUG | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC066 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | RAMIZ | No
DEC068 | 2025-01-04 15:52 | mum.depot@crystalgroup.in | Crystal | HDMU5221979 | 20FT | DAIKIN | REPAIR | STOCK | FOC | CONTROLLER TAKEN FOR SITE BY VIRENDRA,ISO PLUG MISSING, CABLE SHORT | NEED TO FIX CONTROLLER, ISO PLUG REQUIRED AND NEED TO ADD 8 METER POWER CABLE | CONTOLLER DCOS III F, ISO PLUG AND powe cabe 4 CORE CARE 8meters | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC068 | Daikin |  |  |  |  | USed |  | RAMIZ | No
JAN002/25 | 2025-01-04 18:02 | crm@crystalgroup.in | DR REDDY CTO 06 | KKFU6712802 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | Preventive Maintenance | Need to replace Condenser Coil | Carrier Thinline Condenser Coil 1 No Liquid Filter 1 No Refrigerant Gas - R134a 5.2 kgs Nitrogen 1 No Brazing Torch Heavy Duty 1 No Vaccum Pump RX-6D Double Stage (11.8CFM) 1 No | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN002 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | SHAHBUDDIN
JAN004/25 | 2025-01-07 11:55 | service@crystalgroup.in | AMUL GOREGAON MUMBAI | CXRU1056669 | 40 | daikin zestia | SERVICE-AT SITE | LEASE | AMC | unit tripped during normal operation due to MCB defective (32 amps) main cable joint burnt & condenser coil dirty | replaced new 63 AMPS & cable splicing done & cleaned condenser coil with fresh water | EVP MOTOR BEARING | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN004 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | RAMIZ
JAN003/25 | 2025-01-07 12:12 | service@crystalgroup.in | Crystal | CXRU1031758 | 40 ft | 40 ft reefer | REPAIR | STOCK | FOC | R/side Evaporator motor noise | need to replaced bearing both bearing | 2 nos bearing | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN003 | Daikin LXE | Daikin LXE |  |  |  | Used |  | SHAHBUDDIN
JAN005/25 | 2025-01-07 13:29 | service@crystalgroup.in | AMUL GOREGAON MUMBAI | GESU9440129 | 40 ft | carrier elight line | SERVICE-AT SITE | LEASE | AMC | unit tripped during normal operation due to MCB defective (32 amps)& condenser coil dirty | replaced new 63 AMPS & cleaned condenser coil with fresh water . | na | No |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN005 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ
JAN006/25 | 2025-01-07 14:34 | service@crystalgroup.in | Crystal | CXRU1032775 | 40 ft | Daikin | REPAIR | STOCK | FOC | leakage from compressor body bottom side | need to replaced a new compressor | scroll compressor Dakin | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN006 | [7 empty] | SHAHBUDDIN
JAN008/25 | 2025-01-07 19:00 | service@crystalgroup.in | Crystal | CICU2094068 | 10 FT | MP 4000 THERMOKING | REPAIR | STOCK | FOC | DISPLY DEFECTIVE & ISOPLUG MISSIN & MAN TRAP MISSING & STRIP CURTAN 13 NO DAMAGED , FLOOR NORMAL RISTED | FOR FOUTURE PROCRESS NEED TO FIX DISPLY & ISOPLUG | DISPLY IN UNDER WARRENTY | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN008 | Thermoking | Magnum Plus | E0GM029715 | ABC782800321410498 |  | BrandNew |  | RAMIZ
DEC063 | 2025-01-08 13:28 | service@crystalgroup.in | Crystal | TRIU6681671 | 20 ft reefer | carrier thine line | REPAIR | STOCK | FOC | Power plug and curtain missing, N2 Gas, EVP Motor, SM Valve, Contactor, Filter drier, ISO Plug, R134 A gas. | For future process need to fix those spares. | Power plug , EVP Motor, SM Valve, Contactor, Filter drier, ISO Plug, R134 A gas 5KGS . | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC063 | Carrier - Transcold | Transcold | NSG 60383850 | KE 04959025 |  | Used |  | SHAHBUDDIN
DEC064 | 2025-01-08 13:34 | service@crystalgroup.in | Crystal | CCLU1030700 | 20 ft | carrier thine line | REPAIR | STOCK | FOC | Power plug and curtain missing, EVP motor missing, controller damage, Condenser motor bearing need to replace. | For future process need to fix those spares. | ISO plug , EVP motor , controller ML 3, Condenser motor BEARING 2 NOS 6205 . | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC064 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN
JAN001/25 | 2025-01-09 11:54 | service@crystalgroup.in | Reliance Wagholi | PCIU6015055 | 40 ft | Daikin | SERVICE-ON CALL | LEASE | FOC | unit trapping during compressor operation. | as par the customer check all cable connection is ok power supply voltage stable still same condition . need a visit | suspected =1) discharge sensor,2) controller iiiD , 3 )temperature sensor & 4) pt & ct bord , 5)compressor contactor 30 amps | SUSPECTED | loose connection of incoming main power supply & old cable splicing after few hours getting heat then power supply or compressor motor winding over heat reduce & tripped . / suspected discharge sensor or controller or pcct & compressor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN001 | Daikin | Daikin | NA | NA | NA | used |  | RAMIZ | Yes
JAN009/25 | 2025-01-09 14:43 | service@crystalgroup.in | Lupin Ltd | CCLU1036859 | 20 FT | CARRIER THINE LINE | SERVICE-AT SITE | LEASE | FOC | Unit making noise | Need to replace both bearing | 2 nos bearing | Yes | Due to condenser fan motor bearing rusted. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN009 | Carrier |  |  |  |  | Used | JSGA623040314 | SHUBHAM | Yes
JAN010/25 | 2025-01-09 16:10 | crm@crystalgroup.in | Dr Reddy Ct 06 | CXRU1033616 | 40 FT STD | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintenance | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN010 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | SHAHBUDDIN | Yes
JAN007/25 | 2025-01-09 18:53 | service@crystalgroup.in | RELIANCE | TRIU6681440 | 20 ft reefer dual machine | carrier thine line | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Removed ice with hot water . condenser coil clean with fresh water . currently the reefer unit working normal & temperature pulling down to the set point . The reefer unit still under observation . | NA | No | ice foundation on t bar floor , air circulation blockby pcm pad . | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN007 | Carrier - Transcold | Transcold |  |  |  | Used |  | SHUBHAM | Yes
JAN012/25 | 2025-01-10 13:10 | operation@crystalgroup.in | Zepto | TITU9928040 | 40-REEFER | THERMOKING MP4000 | REPAIR | LEASE | FOC | LEAKAGE FOUND NEAR COMRESSOR | N2 TEST & BRAZING NEED TO BE DONE | SILVER BRAZING ROD, NITROGEN ,OXYGEN, R404a, VACUUM PUMP,BRAZING SET | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN012 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | RAMIZ & SHUBHAM | Yes
JAN013/25 | 2025-01-13 10:25 | service@crystalgroup.in | Swadesh milk products pvt ltd | GESU9290991 | 40 ft | carrier thine line | SERVICE-ON CALL | SALE | CHARGEABLE | compressor contactor burnt & controller defective ml3 | replaced compressor contactor & found the controller not responding | yes | Yes | due to compressor contactor coil burnt controller got defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN013 | Carrier | Thineline |  |  |  | Used |  | SHAHBUDDIN | Yes
SEP033 | 2025-01-14 16:10 | crm@crystalgroup.in | UPS | SJKU4000110 | 40 FT | Thermo King | SERVICE-AT SITE | LEASE | FOC | Installation | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP033 | Thermoking | MP-4000 |  |  |  | Brand New |  | SHAHBUDDIN | Yes
SEP031 | 2025-01-14 16:15 | crm@crystalgroup.in | Cipla Unit 3 | TITU9231009 | NA | DAIKIN | NA | NA | NA | REPAIR | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP031 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | NA | Yes
SEP030 | 2025-01-14 16:18 | crm@crystalgroup.in | PI Industry | CXRU1035856 |  | Daikin | NA | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP030 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used |  | NA | No
SEP029 | 2025-01-14 16:24 | crm@crystalgroup.in | Laurus Unit 3 | ARCU4530675 |  | Daikin | NA | NA | NA | Temp Issue | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP029 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used |  | SHAHBUDDIN | No
SEP028 | 2025-01-14 16:29 | crm@crystalgroup.in | Jubilant Consumer | CXRU1030387 |  | Daikin | NA | NA | NA | Unit noisy | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP028 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | SHAHBUDDIN | No
SEP027 | 2025-01-14 16:32 | crm@crystalgroup.in | Qwik Supply | NYKU7931452 |  | Carrier | NA | NA | NA | Temp Issue | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP027 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | SHAHBUDDIN | No
SEP026 | 2025-01-14 16:34 | crm@crystalgroup.in | ITC | PCIU6010243 |  | Daikin | NA | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP026 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | VIRENDRA | Yes
SEP025 | 2025-01-14 16:36 | crm@crystalgroup.in | Chemplast Sanmar Limited | TITU9930222 |  | Thermo King | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP025 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | VIRENDRA | Yes
SEP024 | 2025-01-14 16:39 | crm@crystalgroup.in | Dr Reddy Biotechnology | TITU9930074 |  | THERMO KING MP4000 | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP024 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes
SEP023 | 2025-01-14 16:41 | crm@crystalgroup.in | Dr Reddy Biotechnology | TITU9930114 |  | TK MP 4000 | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP023 | Thermoking | MP-4000 | 14E219055 | EOG1000667 |  |  | JSGA622180063 ¦ JSGA622180011 | VIRENDRA | Yes
SEP021 | 2025-01-14 16:43 | crm@crystalgroup.in | DSV | TITU9930006 |  | TK MP 4000 | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP021 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | VIRENDRA | Yes
SEP020 | 2025-01-14 16:47 | crm@crystalgroup.in | Divis Lab | CONT-3 |  | Carrier | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP020 | [7 empty] | VIRENDRA | Yes
SEP019 | 2025-01-14 16:52 | crm@crystalgroup.in | Qwik Supply | CGMU2988654 |  | Carrier | NA | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP019 | Carrier - Thinline | Thinline | 2907L50458 | LSM60197481 |  | Used |  | NA | Yes
SEP015 | 2025-01-14 16:54 | crm@crystalgroup.in | T 90 | CICU3876523 | 10FT | Thermo King | SERVICE-ON CALL | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No
SEP018 | 2025-01-14 16:57 | crm@crystalgroup.in | Siemens | PRJU4958724 | 40 FT | Carrier | SERVICE-ON CALL | NA | NA | Temperature Issues | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP018 | [7 empty] | SHAHBUDDIN | No
SEP014 | 2025-01-14 17:03 | crm@crystalgroup.in | Dr Reddy FTO-7 | TITU9930074 | 40 FT | Thermo King | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP014 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes
SEP013 | 2025-01-14 17:09 | crm@crystalgroup.in | Dr Reddy FTO-7 | TRIU6632949 |  | Carrier | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP013 | Carrier - Thinline | Thinline | 1808L295 | MS60317785 |  | Used |  | VIRENDRA | Yes
SEP012 | 2025-01-14 17:11 | crm@crystalgroup.in | Dr Reddy FTO-7 | KKFU6712802 |  | Carrier | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP012 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | VIRENDRA | Yes
SEP011 | 2025-01-14 17:13 | crm@crystalgroup.in | Dr Reddy FTO-7 | CXRU1033616 | 40 FT | Daikin | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP011 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | VIRENDRA | Yes
SEP010 | 2025-01-14 17:19 | crm@crystalgroup.in | GMR Hydrabad Air cargo | SJKU4000104 |  | TK MP 4000 | SERVICE-AT SITE | NA | NA | Display & Power | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP010 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN | Yes
SEP009 | 2025-01-14 17:21 | crm@crystalgroup.in | Dr Reddy CTO5 | CXRU1032564 |  | Daikin | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP009 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN | Yes
SEP008 | 2025-01-14 17:26 | crm@crystalgroup.in | Dr Reddy CTO5 | GSOU6384240 |  | NA | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP008 | Carrier | Carrier Thinline | SSB60749120 |  | ML-3 | used | JSGA622340472 | SHAHBUDDIN | Yes
SEP007 | 2025-01-14 17:28 | crm@crystalgroup.in | Dr Reddy CTO5 | CXRU1045896 |  | Daikin | PREVENTIVE MAINTENANCE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP007 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | SHAHBUDDIN | Yes
SEP006 | 2025-01-14 17:30 | crm@crystalgroup.in | Dr Reddy CTO5 | GSOU6384153 |  | NA | SERVICE-AT SITE | NA | NA | NA | NA | NA | NA | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP006 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN | Yes
JAN016/25 | 2025-01-15 18:18 | operation@crystalgroup.in | CRYSTAL YARD | CRIU2151790 | 20FT ISO TANK | NA | REPAIR | STOCK | FOC | TANK PATCH WORK | 3RD PART WORK | NA | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN016 | [7 empty] | MASSK | No
JUL053 | 2025-01-18 16:49 | crm@crystalgroup.in | Oriental Yeast | PCIU6008014 | 40FT | Daikin | REPAIR | SALE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL053 | Daikin | Daikin | AOO4920 |  |  | Used |  | RAMIZ
JUL056 | 2025-01-18 17:22 | crm@crystalgroup.in | Lupin - Bhiwandi | CXRU1030427 | 40FT | Hetero Unit 3 | SERVICE-AT SITE | LEASE | CHARGEABLE | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL056 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | VIRENDRA
AUG022 | 2025-01-18 17:35 | crm@crystalgroup.in | ITC Ltd | PCIU6010243 | 40FT | Thermo King | SERVICE-ON CALL | LEASE | FOC | Showing Alarm F803 | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG022 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | UMESH
JAN017/25 | 2025-01-20 14:51 | service@crystalgroup.in | Reliance Wagholi | CICU1442240 | 10'' | Thermo King MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM Service | PM Service Done |  | No | PM Service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN017 | Thermoking | MP-4000 |  |  |  | Brand New |  | SHAHBUDDIN | No
JAN014/25 | 2025-01-20 17:18 | service@crystalgroup.in | Crystal Yard | CICU1442256 | 40" | Thermo king MP 4000 | MACHINE INSPECTION | STOCK | FOC | 3 Nos Display Blur ,Power Plug Missing ,Logo sticker damaged ,Display door damaged | Need to replace Display assembly ,Power Plug Assembly and display door assembly | Display TK 4000 3 Nos ,Power Plug TK 4000 2 Nos ,Display Door TK 4000 1 Nos ,Logo Sticker TK 4000 1 Nos | Yes | Door Damaged Due to misused , Display issue need to study | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN014 | Thermoking | EOG5003933 | EOG5003933 | 220916, 3.29.00 |  | brand New |  | SHAHBUDDIN | Yes
JAN018/25 | 2025-01-20 17:28 | service@crystalgroup.in | Shah TC | CXRU1186451 | 40" | Daikin | SERVICE-ON CALL | LEASE | FOC | Unit tripping off frequently with Alarm E101 | Temporarily reset | Daikin TXV coil old Model 1 Nos , Silicon 1 Nos | Yes | Suspected TXV coil | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN018 | Daikin | LXE10E136F2 | M002046 | K12102057718 | DECOS 3F 2557 / 1 | Used | JSGA622180066 | Rajkumar | Yes
JAN019/25 | 2025-01-21 18:15 | service@crystalgroup.in | Reliance Hapur | CXRU1043912 | 40' | Daikin | SERVICE-ON CALL | LEASE | FOC | Customer required Mantrap and Light | Na | Mantrap ,Light | Yes | New Requirement | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN019 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | RAMIZ | Yes
JAN020/25 | 2025-01-22 11:05 | service@crystalgroup.in | Reliance Bhopal | MYRU4515188 | 40' | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Noisy and HPT pressure Low | Need to Inspect Compressor ,Expansion Valve, ISV and ESV valve ,Liquid Valve,N2 Test, Vacuum ,Brizing Rod,R134A | Compressor Expansion Valve ISV and ESV Valve Liquated Valve Brazing Rod R 134A | Yes | Due to compressor leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN020 | Daikin | Daikin |  |  |  | Used |  | THIRD PARTY LOCAL | Yes
JAN021/25 | 2025-01-22 15:29 | service@crystalgroup.in | Reliance Kamaspura | TRIU6618391 | 20' | Carrier Tinline | SERVICE-ON CALL | LEASE | FOC | ,Container showing Alarm AASA,DA70 ,AA56 ,AA26 | Need to Replace Supply and Return Sensor ,Ambient Sensor | Supply Sensor 2 Nos Return Sensor 2 Nos Ambient Sensor Spare 1 Nos | Yes | Return and Supply Sensor Failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN021 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA | Yes
JAN024/25 | 2025-01-22 16:25 | operation@crystalgroup.in | CRYSTAL | CRLU3181686 | 20-REEFER | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | Fabrication of Internal Baffle Plate | MASSK VENDOR WORK |  | 3RD PARTY VENDOR | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN024 | Daikin | Daikin |  |  |  | Used |  | MASSK | No
JAN025/25 | 2025-01-22 18:24 | service@crystalgroup.in | Siemens | TRIU6617646 | 20' | Carrier | SERVICE-AT SITE | SALE | AMC | condenser coil leakage to brazing | Need to carry out Brazing of condenser coil, ,N2 test ,Need to replace EVP motor | Brazing Set 1 Nos LPG 1 Nos O2 1 Nos N2 1 Nos R134A 5 KG EVP Motor 1 Nos Brazing Rod 2 Nos Vacuum Pump 1 Nos | Yes | Malfunctioning | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN025 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | SHAHBUDDIN | Yes
JAN022/25 | 2025-01-23 10:30 | crm@crystalgroup.in | Shah TC | CXRU11864512 | 40 FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN022 | [7 empty] | Rajkumar | Yes
JAN023/25 | 2025-01-23 10:35 | crm@crystalgroup.in | Shah TC | CAIU5404270 | 40 FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN023 | DAikin |  |  |  |  | Refurbished |  | Rajkumar | Yes
JAN011/25 | 2025-01-23 11:02 | crm@crystalgroup.in | Lupin Ltd | TRIU6681082 | 20 FT | Carrier | SERVICE-AT SITE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN011 | [7 empty] | SHUBHAM | Yes
JAN027/25 | 2025-01-25 12:48 | service@crystalgroup.in | Dr Reddy CTO 5 | CXRU1045896 | 40' | Daikin | SERVICE-AT SITE | LEASE | FOC | on Operation of compressor contactor ,electricity is getting tripped due to faulty compressor | Need to replace Compressor Compressor contactor (suspected) PCC1 and PCC2 contactor (suspected) N2 Test Vacuum | compressor 01 Nos compressor contactor 01 Nos PCC1 and PCC2 01 Nos Gauge set 0 Nos R134A 5KG | Yes | Compressor and contactor Faulty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN027 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | VIRENDRA | Yes
JAN029/25 | 2025-01-27 12:51 | service@crystalgroup.in | Laurus unit 2 | PRGU4958724 | 40' | Carrier Thinline | SERVICE-AT SITE | LEASE | FOC | Alarm AA19.AA15 | Need to Replace Filter Dryer | Filter Dryer | Yes | Filter Dryer Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN029 | Carrier - Thinline |  |  |  |  | Used |  | THIRD PARTY LOCAL | Yes
JAN028/25 | 2025-01-27 15:48 | service@crystalgroup.in | Laurus unit 2 | GESU9454776 | 40' | Carrier | SERVICE-AT SITE | LEASE | FOC | Found Alarm code AA25 condenser motor capacitor defective | Need to Replace Motor Capacitor | Condenser motor Capacitor 20mfd/370 V | Yes | condenser motor Capacitor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN028 | Carrier | Thineline |  |  |  | Used |  | THIRD PARTY LOCAL | Yes
JAN015/25 | 2025-01-27 17:12 | crm@crystalgroup.in | RELIANCE | CXRU1040322 | 40FT | Daikin | SERVICE-ON CALL | LEASE | FOC | Electric current flowing issue | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN015 | [7 empty] | THIRD PARTY LOCAL | Yes
JAN030/25 | 2025-01-28 11:26 | service@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40' | Blue Star | SERVICE-AT SITE | LEASE | FOC | Low cooling Issue | Need to Refill Gas | Required Gas R22 1kg | Yes | Gas is Low | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN030 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | THIRD PARTY LOCAL | Yes
JAN033/25 | 2025-01-28 13:04 | service@crystalgroup.in | ASPIRO PHARMA | CGMU2991560 | 20' dual Unit | Carrier | SERVICE-AT SITE | LEASE | FOC | Evaporator Motor Over heat and Noisy and ML3 Controller | Need to Replace EVP Motor single phase(Carrier) | EVP Motor single phase(Carrier) 1 Nos Controller Ml3 Thinline | Yes | EVP motor Fail | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN033 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN | Yes
JAN026/25 | 2025-01-29 09:37 | service@crystalgroup.in | Crystal Yard | AKA0004025 | Genset Thermoking | Thermoking | SERVICE-AT SITE | STOCK | FOC | Battery Not Available | Need to Purchase new Battery 12V 180 AH | Battery 12V 180 AH | Yes | Battery Not Available | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN026 | [7 empty] | SHAHBUDDIN | No
JAN034/25 | 2025-01-29 18:23 | mum.depot@crystalgroup.in | Apitoria Pharma | BMOU9787239 | 40FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE NOT REACHED AT SET POINT | NEED TO CHECK LEAKAGE AND ADD GAS.NEED TO CLEAN CONDENSER COIL. | NA |  | SUSPECTED GAS LEAK | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN034 | Daikin |  |  |  |  | Refurbished |  | SHAHBUDDIN | Yes
JAN036/25 | 2025-01-31 14:21 | service@crystalgroup.in | Reliance Bhopal | CRLU6220410 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintenance | Technician to be arranged for Preventive Maintenance | NA | No | Preventive Maintainence | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN036 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA622170434 | VIRENDRA | Yes
JAN037/25 | 2025-01-31 14:24 | service@crystalgroup.in | Reliance Bhopal | CICU3876544 | 10FT | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintainece | Schedule Engg Visit for M |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN037 | Thermoking | Magnum Plus | E0GM030963 | 0322GM030961 | ABC782900321510545 | Brand New |  | VIRENDRA | Yes
JAN040/25 | 2025-02-03 12:34 | operation@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | REPAIR AND MAINTENANCE | - |  | No | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN040 | DAikin |  |  |  |  | Used | JSGA622340482 | SHAHBUDDIN | Yes
JAN054/25 | 2025-02-03 12:47 | operation@crystalgroup.in | Qwik Supply | CICU2779920 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN054 | Thermoking | Magnum Plus | E0GM030270 | ABC782800322010477 |  | BrandNew |  | SHAHBUDDIN | Yes
JAN041/25 | 2025-02-04 10:48 | crm@crystalgroup.in | Divis Labs | CONT 1 | 40 FT | CARRIER-THINLINE | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN041 | [7 empty] | SHAHBUDDIN | Yes
JAN042/25 | 2025-02-04 10:53 | crm@crystalgroup.in | Qwik Supply | CICU1799177 | 10FT | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN042 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 |  | BRand NEW | JSGA622180057 | SHAHBUDDIN | Yes
JAN045/25 | 2025-02-04 11:22 | crm@crystalgroup.in | DSV Solutions | TITU8258978 | 20FT | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN045 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN | Yes
JAN046/25 | 2025-02-04 11:49 | crm@crystalgroup.in | Softbox | GRMU3707470 | 20FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN046 | Daikin |  |  |  |  | used |  | SHAHBUDDIN | Yes
JAN047/25 | 2025-02-04 11:51 | crm@crystalgroup.in | Softbox | TITU8257288 | 20FT | Thermoking MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN047 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | SHAHBUDDIN | Yes
JAN049/25 | 2025-02-04 11:53 | crm@crystalgroup.in | DHL Supply Chain | DFOU6120281 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN049 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | SHAHBUDDIN | Yes
JAN050/25 | 2025-02-04 11:55 | crm@crystalgroup.in | Hetero Unit 3 | PCIU6016370 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN050 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | SHAHBUDDIN | Yes
JAN051/25 | 2025-02-04 12:03 | crm@crystalgroup.in | Hetero Unit 3 | APRU5091041 | 40FT | Carrier-Primeline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN051 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | SHAHBUDDIN | Yes
JAN052/25 | 2025-02-04 12:12 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1026520 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN052 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | SHAHBUDDIN | Yes
JAN053/25 | 2025-02-04 12:13 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1030427 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN053 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | SHAHBUDDIN | Yes
JAN056/25 | 2025-02-04 12:20 | crm@crystalgroup.in | Dr Reddy CTO 5 | GSOU6384240 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN056 | Carrier | Carrier Thinline | SSB60749120 |  | ML-3 | used | JSGA622340472 | SHAHBUDDIN | Yes
JAN057/25 | 2025-02-04 12:25 | crm@crystalgroup.in | Dr Reddy CTO 5 | GSOU6384153 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN057 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN | Yes
JAN058/25 | 2025-02-04 12:29 | crm@crystalgroup.in | Dr Reddy CTO 5 | CXRU1032564 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN058 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN | Yes
JAN059/25 | 2025-02-04 12:32 | crm@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN059 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | SHAHBUDDIN | Yes
JAN060/25 | 2025-02-04 12:33 | crm@crystalgroup.in | Hetero Unit 5 | SUDU6218004 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN060 | Carrier-Primeline | Primeline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | SHAHBUDDIN | Yes
JAN061/25 | 2025-02-04 12:35 | crm@crystalgroup.in | Hetero Unit 5 | CXRU1186425 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN061 | DAikin | LXE10E136F2 | M002116 | K31511151600 | DECOS 3F 2557 / 1 | Used | JSGA621320194 | SHAHBUDDIN | Yes
JAN062/25 | 2025-02-04 12:37 | crm@crystalgroup.in | Hetero Unit 5 | CXRU1186467 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN062 | Daikin | LXE10E136F2 | M002118 | K31503145677 | DECOS 3F 2557 / 12 | Used | JSGA622180060 | SHAHBUDDIN | Yes
FEB001/25 | 2025-02-04 12:39 | crm@crystalgroup.in | NSR Trader | TCLU1112683 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB001 | [7 empty] | SHUBHAM | Yes
FEB002/25 | 2025-02-04 12:41 | crm@crystalgroup.in | LAURAS UNIT 1 | APRU5000210 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB002 | Carrier - Thinline | Thinline | 2594J02559 | GGCR80067211 |  | Refurbished |  | SHUBHAM | Yes
FEB003/25 | 2025-02-04 12:44 | crm@crystalgroup.in | LAURAS UNIT 1 | PCIU6006639 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB003 | Daikin |  |  |  |  | used |  | SHUBHAM | Yes
FEB004/25 | 2025-02-04 12:47 | crm@crystalgroup.in | Lauras Unit 3 | KKFU6711724 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB004 | Carrier - Thinline | Thinline | 4515UD3741 | LSX60253415 |  | used |  | SHUBHAM | Yes
FEB005/25 | 2025-02-04 12:49 | crm@crystalgroup.in | Lauras Unit 3 | MYRU4519115 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB005 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHUBHAM | Yes
FEB008/25 | 2025-02-05 14:45 | technician@crystalgroup.in | DR. REDDY BIOLOGICS BACHUPALLY | TITU9930114 | 40 | TK MP 4000 | SERVICE-ON CALL | LEASE | FOC | FOUND COMPRESSOR OVER HEAT & NOISY. | NEED TO REPLACED COMPRESSOR / FILTER DRIER & VACUM WITH GAS R404 | THERMOKING COMPRESSOR/ FILTER DRIER/ GASKET DIS WITH O- RING SUC & GAS R 404 5 KG/ VACUM PUMP AND NITOGEN FOR LEAK TEST | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB008 | TK MP 4009 | TK MP 4009 | NA | NA | NA | USED | NA | SHAHBUDDIN | No
JAN035/25 | 2025-02-06 12:18 | service@crystalgroup.in | Laurus Synthesis Pvt Ltd Unit2 | TRIU6680994 | 40 ft | carrier | SERVICE-AT SITE | LEASE | FOC | condenser fan motor capacitor defective | removed old capacitor & need to fix new one 15 uf | capacitor 15 UF (440 &50 to 60 HZ ,stating capacitor ) | Yes | getting old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN035 | man unit | thine line | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
JAN038/25 | 2025-02-06 12:30 | service@crystalgroup.in | Navin fluorine Dhej | CCLU1031878 | 20-REEFER | CARRIER THINELINE | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | CLEAN CONDENSER COIL WITH FRESH WATER | NA | No | CONDENSE COIL DIRTY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN038 | main unit | CARRIER THINELINE | NA | NA | NA | USED | NA | RAJESH | No
JAN032/25 | 2025-02-06 14:44 | service@crystalgroup.in | REALIANCE | CXRU1042578 | 40 reefer | daikin | SERVICE-AT SITE | LEASE | FOC | found oil satin from DPR NRV | need to charge 4 can R134a & (1.8 kgs) | Gas R134a 1.8 kgs | Yes | leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN032 | main unit | daikin decose iiif | OK | OK | OK | Used | OK | THIRD PARTY LOCAL | Yes
FEB006/25 | 2025-02-06 14:55 | service@crystalgroup.in | JUBILIENT | TRIU6687350 | 20 ft reefer | carrier | SERVICE-ON CALL | LEASE | FOC | temperature not pull down to the set point - 25C | clean condenser coil with fresh water | no | No | condenser coil to much dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB006 | main unit | carrier prime line | ok | ok | ok | USED | NA | RAMIZ | No
FEB010/25 | 2025-02-07 09:59 | service@crystalgroup.in | Crystal Dhulagarh | CRLU3179858 | 40' | NA | SERVICE-AT SITE | LEASE | FOC | Need to Carry out Painting | NA | Blue Paint 5002 SR Thinner | Yes | Need to deploy at New Site | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB010 | NA | NA | NA | NA | NA | Used | NA | THIRD PARTY LOCAL | No
FEB009/25 | 2025-02-07 10:01 | service@crystalgroup.in | Crystal Dhulagarh | TRLU5253890 | 40' | NA | SERVICE-AT SITE | LEASE | FOC | Need to Carry Out Painting | NA | Blue Paint 5002 SR Thinner and Primer | Yes | Need to deploy on new Site | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB009 | NA | NA | NA | NA | NA | Used | NA | THIRD PARTY LOCAL | No
FEB020/25 | 2025-02-07 15:42 | service@crystalgroup.in | Crystal Yard | CXRU1034382 | 40FT STD RF | Thermoking | SERVICE-AT SITE | LEASE | FOC | Modification in container | Need to Cut Container body and need to reinstall same | NA | No | Need to Install In New Order with 2 Unit | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB020 | Daikin LXE | Daikin LXE | NA | DECOSIII/2551/1 | ABC782900321510023 | Used | NA | THIRD PARTY LOCAL | No
FEB019/25 | 2025-02-07 16:00 | service@crystalgroup.in | QWIK SUPPLY | TRIU8850831 | 40FT STD RF | carrier thine line | SERVICE-ON CALL | LEASE | FOC | suspected less gas , compressor heavy noise . | check on VC / need technician visit | gas R134a 4 kgs , filter drier | Yes | After find leakage we can explant | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB019 | Carrier - Thinline | Thinline | ok | ok | ok | Used | JSGA622180048 | VIRENDRA | Yes
FEB018/25 | 2025-02-07 16:06 | crm@crystalgroup.in | Divis Labs | CONT 9 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB018 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB017/25 | 2025-02-07 16:07 | crm@crystalgroup.in | Divis Labs | CONT 8 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB017 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB016/25 | 2025-02-07 16:10 | crm@crystalgroup.in | Divis Labs | CONT 7 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB016 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB015/25 | 2025-02-07 16:13 | crm@crystalgroup.in | Divis Labs | CONT 6 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB015 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB014/25 | 2025-02-07 16:15 | crm@crystalgroup.in | Divis Labs | CONT 5 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB014 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB013/25 | 2025-02-07 16:18 | crm@crystalgroup.in | Divis Labs | CONT 4 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB013 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB012/25 | 2025-02-07 16:25 | crm@crystalgroup.in | Divis Labs | CONT 3 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB012 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB011/25 | 2025-02-07 16:27 | crm@crystalgroup.in | Divis Labs | CONT 2 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB011 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB021/25 | 2025-02-08 14:40 | service@crystalgroup.in | Crystal Yard | SEGU9511192 | 40FT STD RF | CARRIER THINELINE | SERVICE-AT SITE | LEASE | FOC | Additional reefer machine , Ante room for QAS-5449A/24-25 | Need to Cut Container body and need to reinstall same | NA | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB021 | Carrier | Thinline | Na | NA | NA | Used | NA | Rajkumar | Yes
FEB023/25 | 2025-02-09 17:21 | operation@crystalgroup.in | HETERO PLASMA | MYRU4500887 | 40FT STD RF | DAIKIN | MACHINE INSPECTION | LEASE | FOC | NO GAS IN SYSTEM ,COMMPRESSOR NOT PERFORMING THE DISCHARGE PRESSURE SUSPECTED DAMAGED INTERNALLY | REPLACE COMPRESSOR |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB023 | Daikin | Daikin | NOT AVAILABLE | LXE10E136A | DECOS 3E | Refurbished | NOT AVAABLE | SHAHBUDDIN | Yes
FEB024/25 | 2025-02-10 16:57 | crm@crystalgroup.in | Reliance - Jamnagar | CGMU2991679 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB024 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | Raj Kumar | Yes
FEB035/25 | 2025-02-12 12:55 | operation@crystalgroup.in | Reliance Taloja | TRIU6681440 | 20FT STD RF - Dual Machine Carrier | Carrier Thinline | REPAIR | LEASE | FOC | filter drier chock, heater failure, alarm aa60, aa61 | . |  | Yes | . | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB035 | Carrier - Transcold | Transcold | . | . | . | Used | . | VIRENDRA | Yes
FEB022/25 | 2025-02-12 16:13 | crm@crystalgroup.in | Navin Fluorine | CCLU1031878 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | Gas top up | Required Gas top up R134 | Gas top up R134 | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB022 | Carrier - Thinline | Thinline | NA | NA | NA | Used | NA | Rajkumar | Yes
FEB037/25 | 2025-02-12 17:47 | service@crystalgroup.in | Reliance Kerala | CICU2094089 | 10 ft reefer | TK MP 4000 | SERVICE-AT SITE | LEASE | FOC | Compressor Contactor Burn | Need to Replace Compressor Contactor 25 A | 1) TK Compressor Contactor 25 A 1 Nos 2)Mantrap Hooter 1 Nos 3)Transformer 1 Nos | Yes | Compressor contactor Burn | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB037 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 | NA | BrandNew | NA | VIRENDRA | Yes
FEB033/25 | 2025-02-13 10:34 | service@crystalgroup.in | Shah TC | CXRU1186451 | 40 reefer | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | ISO PLUG BURNT | replaced ISO plug with new one | na | No | POWER Fluctional | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB033 | DK | DAIKIN LXE10 E | OK | OK | OK | USED | OK | RAMIZ | No
FEB035/25 | 2025-02-13 12:01 | service@crystalgroup.in | RELIANCE TOLOJA | TRIU6681440 | 4O FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | FOUND HEATER COIL DEFECTIVE 6 NOS | NEED TO REPLACED AS SOON AS POSITIBLE | HEATER COIL 6 NOS | Yes | MFG DATE EXPIRD | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB035 | MAIN | CARRIER THINE LINE | OK | OK | OK | USED | NA | VIRENDRA | Yes
FEB037/25 | 2025-02-13 13:12 | rahul.gawade@crystalgroup.in | Reliance Kerala (Quick Supply) | CICU2094089 | 10FT | THERMOKING | SERVICE-ON CALL | LEASE | AMC | Compressor Cotactor burnout, Mantrack hooter Speakor not working, Transformer Noice with vibration (Suspected Issue) | Need to replace Compressor Cotactor (25Amp) | Compressor Cotactor 25AMP 3 pole for MP4000 | Yes | Dirty Condenser Coils: Poor heat dissipation forces the compressor to work harder, increasing current draw. 2.Voltage Fluctuations: Low or high voltage can cause excessive heating in the contactor coil and contacts, leading to failure. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB037 | MAGNUM PLUS MP4000 | MAGNUM PLUS MP4000 | Ok | Ok | OK | New | Not Available | VIRENDRA | Yes
FEB038/25 | 2025-02-15 14:35 | crm@crystalgroup.in | Hetro Unit 3 | CXRU1326276 | 40FT STD RF | Carrier Primeline | INSTALLATION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB038 | Carrier | Primeline | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
FEB039/25 | 2025-02-15 14:37 | crm@crystalgroup.in | Hetro Unit 3 | CXRU1550769 | 40FT STD RF | Carrier - Primeline | INSTALLATION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB039 | Carrier | Primeline | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
FEB040/25 | 2025-02-15 17:31 | service@crystalgroup.in | Ajinomoto Bio | BMOU9766180 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Supply return ,Ambient ,Inlet ,Outlet sensor issue, Decos 3iF controller suspectead | Need to replace all sensors .if issue not resolved need to replace controller also. | Temp Sensor 6 Nos Decos 3iF controller | Yes | Sensor Failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB040 | Daikin | NA | NA | NA | Decos 3iF | used | NA | VIRENDRA | Yes
FEB042/25 | 2025-02-17 11:36 | service@crystalgroup.in | RELIANCE kamaspura | TRIU6618391 | 20 ' FT REEFER | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | LEAKAGE FROM FILTER DRIER , SUPLLY & RETURN SENSOR & DEFROST SENSOR FOR SUSPECTED | need to replaced filter drier & gas charged 5 KGS | SUPPLY SENSOR 2NOS,RETURN SENSOR 1, DEFROST SENSOR 1 , FILTER DRIER 1 & GAS R134a 5 KGS .. | Yes | A filter drier leakage problem can occur due to a clogged filter drier, which happens when contaminants like moisture, dirt, or debris accumulate within the desiccant material, restricting refrigerant flow and potentially causing leaks at the seals or casing due to increased pressure build-up. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB042 | DUAL | CARRIER THINE LINE | NA | NA | NA | USED | NA | VIRENDRA | Yes
FEB034/25 | 2025-02-18 12:14 | crm@crystalgroup.in | Laurus Unit 3 | DFOU6120384 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB034 | Daikin | Daikin | MOO4338 | NA | NA | Used | NA | SHUBHAM | Yes
FEB036/25 | 2025-02-18 12:16 | crm@crystalgroup.in | LAURUS UNIT 3 | BMOU9784137 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB036 | Daikin | NA | NA | NA | NA | used | NA | SHUBHAM | Yes
FEB025/25 | 2025-02-18 15:01 | crm@crystalgroup.in | Kirloskar Corrocoat | ARCU4530799 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB025 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | SHUBHAM | Yes
FEB043/25 | 2025-02-18 18:39 | service@crystalgroup.in | Transy Global | TITU8259378 | 20FT Spl RF with Wheels | Thermoking MP-4000 | SERVICE-ON CALL | LEASE | FOC | Supply Sensor Alarm on display | Need to Replace 1 Nos Supply Sensor | Supply Sensor 1 Nos | Yes | Supply sensor failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB043 | Thermo King MP-4000 | MP 4000 | NA | NA | MP4000 3.5 | Used | NA | SHAHBUDDIN | Yes
FEB046/25 | 2025-02-21 09:59 | crm@crystalgroup.in | Cliantha Research Ltd | CICU1938267 | 20FT Super RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB046 | Thermoking MP-4000 | MP 4000 | NA | NA | NA | Brand New | NA | RAJ KUMAR | Yes
FEB027/25 | 2025-02-21 18:17 | crm@crystalgroup.in | Qwik Supply -Ahmedabad | TDRU5815332 | 40FT STD RF | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB027 | Carrier - Thinline | Thinline | NA | NA | NA | NA | NA | RAJ KUMAR | Yes
FEB042/25 | 2025-02-22 11:22 | service@crystalgroup.in | RELIANCE kamaspura | TRIU661831 | 20' | Daikin | SERVICE-AT SITE | LEASE | FOC | One Reefer Unit is not Operating on Inspection found gas leakage from Filter Drier ,Alarm AL54 is coming ,we have observe unit and found suplly sensor ,DIF 2 Nos ,Compressor Run ByPass Mode. | Need to Topup Gas R134A,Supply Sensor ,Compressor, Suction and Discharge Gasket ,Compressor Oil | 1)Gas R134A 2)Filter Drier 3)Supply Sensor 4)Suction and Discharge gasket 5)Compressor Oil | Yes | Gas leakage from filter drier ,Suppy Sensor Failure, | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB042 | NA | Thinline | NA | NA | ML3 | Used | NA | Local Supplier OM Sai air conditioner | Yes
FEB047/25 | 2025-02-24 12:40 | crm@crystalgroup.in | Navin Fluorine | CCLU1031878 | 20FT | Carrier - Thinline | SERVICE-AT SITE | LEASE | FOC | Container not cooling down | Filter drier needs to replaced | Filter drier | Yes | Filter drier needs to replaced | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB047 | NA | Thinline | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
FEB026/25 | 2025-02-24 16:46 | crm@crystalgroup.in | DHL Supply Chain | TCLU1912270 | 20FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=%20FEB026 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | Yes
FEB030/25 | 2025-02-25 17:17 | crm@crystalgroup.in | Navin Fluorine | HJCU6013796 | 40FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB030 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | RAJ KUMAR | Yes
FEB044/25 | 2025-02-25 17:26 | service@crystalgroup.in | ARAI & Chennai | CCLU1036545 | NA | Carrier Thenline | SERVICE-AT SITE | LEASE | CHARGEABLE | Condensor Coil Leakage Issue | Need to Carriy N2 Test ,Braising Set,O2,LPG,Brazing Rod,Vaccum Pump | N2 Brazing Set O2 LPG N2 Brazing Rod Vaccume Pump | Yes | Leakage from Container | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB044 | NA | Thinline | NA | NA | NA | Used | NA | LOcal Supplier | Yes
FEB052/25 | 2025-02-26 10:58 | crm@crystalgroup.in | DSV Solutions | TITU8258978 | 20FT Spl RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB052 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 | NA | Used | NA | RAMIZ | No
FEB029/25 | 2025-02-26 11:00 | crm@crystalgroup.in | PI Industries | CXRU1035856 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB029 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used | NA | RAJ KUMAR | Yes
FEB031/25 | 2025-02-26 11:03 | crm@crystalgroup.in | Switz International | TITU8259465 | 20FT Spl RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB031 | Thermoking MP-4000 | MP 4000 | NA | NA | NA | Brand New | NA | RAJ KUMAR | Yes
FEB049/25 | 2025-02-26 12:08 | service@crystalgroup.in | Qwik Supply | HDMU5499131 | 40FT STD RF | Daikin 3D | SERVICE-AT SITE | LEASE | FOC | NA | NA | NA | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB049 | Daikin | Daikin | NA | NA | 3D | Used | NA | VIRENDRA | No
FEB050/25 | 2025-02-26 16:34 | crm@crystalgroup.in | Qwik Supply | MYRU4518166 | 40FT STD RF | Carrier - Thinline | MACHINE INSPECTION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB050 | Carrier - Thinline | Thinline | NA | NA | NA | Used | NA | VIRENDRA | Yes
FEB053/25 | 2025-02-27 15:01 | crm@crystalgroup.in | Reliance Surat | APRU5066497 | 40FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB053 | Carrier - Thinline | Thinline | NA | NA | NA | NA | JSGA623040296 | RAJ KUMAR | Yes
FEB054/25 | 2025-02-28 17:17 | service@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Winding Grounded | Need to Replace Compressor ,Clean Floor and need to keep Material in Pelletized way. | 1)Compressor 2)N2 Test 3)R134A Gas 4 KG 4)Compressor Oil | Yes | Suspected Insufficient Air Flow due to Ice Formation on T Bar and Material is Not pelletised | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB054%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | Na | RAMIZ | Yes
FEB055/25 | 2025-02-28 17:25 | service@crystalgroup.in | Reliance Bhopal | MYRU4515188 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp Fluctuation observed | Need to Replace Evaporator Motor ,PT/CT Board, Compressor Contactor and if required compressor also need to be replaced (Suspected) | 1)Evaporator Motor 2)PT/CT Board 3)Compressor Contactor 4)Compressor (Suspected) 5)Brazing set 6)R134A Gas | Yes | Suspectead Evaporator Motor and PT/CT board Failure .Also Compressor Is Heavy Noicy | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB055%2F25 | Daikin | Daikin | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
MAR001/25 | 2025-03-03 14:48 | crm@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | DAikin | Breakdown | LEASE | FOC | Compressor winding grounded, insufficient gas , Ice formation | Need to replace Compressor, top up gas | Compressor 1 Filter Drier 1 Suction Gas Kit 1 Discharge Gas Kit 1 R134a gas 6kg Nitrogen 1 Vaccum Pump 1 HP 1 | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR001%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | NA | RAMIZ | Yes
FEB045/25 | 2025-03-05 12:04 | crm@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40FT STD RF | 2008 | REPAIR | LEASE | FOC | NA | Filter Drier to be replaced Gas top up required | Filter Drier | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB045%2F25 | DAikin | DAikin | NA | NA | NA | Used | JSGA622340482 | RAMIZ | Yes
MAR003/25 | 2025-03-05 16:50 | technician@crystalgroup.in | Eugia Steriles Private Limited | CICU2093987 | 40FT STD RF | THERMOKING | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Unit need to manual Defrost with duty person advise producers | On duty Engineer advance for manual Defrost pro | NA | No | Defrosting issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR003%2F25 | Thermoking | Magnum Plus | E0GM029791 | ABC782800321460084 | NA | BrandNew | NA | SHAHBUDDIN | No
MAR006/25 | 2025-03-06 01:10 | service@crystalgroup.in | Hetero plasma | MYRU4500887 | 40FT | Daikin dual | SERVICE-ON CALL | LEASE | AMC | compressor noise & pumping fail | need to replaced compressor & filter drier & gas R34a & n2 & vacuumpump 1 hp | compressor , gas R134a 6 kgs & filter drier &suctions & discharge gas ket & vacuum pump | Yes | insufficient lubrication, overheating, electrical issues, contamination, restricted airflow, excessive refrigerant pressures, inadequate oil return, voltage fluctuations, | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR006%2F25 | standby | daikin | na | ok | ok | used | na | RAMIZ | Yes
MAR007/25 | 2025-03-07 11:39 | technician@crystalgroup.in | Simbiotech Indore | MYRU4506360 | 40FT HC RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | PM SERVICE REQ BY CLINTS | PM service done | NA | No | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR007%2F25 | DAIKIN | Daikin | MFG 005137 | DECOS III | Na | USED | NA | SHAHBUDDIN | Yes
MAR008/25 | 2025-03-07 11:42 | technician@crystalgroup.in | SIMBIOTECH | TRIU6632532 | 20" | Cartier | SERVICE-ON CALL | SALE | CHARGEABLE | PM SERVICE | Tech. On field | NA | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR008 | Carrier | Carrier | MSS60317678 | 541320 | 5178 | Used | NA | SHAHBUDDIN | Yes
MAR009/25 | 2025-03-07 11:46 | technician@crystalgroup.in | Simbiotech Indore | TRIU6632126 | 20" | Carrier | SERVICE-ON CALL | SALE | CHARGEABLE | PM SERVICE | Tech. On field | NO | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR09%2F2025 | Carrier | Thin line 541-320 | MSS60317716 | 541320 | 5176 | Used | NA | SHAHBUDDIN | Yes
FEB032/25 | 2025-03-07 16:35 | rahul.gawade@crystalgroup.in | EmCure | CICU1938143 | 20ft | Thermoking | REPAIR | SALE | CHARGEABLE | Controller issue (Required 2C, automatecally changes to -69 | Need to replace contoller with our existing Reefer unit's controller. Existing Reefer unit's controller need to modify and test for 3 days before dispatch. | Modified software installed and tested Controller from Existing unit. | Yes | Suspected Controller software issue. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB032%2F25 | Thermoking Superfreezer | Thermoking MP4000 Superfreezer | Missing | Missing | MP4000 | Brandnew | NA | SHAHBUDDIN | Yes
MAR011/25 | 2025-03-07 17:12 | technician@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | GESU9568130 | 40" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | PM service | Tech. On field | NA | No | Pm service only | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR011%2F25 | Carrier | 561-018 | NSJ60396208 | 561018 | 5385 | Used | NA | SHAHBUDDIN | Yes
MAR009/25 | 2025-03-07 17:17 | technician@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | TRIU6632532 | 20" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | PM SERVICE clints request | Tech. On field | Compressor contactor 25A | No | Client request for AUDIT pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR009%2F25 | Carrier | 541320 | MSS60317678 | 541320 | 5178 | Used | NA | SHAHBUDDIN | Yes
MAR008/25 | 2025-03-07 17:21 | technician@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | TRIU6632126 | 20" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | PM service | Tech. On field | Compressor contactor | Yes | Clint request for pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR008%2F25 | Carrier | 541-320 Thin line | MSS60317716 | 541320 | 5178 | Used | NA | SHAHBUDDIN | Yes
MAR007/25 | 2025-03-07 17:37 | technician@crystalgroup.in | Symbiotec | MYRU4506360 | 40" | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | PM SERVICE | Tech .on field | DAIKIN SHEET KEY AND FILTER DRIER | Yes | Client request for PM service only for AUDIT | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR007%2F25 | DAIKIN | DAIKIN- LXE -10-E / 136A | MFG: M005137 | DECOS - III E | 25 series | Used | NA | SHAHBUDDIN | Yes
MAR004/25 | 2025-03-07 17:41 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | GESU9460634 | 40" | Carrier | SERVICE-ON CALL | LEASE | FOC | INSTALATION DONE ✔️ WITH AL 06 KEY PAD HANGUP | Need to send through courier key pad | Carrier key pad | Yes | Carrier key pad hangup | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR004%2F25 | Carrier | Carrier | NA | NA | NA | Used | NA | SHAHBUDDIN | No
MAR013/25 | 2025-03-07 20:10 | service@crystalgroup.in | Divis Labs | Cont 4 | 40 reefer | carrier thine line | SERVICE-ON CALL | LEASE | CHARGEABLE | temperature no achieve as desired | try to find leakage by engg | no yet conform | No | suspected leakage from discharge side | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR013%2F25 | reefer | carrier thine line | na | ok | ok | used | na | RAMIZ | No
FEB048/25 | 2025-03-08 10:43 | technician@crystalgroup.in | Transys Global Forwarding Private Limited | TITU8259378 | 20" | TK MP 4000 | SERVICE-ON CALL | LEASE | FOC | Temp. Issue with Display faded | Advise to clean ice from bottam | TK MP 4000 DISPLAY & DOOR ONLY | Yes | Frosting inside bottam area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB048%2F25 | THERMOKING | Tk MP 4000 | EOG1000179 | NA | NA | Used | NA | SHAHBUDDIN | No
MAR014/25 | 2025-03-08 11:11 | technician@crystalgroup.in | PI INDUSTRIES LTD | MYRU4502299 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | Done | FilterDrier | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR014%2F25 | Daikin | Daikin | NOT AVAILABLE | LYE10E136A2 | NOT AVAILABLE | Refurbished | NA | RAJ KUMAR | No
MAR017/25 | 2025-03-08 22:03 | service@crystalgroup.in | Softbox | GRMU3707470 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Compressor abnormal noise & less gas suspected & isv & esv valve defective . | have to return mumbai | isv esv gas r134a filter drier breezing set all equipment | Yes | leakage or isv & esv defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR017%2F25 | Daikin | daikin | na | ok | decose iiid | used | yes | RAMIZ | No
MAR016/25 | 2025-03-08 22:15 | service@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | daikin | SERVICE-AT SITE | LEASE | FOC | ice foundation on evaproter coil & supply air flow block y cargo & Ice foundation t bar floor. | advice them by pallets & keep proper sir circulation away. | na | No | in proper staking cargo | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR016%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | na | RAMIZ | No
MAR015/25 | 2025-03-08 22:28 | service@crystalgroup.in | Laurus Labs Limited-Unit 1 | CXRU1037308 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | AMC | condenser coil normal dirty | clean condenser coil with fresh water . | na | No | no clean condenser coil on time | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR015%2F25 | Daikin | LXE10E147F2 | M000334 | K31505146690 | DECOS 3F 2553 / 1 | Used | na | VIRENDRA | No
MAR012/25 | 2025-03-08 22:34 | service@crystalgroup.in | Laurus Labs Limited-Unit 1 | PCIU6006639 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | suctions gas sensor or condenser coil dirty | replaced suctions gas sensor with new & clean condenser coil with fresh water | na | No | condenser coil not clean on timely | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR012%2F25 | Daikin | daikin | na | ok | III d | used | na | VIRENDRA | No
FEB051/25 | 2025-03-08 22:43 | service@crystalgroup.in | Laurus unit 2 | PRGU4958724 | 40 reefer | carrier thne line | SERVICE-AT SITE | LEASE | FOC | condenser fan defective & htt defective & fues burn 7.5 amps 1 nos condenser fan motor noise | replaed condenser fan motor new. | EVP MOTOR CONDENSOR FAN BLADE ML 3 CONTROLLER | Yes | HTT SHORT circuit & motor bearing risted | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB051%2F25 | reefer carrier | thine line | na | na | ok | used | na | VIRENDRA | Yes
MAR018/25 | 2025-03-08 23:03 | service@crystalgroup.in | HETERRO UNIT 5 | SUDU6218004 | 40FT STD RF | CARRIER ELIGHT LINE | PREVENTIVE MAINTENANCE | LEASE | FOC | CONENSER COIL NORMAL DIRTY | CLEAN CONDENSER COIL WITH FRESH WATER |  | MAN TRAF NEED TO FIX | NOT CLEAN IN TIEMLY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR018%2F25 | Carrier-Primeline | Primeline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | NA | RAMIZ | Yes
MAR005/25 | 2025-03-10 17:27 | service@crystalgroup.in | Hetero Unit 3 | PCIU6016370 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | found fungus on cargo dram label sticker . | need to clean evaporator coil & container internal | na | No | evaporator coil oxidized or fungus occurred | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR005%2F25 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | RAMIZ | Yes
MAR019/25 | 2025-03-10 18:16 | crm@crystalgroup.in | Qwik Supply Chain Pvt Ltd | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-ON CALL | LEASE | FOC | Motor making heavy noise | Need to replace Bearings, Evp motor (suspected) | Bearings | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR019%2F25 | Daikin | Daikin | NA | NA | NA | Used | NA | RAMIZ | Yes
MAR010/25 | 2025-03-11 03:32 | service@crystalgroup.in | qwik supply | CICU1799140 | 10 ft blast | THERMO KING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | need to up lode latest software , for leakage need to visit | software card lp switch temperature sensor return temperature sensor supply filter drier gas 404A 5 kgs vacuum pump | Yes | software or less gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR010%2F25 | 10 FT BLAST REEFER | THERMOKING MP 4000 | OK | OK | OK | BRAND NEW | NO | VIRENDRA | Yes
MAR002/25 | 2025-03-11 03:43 | service@crystalgroup.in | Reliance - Jamnagar | CGMU2991679 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | condenser fan contactor 12 defectives ,al 58 & al 72 & al 74 | need to replaced contactor 12 amps | contactor 12 amps HP switch suspected | Yes | electrical overload, arcing, overvoltage, high surge voltages, frequent cycling, poor wiring, and environmental factors like dirt, dust, or moisture. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR002%2F25 | Carrier - Thinline | Thinline | ok | ok | ok | Refurbished | a | RAJ KUMAR | Yes
MAR021/25 | 2025-03-11 04:08 | service@crystalgroup.in | Reliance - Jamnagar | TRIU6618663 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | al 54,al 60 al 61,al 72 visible | need to replace defective heater & supply temperature sensor | supply temperature sensor 2 nos defrost sensor defrost heater 6 nos | Yes | chemical contamination, damaged transition junctions, self-heating, excessive mechanical stress, and electrical overload. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR021%2F25 | Carrier - Thinline | Thinline | ok | ok | ok | Refurbished | na | RAJ KUMAR | Yes
MAR020/25 | 2025-03-11 04:14 | service@crystalgroup.in | Reliance - Jamnagar | CCLU1031918 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | condenser fan motor bearing noise & key pad defective & compressor oil leakage | need to replace condenser fan motor & keypad | condenser fan motor bearing 2 nos ( suspected to motor defective) key pad | Yes | damaged bearings, a faulty motor, loose components | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR020%2F25 | Carrier - Thinline | Thinline | na | ok | ok | brand New | na | RAJ KUMAR | Yes
MAR022/25 | 2025-03-12 01:25 | service@crystalgroup.in | qwick supply | CICU1799177 | 10FT Spl RF | tk mp 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | condense coil very dirty | clean condenser coil with fresh water | na | No | condense coil very dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR022%2F25 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 | ok | BRand NEW | JSGA622180057 | RAMIZ | No
FEB028/25 | 2025-03-12 10:39 | technician@crystalgroup.in | PI Industries Limited unit 6 | MYRU4502299 | 40' | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB028%2F25 | DAIKIN | LXE 10-E | NA | NA | NA | Used | NA | Pm Done by Rajkumar | No
MAR023/25 | 2025-03-13 08:57 | service@crystalgroup.in | Hetero Plasma | MYRU4500887 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | compressor over current & abnormal noise | need to replace compressor | compressor compressor oil gas R134a 6 kgs n2 cylinder big filter drier vacuum pump | Yes | Problems with wiring, contaminated refrigerant oil can cause friction and overheating, leading to overcurrent and compressor failure. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR023%2F25 | Daikin | Daikin | na | LXE10E136A | decose iiid | Refurbished | na | RAMIZ | Yes
MAR030/25 | 2025-03-15 19:39 | service@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | tk mp 400 | SERVICE-AT SITE | LEASE | FOC | display defective | need to replace | display | Yes | getting old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR030%2F25 | Thermoking | MP-4000 | 05G7619AG | E001051602 | ok | used | JSGA622180047 ¦ JSGA622180052 | RAMIZ | Yes
MAR031/25 | 2025-03-17 21:58 | service@crystalgroup.in | Adya Dairy | BMOU972939 | 40 | daikin | SERVICE-ON CALL | LEASE | FOC | al 109 low pressor / filter drier /FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, | need to replaced filter drier & R134a 5 kgs & vacuum pump | 1) filer drier 2) gas R134a 5 kgs 3)vacuum pump | Yes | filer drier & less gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR031%2F25 | daikin | daikin | na | na | ok | used | ok | Vibak | Yes
MAR034/25 | 2025-03-18 15:14 | technician@crystalgroup.in | Eugia Steriles Private Limited | CICU3876610 | 10FT STD RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | Temp. | Co. Own house keeping under progress... | NA | Still obs aftet dudpected return tk sendor | Blockage conf.coil & inside bottom area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR034%2F25 | Thermoking | Magnum Plus | E0GM031439 | 0422GM031439 | ABC782900322060170 | Brand New | NA | Not yet unit u/ obs dury person | No
MAR037/25 | 2025-03-20 20:46 | service@crystalgroup.in | DSV | SJKU4000104 | 40FT STD RF | 2019 | PREVENTIVE MAINTENANCE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | na | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR037%2F25 | Thermoking | MP-4000 | ok | ok | ok | Refurbished | na | RAMIZ | No
MAR038/25 | 2025-03-20 20:57 | service@crystalgroup.in | DSV | TITU9930006 | 40FT Spl RF | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | na | No | due to long run | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR038%2F25 | Thermoking | Plus | 14D8550HT | EOG1000568 | pk | brand New | na | RAMIZ | No
MAR035/25 | 2025-03-24 14:38 | technician@crystalgroup.in | Swabhimani Agro | DMOU9226840 | N/a | N/a | SERVICE-ON CALL | NA | NA | Compressor df due to ground | Need to be replaced compressor | Compressor 1nos Compressor oil 3ltr N2 test and flush Vaccum pump Fillter Drier 1nos R-134a 5kg | Yes | Compressor ground | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR035%2F25 | Reefer unit | Prime line | N/a | N/a | Ml3 | N/a | N/a | VIRENDRA | Yes
MAR040/25 | 2025-03-28 11:31 | technician@crystalgroup.in | Crystal Group mumbai | CRLU3179858 | 20FT STD RF | Carrier | SERVICE-AT SITE | STOCK | FOC | Fan capacitor & power plug Defective | Need to replaced parts | 20 Uf Fan capacitor & power plug | Yes | PTI FAIL | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR040%2F25 | Carrier | Thineline | NA | NA | NA | Used | NA | Vendor | Yes
MAR039/25 | 2025-03-28 11:37 | technician@crystalgroup.in | Crystal Yard | CXRU1036019 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | STOCK | FOC | PTI FAIL WITH ALARM | Need to replaced spare | Power plug / Temp. Sensor Nos.4 | Yes | PTI FAIL | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR039%2F25 | DAikin | LXE10E147F2 | M001044 | K31511115441 | DECOS 3F 2513 / 1 | used | NA | Vendor | Yes
MAR041/25 | 2025-04-01 16:05 | technician@crystalgroup.in | Reliance - Lucknow | MYRU4718356 | 40 | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Not working | Electrical wiring check and need to replaced Fuse blown with | PTCT board & Fuse | Yes | Power issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR041%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Used | NA | RAJ KUMAR | No
APR001/25 | 2025-04-03 12:44 | technician@crystalgroup.in | LAND FLAVOUR BONDA FACTORY | CXRU1043337 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Light / courtan fixing with kick plate & compressor frosting | Unit maintain pressure and under observation / kick plate / courtan fixed | Tube light / cable / tube light/ casing Pati..etc... | Yes | Power issue with compressor low pumping | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR001%2F25 | https://drive.google.com/drive/folders/1-wT8o-5gU0fGeM-zDesg8npMxU6uKTim?usp=sharing | CARRIER-THINLINE | -22 | 541 320 | 5186 | Used | NA | SHAHBUDDIN | Yes
APR003/25 | 2025-04-04 14:57 | technician@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | HDMU5537036 | 40" | Carrier- Thin Line | SERVICE-AT SITE | LEASE | FOC | Compressor over heat tripping off | Tech Allian for cross check | Thinline carrier compressor/ filter Drier/ R134a Gas/ / N2 / vacum pump etc | Yes | Compressor winding internal faultt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR003%2F25 | Carrier- Reef | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
APR005/25 | 2025-04-04 15:02 | technician@crystalgroup.in | Dr Reddy CTO5 | CXRU1045896 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Evp. Motor | On the way motor | Evp. Motor | Yes | Voltage low or high | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR005%2F25 | https://drive.google.com/file/d/1q4GJVx5gc4pqWsh2QRfHRiY--CfDw21J/view?usp=sharing | DAIKIN | -18 | NA | DAikin | DECOS 3F 2606 / 1 | 1001349 | VIRENDRA | Yes
APR004/25 | 2025-04-04 15:54 | technician@crystalgroup.in | Dr Reddy CTO5 | CXRU1032S64 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | Pm | Spare arrange | Evp motor Daikin | Yes | Evp motor def | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR004%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | VIRENDRA | Yes
APR007/25 | 2025-04-04 15:57 | technician@crystalgroup.in | Adya Dairy Products Pvt. Ltd. | BMOU9729398 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | EEV COIL DEFECTIVE | Spare arrange | EEV COIL daikin | Yes | EEV COIL NOT FUNCTION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR007%2F25 | https://drive.google.com/drive/folders/1Yhya5jN03ZP2Abu9Rry6Lzq5zWNkOdso?usp=drive_link | DAIKIN | NA | NA | NA | Used | NA | RAJ KUMAR | No
APR006/25 | 2025-04-04 16:05 | technician@crystalgroup.in | LAND FLAVOUR BONDA FACTORY | TRIU6616594 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | PM | Done | Condenser fan grill and carrier key pad | Yes | PM due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR006%2F25 | Carrier | CARRIER-THINLINE | NSX60329650 | 541320 | NA | Used | NA | SHAHBUDDIN | No
APR008/25 | 2025-04-05 01:04 | technician@crystalgroup.in | Tata Advanced Systems | CBHU281176 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp not achievement | On call inspection | NA | No | Suspected system leak | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR008%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR002/25 | 2025-04-05 11:05 | technician@crystalgroup.in | HETERO PLASMA | N/A | 40 | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor | Spare on the way HYD | NA | No | Compressor internal | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR002%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | VIRENDRA | Yes
APR009/25 | 2025-04-05 23:46 | technician@crystalgroup.in | Dr Reddy CTO5 | GSOU6384153 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Evp motor noisy | Need to replaced mot | NA | Yes | Motor bearing issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR009%2F25 | https://drive.google.com/drive/folders/1_ZK5F29US0GgzcZrr1IzFWttLbFPbfY4?usp=sharing | CARRIER-THINLINE | -18 | NA | Carrier | ML-3 | 1001345 | VIRENDRA | Yes
APR011/25 | 2025-04-09 16:09 | service.support@crystalgroup.in | ITC Ltd | MYRU4517508 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Icing and not reaching to set point | technician aligned | NA | No | Frosting | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR011%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR012/25 | 2025-04-09 16:29 | service.support@crystalgroup.in | Sai Life Science Pvt ltd | TITU9930032 | 40" | Thermoking Mp-4000 | SERVICE-AT SITE | LEASE | FOC | Unit tripping off | Technician visit | Filter Drier | Yes | High pressure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR012%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
APR014/25 | 2025-04-12 13:12 | service.support@crystalgroup.in | ITC Limited | CGMU2990461 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Temperature issue | Leak found thru video call. | Filter Drier, R134a gas 4kg | Yes | Temperature Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR014%2F25 | Carrier - Thinline | CARRIER-THINLINE | 4612UD6633 | LSM60197686 | NA | New | NA | SHAHBUDDIN | No
APR010/25 | 2025-04-14 11:05 | service.support@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | TTNU9930069 |  | Thermoking | SERVICE-AT SITE | LEASE | FOC | PM | PM done | NA | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR010%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | USED | NA | SHAHBUDDIN | No
APR013/25 | 2025-04-15 18:41 | service.support@crystalgroup.in | Navin Fluorine International Limited | CGMU2988654 | 10FT STD RF | Carrier | Breakdown | LEASE | FOC | Tripping | Light connection wiring |  | No | Electric issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR013%2F25 | NA | CARRIER-THINLINE | -18 | NA | Carrier - Thinline | Used | N/A | SHAHBUDDIN | Yes
APR018/25 | 2025-04-17 10:43 | technician@crystalgroup.in | CRYSTAL GROUP | CR0012 | N/a | Thineline | REPAIR | NA | NA | Staper motor df 1nos Evp motor df 2nos Compressor heavy rusted to replace | NEED REPAIR | STAPER MOTOR 1NOS, EVP MOTOR 2NOS, FILLTER DRIER 1NOS, SECTION AND DISCHARGE GASKIT 1NOS EACH | Yes | STAPER MOTOR DF ,EVP MOTOR DF, | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR018%2F25 | Yes | CARRIER-THINLINE | NSG60383850 | 69NT40-541-320 | ML3I | N/A | N/A | VIRENDRA | No
APR017/25 | 2025-04-17 10:50 | technician@crystalgroup.in | Crystal Yard | CR0011 | N/A | 2010 | REPAIR | NA | NA | LEAKAGE FROM LSV VALVE,EVP MOTOR DF , | NEED TO REPAIR | LSVALVE, EVP MOTOR 2NOS, COMPRESSOR OIL 3LTR, COMPRESSOR 1NOS, FILLTER DRIER 1NOS, SECTION AND DISCHARGE GASKIT | Yes | LEAKAGE AND EVP MOTOR DF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR017%2F25 | DAIKIN | DAIKIN LXE10E | M003245 | LXE10E136A2 | DECOS IIIE | N/A | N/A | VIRENDRA | No
APR016/25 | 2025-04-17 11:12 | technician@crystalgroup.in | Crystal YArd | CR0002 | N/A | 2003-10-01 | REPAIR | NA | NA | LEAKAGE AND STAPPER MOTOR DF,EVP MOTOR DF | NEED TO REPAIR | STAPER MOTOR 1NOS,EVPMOTOR 2NOS,FILLTER DRIER 1NOS,R-134a 5KG CONTROLLER ML3I | Yes | EVPMOTOR DF 2NOS,LEAKAGE ,STAPER MOTOR DF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR016%2F25 | THINELINE | CARRIER-THINLINE | JSL90656195 | 69NT40-541363 | ML2I | N/A | N/A | VIRENDRA | No
APR015/25 | 2025-04-17 11:17 | technician@crystalgroup.in | Crystal Yard | CR0010 | N/A | 2011 | REPAIR | NA | NA | EVP COIL LEAKAGE | NEED TO REPAIR | EVP COIL 1NOS, FILLTER DRIER 1NOS,R-134a 5KG | Yes | EVP COIL LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR015%2F25 | DAIKIN | DAIKIN LXE10E | MOO2030 | LXE10E147F2 | DECOS IIIF | N/A | N/A | VIRENDRA | No
APR019/25 | 2025-04-17 14:58 | service.support@crystalgroup.in | Tianish Laboratories Private Limited | TRLU1741601 | 40FT STD RF | Thermo King | SERVICE-ON CALL | LEASE | FOC | Humidity setting issue | Guide setting process for humidity set |  | No | Setting issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR019%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | used | NA | VIRENDRA | No
MAR028/25 | 2025-04-17 16:39 | service.support@crystalgroup.in | Sai Life Science Pvt Ltd | TITU9930032 | 40FT Spl RF | Thermo King | SERVICE-AT SITE | LEASE | FOC | Closed PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR028%2F25 | Thermoking | TK-MP4000 | 14E6357AT | EOG10005532 | NA | Used | NA | RAJ KUMAR | No
APR022/25 | 2025-04-19 11:44 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9454776 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM | EVP MOTOR SINGLE PHASE | Yes | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR022%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR023/25 | 2025-04-19 11:46 | service.support@crystalgroup.in | Lauras Lab Unit 2 | TITU99302223 | 40FT Spl RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM | CURTAIN LIGHT MP4000 DISPLAY | YES | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR023%2F25 | Thermoking MP-4000 | TK-MP4000 | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR025/25 | 2025-04-19 11:51 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CRSU6101910 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR025%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR024/25 | 2025-04-19 11:53 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CXRU2031845 | 40ft | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR024%2F25 | NA | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
APR026/25 | 2025-04-19 11:55 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CXRU1036533 | 40ft | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR026%2F25 | NA | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
APR027/25 | 2025-04-19 11:56 | service.support@crystalgroup.in | Lauras Lab Unit 2 | BMOU9782197 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR027%2F25 | DAikin | DAIKIN | NA | DECOSIIIF/2553/1 | NA | Used | NA | SHAHBUDDIN | Yes
APR028/25 | 2025-04-19 11:59 | service.support@crystalgroup.in | Lauras Lab Unit 2 | HDMU5584444 | 40FT STD RF | Thermo King | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR028%2F25 | Thermoking MP 4000 | TK-MP4000 | NA | NA | NA | USed | NA | SHAHBUDDIN | Yes
APR029/25 | 2025-04-19 12:01 | service.support@crystalgroup.in | Lauras Lab Unit 2 | HDMU5586473 | 40FT STD RF | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  |  | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR029%2F25 | Thermoking MP 4000 | TK-MP4000 | PM | PM | PM | USed | NA | SHAHBUDDIN | Yes
APR021/25 | 2025-04-19 12:03 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9529290 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR021%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR030/25 | 2025-04-19 17:49 | tender@crystalgroup.in | Mundra Depot | WIKU5237623 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR030%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes
APR031/25 | 2025-04-19 17:51 | tender@crystalgroup.in | Mundra Depot | HNKU6113303 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR031%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes
APR032/25 | 2025-04-19 17:53 | tender@crystalgroup.in | Mundra Depot | WIKU5243523 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR032%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes
APR033/25 | 2025-04-19 17:55 | tender@crystalgroup.in | Mundra Depot | HNKU6272619 | 40ft HC | NA | REPAIR | SALE | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR033%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes
APR034/25 | 2025-04-19 17:56 | tender@crystalgroup.in | Mundra Depot | HNKU6272820 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | NA | NA | NA | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR034%2F25 | NA | DRY | NA | NA | NA | Brand New | na | AKSHAY | Yes
APR035/25 | 2025-04-19 17:58 | tender@crystalgroup.in | Mundra Depot | HNKU6282622 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | NA | NA | NA | No | PAINT | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR035%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | No
APR020/25 | 2025-04-21 11:52 | technician@crystalgroup.in | Lauras Lab Unit 2 | PRGU4958724 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Evaprator & condenser fan motor not working | Waiting spare | ML controller/ Evaprator motor & condenser fan blade | Yes | Motor break down | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR020%2F25 | Carrier- Thin Line | CARRIER-THINLINE | NA | NA | NA | Usam | Used | SHAHBUDDIN | Yes
APR008/25 | 2025-04-21 18:07 | technician@crystalgroup.in | Tata Advanced Systems | CBHU281176 | 40" | Carrier | SERVICE-ON CALL | LEASE | FOC | Temp.not reach set | Clean Internal house keeping | HTT Sensor and carrier key pad | Yes | Air flow block | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR008%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | No
APR038/25 | 2025-04-23 15:06 | technician@crystalgroup.in | Crystal Vizag Depot | ARCU4530675 | 40" | Carrier | SERVICE-AT SITE | STOCK | FOC | Power cable & plug missing after PTI | Fixed cable plug | 15 never power cable & power plug with 15 A mcb | Yes | Empty repair & Pti | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR038%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR037/25 | 2025-04-23 15:11 | technician@crystalgroup.in | Crystal Vizag Depot | MYRU4509035 | 40FT STD RF | Daikin | SERVICE-AT SITE | STOCK | FOC | Power cable & plug missing and for PTI | Spare arrange | 15 Mt power cable and powwer plug with 16A ncb | Yes | Empty repair missing cable & plug mcb | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR037%2F25 | Daikin | DAIKIN | 802602 | LXE10E136A | NA | Used | NA | SHAHBUDDIN | Yes
APR036/25 | 2025-04-23 20:53 | technician@crystalgroup.in | SWADESH MILK | GESU9290991 | 40" | CARRIER | SERVICE-AT SITE | SALE | CHARGEABLE | Condenser fan motor heavy Noisy | Need to replaced | Condenser Fan Motor - carrier thin line single phase with Fan Blade. | Yes | Motor Rust with old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR036%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | No
APR042/25 | 2025-04-25 00:04 | technician@crystalgroup.in | Laurus Unit 3 | TDRU7153256 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM service | PM service Done | NA | No | Pm service due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR042%2F25 | Daikin | DAIKIN | MFG : A001117 | NA | NA | used | NA | SHAHBUDDIN | Yes
APR041/25 | 2025-04-25 00:19 | technician@crystalgroup.in | Laurus Unit 3 | BMOU9784137 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | PM SERVICE DONE | Daikin sheet key complit set /EIS /EOS/TEMP. SENSOR | Yes | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR041%2F25 | Daikin | DAIKIN | NA | NA | NA | used | NA | SHAHBUDDIN | Yes
APR040/25 | 2025-04-25 00:44 | technician@crystalgroup.in | Laurus Unit 3 | PCLU1912290 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | PM service | PM service arranged | EIS SENSOR & TEMP. SENSOR | Yes | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR040%2F25 | Daikin | DAIKIN | MFG:M .004715 | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR039/25 | 2025-04-25 01:00 | technician@crystalgroup.in | Laurus Unit 3 | MYRU4505847 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | Done | NA | No | Pm service only | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR039%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | No
APR043/25 | 2025-04-28 15:34 | technician@crystalgroup.in | Laurus Unit 3 | KKFU6711724 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service | PM service Done | NA | No | Due pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR043%2F25 | Carrier - Thinline | CARRIER-THINLINE | LSX60253435 | 541321 | 5487 | used | NA | SHAHBUDDIN | Yes
APR044/25 | 2025-04-28 15:48 | technician@crystalgroup.in | Laurus Unit 3 | MYRU4519115 | 40FT STD RF | Dakin | SERVICE-AT SITE | LEASE | FOC | PM Due | PM SERVICE DONE | NA | No | P. M. Due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR044%2F25 | Daikin | DAIKIN | 806162 | LXE10E136A2 | Na | Refurbished | NA | SHAHBUDDIN | Yes
APR045/25 | 2025-04-28 16:30 | technician@crystalgroup.in | Laurus Unit 3 | KKFU6710760 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Due pm | PM DONE | Supply sensor cartoer nos.2 & Discharge transducer jack | Yes | Pm due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR045%2F25 | Carrier - Thin line | CARRIER-THINLINE | LSU60253959 | 541321 | 5167 | Used | NA | SHAHBUDDIN | Yes
APR046/25 | 2025-04-28 16:46 | technician@crystalgroup.in | Laurus Unit 3 | APRU5091340 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Due pm | P. M. Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR046%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA A | Used | NA | SHAHBUDDIN | Yes
APR047/25 | 2025-04-28 17:08 | technician@crystalgroup.in | Laurus unit 3 | SUDU6257274 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Due pm | PM Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR047%2F25 | Carrier - prime line | CARRIER-PRIMLINE | NSR60443683 | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR048/25 | 2025-04-28 17:33 | technician@crystalgroup.in | Laurus Unit 3 | DFOU6120384 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Due pm | P. M. Complit | PT/CT BOARD & EIS DAIKIN SENSOR | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR048%2F25 | Daikin | DAIKIN LXE10E | MOO4338 | NANA | NA | Used | NA | SHAHBUDDIN | Yes
APR050/25 | 2025-04-28 18:44 | technician@crystalgroup.in | Indradeep Construction | MYRU4513729 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp. Sensor abnormal reading | Check & need to replaced | Daikin supply sensor nos. 3 | Yes | Sensors dauilty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR050%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | Yes
APR051/25 | 2025-04-29 14:57 | technician@crystalgroup.in | Gyan Enterprises Nepal gung | CXRU1030854 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor Noisy & leak back | Need to replaced | DIkin compressor/ suction gasket / O ring discharge/ filter Drier / Gas R 134a 5 kg/ Nitogen leak test/ vacum pump | Yes | Frequency | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR051%2F25 | Daikin | DAIKIN LXE10E | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used | NA | RAJ KUMAR | Yes
APR049/25 | 2025-04-29 15:11 | technician@crystalgroup.in | Zepto | SEGU9052030 | 40FT STD RF | Carrier prime line | SERVICE-AT SITE | LEASE | FOC | Tripping | Tech on way | NA | No | Power issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR049%2F25 | Carrier | CARRIER-PRIMLINE | NANA | NA | NA | Used | NA | RAJ KUMAR | Yes
APR062/25 | 2025-04-29 15:14 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9454776 | 40FT STD RF | Carrier | RUNNING WITH ISSUES | LEASE | FOC | RUNNING WITH ISSUES | PM | EVP MOTOR SINGLE PHASE | Yes | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR022%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR063/25 | 2025-04-29 15:20 | service.support@crystalgroup.in | Lauras Lab Unit 2 | TITU99302223 | 40FT Spl RF | Carrier | RUNNING WITH ISSUES | LEASE | FOC | RUNNING WITH ISSUES | PM | CURTAIN LIGHT MP4000 DISPLAY | YES | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR023%2F25 | Thermoking MP-4000 | TK-MP4000 | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
APR055/25 | 2025-04-29 16:22 | service@crystalgroup.in | crystal yard | GRMU3707470 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Compressor abnormal noise & less gas suspected & isv & esv valve defective . | have to return mumbai | isv esv gas r134a filter drier breezing set all equipment | Yes | leakage or isv & esv defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR017%2F25 | Daikin | daikin | na | ok | decose iiid | used | yes | RAMIZ | No
APR060/25 | 2025-05-02 16:33 | technician@crystalgroup.in | Lupin | CCLU1036859 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. & Display faded | Need to replaced display & service | Carrier Display | Yes | Display | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR060%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
APR052/25 | 2025-05-02 16:39 | technician@crystalgroup.in | Qwik Supply | CRLU6220410 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp | Advise to clints duty person to clen inside | NA | No | Air flow blocking | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR052%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | No
APR061/25 | 2025-05-03 16:27 | qualitycontrol@crystalgroup.in | BCC | CRIU2152251 |  | ISO Tank | SERVICE-ON CALL | LEASE | CHARGEABLE | Leakage from foot valve as been told but the customer is not able to provide clear photo /video of the leakage | First need to check properly |  | Not clear at present | Mishandling by the client | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR061%2F25 | NA | ISO TANK | NA | NA | NA | USED | NA | VIRENDRA | Yes
APR064/25 | 2025-05-03 16:39 | technician@crystalgroup.in | Laurus Unit 2 | CXRU1036334 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC |  | On way tech | All daikin sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR064%2F25 | Daikn | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY002/25 | 2025-05-03 16:43 | technician@crystalgroup.in | UPS | HDMU5220720 | 20FT STD RF | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Tech on way | NA | Depend check | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY002%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | USed | NA | RAMIZ | Yes
MAY003/25 | 2025-05-05 14:30 | service@crystalgroup.in | LUPIN LIMITED | TRIU6681882 | 20 ft | carrier thin line | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor tripping issue | Filter Drier replacement, refrigerant top up | Filter Drier 01 nos. Refrigerant | Yes | FILTER DRIER CHOKED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY003%2F25 | 20 ft Reefer | CARRIER-THINLINE | 0 | 0 | Advance | USED | 0 | VIRENDRA | Yes
APR060/25 | 2025-05-05 14:33 | service@crystalgroup.in | Lupin | CCLU1036859 | 20FT STD RF | carrier | REPAIR | LEASE | CHARGEABLE | COMPRESSOR TRIPPING ISSUE | FILTER REPLACEMENT | FILTER DRIER, REFRIGERANT, VEHICLE | Yes | FILTER DRIER CHOKED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR060%2F25 | Carrier | CARRIER-THINLINE | 0 | 0 | 0 | Used | 0 | VIRENDRA | Yes
APR053/25 | 2025-05-05 16:07 | crm@crystalgroup.in | Crystal Yard | CRSU6017476 | 40 FT | NA | REPAIR | NA | NA | EVP MOTOR NOISY | Need to replace Bearing | 6203 tune wise & 6205 tunewise | Yes | Bearing Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR053%2F25 | CARRIER-THINLINE | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | No
APR054/25 | 2025-05-05 16:10 | crm@crystalgroup.in | Crystal Yard | GESU9454950 |  | NA | REPAIR | NA | NA | EVP MOTOR NOISY | Need to replace bearing | 6203 tune wise, 6205 tune wise | Yes | Bearing Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR054%2F25 | CARRIER-THINLINE | CARRIER-THINLINE | NA | NA | NA | NA | NA | RAMIZ | No
MAY004/25 | 2025-05-05 17:40 | service@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | SJKU4000104 | 40FT | NA | SITE INSPECTION | LEASE | CHARGEABLE | Extreme sound coming from, Condenser Fan, variation in temperature | on site inspection |  | on site inspection | Need To Check Physically | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY004%2F25 | 40REEFER | NA | 0 | 0 | 0 | USED | 0 | VIRENDRA | Yes
MAY005/25 | 2025-05-05 17:52 | crm@crystalgroup.in | Verka Amritsar Dairy | CXRU1186385 | 40FT STD RF | NA | REPAIR | LEASE | CHARGEABLE | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | Compressor 3 abnormal noise | New Compressor, R134A Gas - 5KG, Drier Filter, Gaskit & Compressor Oil 3Ltr | Yes | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY005%2F25 | Daikin | DAIKIN | M002086 | K31505147912 | DECOS 3F 2557 / 1 | Used | CXRU1186385 | RAMIZ | Yes
JAN031/25 | 2025-05-06 16:53 | crm@crystalgroup.in | MOCHAN food processors private limited | GRMU3707525 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN031%2F25 | NA | NA | NA | NA | NA | NA | NA | RAMIZ | No
MAR029/25 | 2025-05-06 16:56 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | MYRU4518042 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR029%2F25 | NA | NA | NA | NA | NA | NA | NA | VIRENDRA | No
MAR033/25 | 2025-05-06 17:01 | crm@crystalgroup.in | Dr. Reddy FTO7 | SEGU9511192 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR033%2F25 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | No
MAR036/25 | 2025-05-06 17:05 | crm@crystalgroup.in | Qwik Supply Reliance | SJKU4000017 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR036%2F25 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | No
MAY012/25 | 2025-05-07 22:27 | technician@crystalgroup.in | CIPLA | CRIU4024049 | 40" | Thermoking | INSTALLATION | SALE | CHARGEABLE | New container for Instalation Two way | Job strat | NA | No | Instalation two way | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY012%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | Yes
MAY007/25 | 2025-05-07 22:33 | technician@crystalgroup.in | CIPLA | CRIU4024033 | 40FT 2BAY RF | Thermoking | INSTALLATION | SALE | CHARGEABLE | Two way Instalation | Job start | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY007%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | Yes
MAY006/25 | 2025-05-08 09:28 | technician@crystalgroup.in | ITC AQUA | MYRU4517508 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp. | NA | EIS sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY006%2F25 | Daikin | DAIKIN LXE10E | M002805 | LXE10E136A | NOT AVAILABLE | Used | NA | SHAHBUDDIN | Yes
MAY026/25 | 2025-05-10 16:40 | service@crystalgroup.in | Sai Life | HDMU5542114 | 40FT STD RF | Carrier | SERVICE-AT SITE | SALE | AMC | Controller Display is not readable in sun light | Discussed with customer, and agreed for PM and check the controller display | CARRIER THINELINE CONTROLLER | Yes | Controller Display is not readable in sun light | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY026%2F25 | RFH40R | CARRIER-THINLINE | HDMU5542114 | RFH40R | 0 | used | 0 | SHAHBUDDIN | Yes
MAY027/25 | 2025-05-10 17:45 | technician@crystalgroup.in | MEDISPARAY LOBORATORIES PVT.LTD. | TRIU6681434 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service Due | PM service | NA | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY027%2F25 | Carrier - Thinline | CARRIER-THINLINE | NSG60383847 | 541320 | 5176 | Used | NA | SHAHBUDDIN | Yes
MAY001/25 | 2025-05-10 17:58 | service@crystalgroup.in | Qwik Supply | CICU3876610 | 10FT STD RF | Thermoking | SERVICE-ON CALL | NA | NA | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin |  | No | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY001%2F25 | Thermoking | Magnum Plus | E0GM031439 | 0422GM031439 | ABC782900322060170 | Brand New | nill | SHAHBUDDIN | No
MAY017/25 | 2025-05-10 18:07 | service@crystalgroup.in | LUPIN LIMITED | TRIU6681882 | 20FT STD RF | Carrier - Thinline | SERVICE-ON CALL | NA | NA | Need Temperature alarm system quotation | Need share quotation |  | No | Need Temperature alarm system quotation | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY017%2F25 | Carrier - Thinline | CARRIER-THINLINE | RFG20R | nill | imart | Used | na | VIRENDRA | No
MAY018/25 | 2025-05-12 12:47 | service@crystalgroup.in | Dr Reddy CTO 6 | CXRU1033616 | 40FT STD RF | DAikin | SERVICE-AT SITE | NA | NA | No cooling | Replacement of Supply and return sensor. 06 nos. | Diakin Thermistor- 2509541 Supply and return sensor. 06 nos. | Yes | no cooling | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY018%2F25 | LXE10E147F2 | DAIKIN | M001192 | K31508150460 | DECOS 3F 2557 / 1 | used | 0 | SHAHBUDDIN | Yes
MAY016/25 | 2025-05-12 15:57 | service@crystalgroup.in | Crystal Vizag Depot | MYRU4509035 | 40FT STD RF | Daikin | SERVICE-ON CALL | NA | NA | Power cable not available, display not working | Need to replace Diakin Dispaly, Machine has moved to Customer | Diakin Dispaly | Yes | Power cable not available, display not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY016%2F25 | RFH40R | DAIKIN | 802602 | LXE10E136A | LXE10E136A | USED | 0 | SHAHBUDDIN | No
MAY013/25 | 2025-05-13 00:35 | technician@crystalgroup.in | Lauras unit III | KKFU6710760 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Cable transducer | Temperley repaired | Discharge transducer jack& two supply sensor carrier | Yes | Cabale damaged small | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY013%2F2025 | Carrier | CARRIER-THINLINE | LSU60353959 | 541321 | 5178 | Used | NA | SHAHBUDDIN | Yes
MAY014/25 | 2025-05-13 00:40 | technician@crystalgroup.in | Lauras unit III | DFOU6120384 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | AL E407 | Temperley unit run | EIS SENSOR & PT CT BOARD | Yes | EIS SENSOR FAILURE& PTCT BOARD | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY014%2F2025 | Daikin | DAIKIN LXE10E | M004338 | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY015/25 | 2025-05-13 00:44 | technician@crystalgroup.in | Lauras unit III | PCIU1912290 | 20" | Daikin | SERVICE-AT SITE | LEASE | FOC | E407 | Temperley unit run by pass | EIS SENSOR | Yes | EIS SENSOR FAILURE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY015%2F2025 | Daikin | CARRIER-ELITLINE | M004715 | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY032/25 | 2025-05-13 23:21 | technician@crystalgroup.in | BIOCON | CCLU1035976 | 20FT STD RF- Dual Machine - Carrier Thinline with Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | PM service plan | NA | No | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY032%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | used | NA | SHAHBUDDIN | Yes
MAY031/25 | 2025-05-13 23:23 | technician@crystalgroup.in | Biocon | TRIU6681542 | 20FT STD RF With Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service & Evaprator .motor left not working | PM plan | Evaprator motor single phase for Thin Line | Yes | Evaprator motor & p. M. Service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY031%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY035/25 | 2025-05-14 17:24 | technician@crystalgroup.in | Qwik Supply | CICU2779935 | 10 ft reefer | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Advise to clean clints | NA | No | Cond. Coil dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY035%2F25 | Thermoking | TK-MP4000 | E0GM030274 | ABC782800322010476 | NA | BrandNew | NA | SHAHBUDDIN | No
MAY036/25 | 2025-05-14 17:28 | technician@crystalgroup.in | Qwik Supply | CICU2779909 | 10 ft reefer | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Advise to clean by clints | NA | No | Condenser coil dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY036%2F25 | Thermoking | TK-MP4000 | E0GM030263 | ABC782800322010201 | NA | BrandNew | NA | SHAHBUDDIN | No
MAY037/25 | 2025-05-14 17:33 | technician@crystalgroup.in | Qwik Supply Chain Pvt Ltd | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-AT SITE | LEASE | FOC | Motor Noisy | Plan for vandor | NA | Waiting for vandor respond | Motor Noisy Bearing | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY037%2F25 | Daikin | DAIKIN LXE10E | NA | NANA | NA | Used | NA | SHAHBUDDIN | Yes
MAY034/25 | 2025-05-14 17:44 | technician@crystalgroup.in | Lauras unit III | BMOU9784137 | 40" | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EIS /"STS / SHEET KEY REQUIRED | Spare on the way | DAIKIN - TEMP SENSIR-2 / EIS SENSOR- 1& SHEET KEY | Yes | Sensor's abnormal temp. Readings | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY034%2F2025 | Daikin | DAIKIN LXE10E | Mooo881 | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY033/25 | 2025-05-14 17:50 | technician@crystalgroup.in | Quick supply srihind punjab | NYKU793145 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Discharge pipe Gas leakage | Tech. On location | Brazing Rod/ R234a Gas / brazing set / vacum pump etc. | Yes | Gas leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY033%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
MAY030/25 | 2025-05-14 17:55 | technician@crystalgroup.in | Lupin Bhivandi THANE | CCLU1036859 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. & DISPLAY faded | Tech.chk | Carrier Display / Gas | Yes | Display faded & low Gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY030%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | Yes
MAY029/25 | 2025-05-14 18:01 | technician@crystalgroup.in | Ril - Retail punjab | CICU3876631 | 10" | Thermoking | SERVICE-AT SITE | LEASE | FOC | Unit high pressure tripping off compressor | Advise to clean coil with water by clints | NA | No | Condenser coil dirty with mud & dust | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY029%2F2025 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | RAJ KUMAR | No
MAY028/25 | 2025-05-17 18:59 | service@crystalgroup.in | Hetero Bio Pharma Unit 1 | CICU3876539 | 10FT STD RF | Thermoking | SERVICE-AT SITE | NA | CHARGEABLE | Display found Defective | Need Replace Display | Thermoking Magnum Plus Display | Yes | Display defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY028%2F25 | Magnum Plus | TK-MP4000 | E0GM030961 | 0222GM030291 | ABC782800321480005 | Brand New | 0 | SHAHBUDDIN | Yes
MAY040/25 | 2025-05-19 19:51 | technician@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | SJKU4000038 | 40FT HC RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. Not received to set | Spare | Carrier prime line scroll compressor/ Gadket/ filter Drier/ Gas 5kg/ vacum pump/N2 | Yes | Compressor leak back | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY040%2F25 | Carrier-Primeline | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
MAY043/25 | 2025-05-19 19:57 | technician@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | GRMU3707485 | 20FT STD - 3 machine | Carrier | SERVICE-AT SITE | LEASE | FOC | Unit not working with AL 22 | Disconnected Defective motor & wiring | Thin Line single phase Evaprator motor | Yes | Evaporator motor Defective over heating | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY043%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | used | NA | SHAHBUDDIN | Yes
MAY046/25 | 2025-05-21 11:08 | service@crystalgroup.in | ITC LTD | BMOU9785278 | 40FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Compressor not working/ No cooling | Need to change compressor terminal/ Compressor. | Compressor Terminal, Compressor, compressor gasket, refrigerant | Yes | Compressor not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY046%2F25 | RFH40R | DAIKIN | 0 | 0 | 0 | Used | 0 | RAJ KUMAR | Yes
MAY047/25 | 2025-05-22 19:27 | service@crystalgroup.in | Hetero Bio Pharma | CICU3876565 | 10FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Display not working, compressor tripping above the set temp. | Onsite check | Daikin Display | Yes | compressor tripping, temperature not going below -16 c. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY047%2F25 | Daikin | DAIKIN | 0 | 0 | 0 | Brand New | 0 | SHAHBUDDIN | Yes
MAY048/25 | 2025-05-22 19:37 | service@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | TITU9930004 | Thermoking | Plus | SERVICE-AT SITE | NA | CHARGEABLE | Display not working | Replace display | Thermoking Display | Yes | Display not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY048%2F25 | 14D8550HT | plus | 14D8550HT | EOG1000568 | 0 | NEW | 0 | SHAHBUDDIN | Yes
MAY049/25 | 2025-05-22 19:45 | service@crystalgroup.in | Zepto | KKFU6711832 | 40FT STD RF | Carrier - Thinline | SERVICE-AT SITE | NA | NA | Temperature fluctuation, breakdown | site check |  |  | site check | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY049%2F25 | Carrier - Thinline | CARRIER-THINLINE | 0 | 0 | 0 | Refurbished | 0 | RAJ KUMAR | Yes
MAY052/25 | 2025-05-26 11:47 | crm@crystalgroup.in | Qwik Supply | NYKU7931452 | 40 Feet Refer | Carrier | REPAIR | LEASE | FOC | Supply Sensor Replacement | Sensor required 2nos | Supply Sensor 2 Nos | Yes | SUPPLY SENSOR INSTALLATION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY052%2F25 | Carrier 40 Feet | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
MAY053/25 | 2025-05-26 14:32 | crm@crystalgroup.in | Qwik Supply | MYRU4501435 | 40 Feet | Daikin | SERVICE-ON CALL | LEASE | FOC | After completing PM service required spares | Keypad, Section Gas Sesor, Ambient Sensor | Keypad, Section Gas Sesor, Ambient Sensor | Yes | Spares required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY053%2F25 | DAIKIN III | DAIKIN | NA | LXE10E136A | NA | Refurbished | NA | RAJ KUMAR | Yes
MAY051/25 | 2025-05-26 18:44 | service@crystalgroup.in | RIL QWIK SUPPLY | CICU1799135 | 10FT Spl RF | Thermoking MP-4000 | SERVICE-ON CALL | NA | NA | Compressor tripping issue, Cooling Low | On call service done by technician , now cooling is okay. |  | No | Compressor tripping issue, Cooling Low | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY051%2F25 | Thermoking MP-4000 | TK-MP4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW | 0 | SHAHBUDDIN | No
MAY054/25 | 2025-05-27 19:33 | service@crystalgroup.in | Vins Bio Products Pvt Ltd | CPLU3181670 |  | NA | SERVICE-AT SITE | NA | NA | MOTOR MAKING NOISE | REPLACEMENT OF EVP Motor - 2nos | EVP Motor - 2nos | Yes | EVP Motor not working properly 2nos | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY054%2F25 | NA | NA | 0 | 0 | 0 | NA | 0 | SHAHBUDDIN | Yes
MAY055/25 | 2025-05-27 19:42 | service@crystalgroup.in | UPS | SJKU4000110 | 40FT STD RF | Thermoking | SERVICE-AT SITE | NA | NA | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | need to replace display Thermoking mp- 4000 | Thermoking mp- 4000 | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY055%2F25 | Thermoking | TK-MP4000 | 0 | 0 | 0 | Brand New | 0 | SHAHBUDDIN | Yes
MAY056/25 | 2025-05-27 19:46 | service@crystalgroup.in | UPS | HDMU5220720 | 20FT STD RF | Carrier Thineline | SERVICE-AT SITE | NA | NA | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | Replacement of of Carrier Thinline Display | Carrier Thinline Display | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY056%2F25 | Carrier Thineline | CARRIER-THINLINE | 0 | 0 | 0 | USed | 0 | SHAHBUDDIN | Yes
MAY057/25 | 2025-05-29 11:29 | service@crystalgroup.in | Hetero Unit 5 | SUDU6218004 | 40FT STD RF | Carrier-Primeline | SERVICE-AT SITE | NA | NA | Water leakage in Control Panel, Service Of Reefer Unit, need External Alarming & Mantrap system | Service needed | Mantrap system with 2nos. switch, External temp. alarm system and servicing material | Yes | Servicing of unit | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY057%2F25 | Carrier-Primeline | CARRIER-PRIMLINE | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | 0 | RAJ KUMAR | Yes
MAY058/25 | 2025-05-29 11:34 | service@crystalgroup.in | Qwik Supply Bhiwadi | CICU1799161 | 10 FT BLAST | Thermoking MP-4000 | SERVICE-AT SITE | NA | NA | Temperature not archive to set temperature, temperature fluctuation. | Site check. |  | No | Temperature not archive to set temperature, temperature fluctuation. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY058%2F25 | Thermoking MP-4000 | TK-MP4000 | 0 | LSM60198823 | 0 | BRand NEW | 0 | SHAHBUDDIN | Yes
MAY059/25 | 2025-05-29 11:37 | service@crystalgroup.in | Qwik Supply Bhiwadi | CICU2094031 | 10 ft reefer | Thermoking | SERVICE-AT SITE | NA | NA | Temperature not archive to set temperature, temperature fluctuation. | site check |  | No | Temperature not archive to set temperature, temperature fluctuation. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY059%2F25 | Thermoking | Magnum Plus | E0GM029789 | ABC782800321480264 | 0 | BrandNew | 0 | SHAHBUDDIN | Yes
MAY061/25 | 2025-06-04 15:44 | crm@crystalgroup.in | DHL | TCLU1912270 | 20 Feet | Daikin | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | NEED TO SET TEMPERATURE |  |  | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY061%2F25 | 20 Feet | TK-MP3000 | NA | NA | NA | NA | NA | RAJ KUMAR | Yes
MAY062/25 | 2025-06-04 16:27 | crm@crystalgroup.in | Lauras Lab Unit 2 | PRGU4958724 | 40 Feet | Carrier | SERVICE-AT SITE | LEASE | FOC | Controller Panel | HTT Sensor, Defrost Sensor & Keypad | HTT Sensor, Defrost Sensor & Keypad - Qty 01 Nos | Yes | Controlller Panel | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY062%2F25 | 40 Feet | CARRIER-THINLINE | NA | NA | NA | NA | NA | RAMIZ | Yes
JUN024/25 | 2025-06-07 16:37 | crm@crystalgroup.in | Qwik Supply | PCIU6015055 | 40 FEET | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DOOR STRUCTURE DAMAGE | ARRANGING A STRUCTURE PERSON | NA | No | DOOR DAMAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN024%2F25 | DAIKIN | DAIKIN LXE10E | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
JUN028/25 | 2025-06-07 16:43 | crm@crystalgroup.in | NSR TRADER | TCLU1112683 | 40 FEET | THERMOKING | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR CONTACTOR BURNED | TEMPERARLY RUN WITH ONE CONTACTOR BYPASS | TK MP 3000 COMPRESSOR CONTACTOR | Yes | COMPRESSOR CONTACTOR BURNED, FOR TIME BEING RUNNING WITH ONE CONTACTOR BYPASS | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN028%2F25 | THERMOKING | TK-MP3000 | NA | NA | NA | USED | NA | RAMIZ | Yes
JUN029/25 | 2025-06-07 16:47 | crm@crystalgroup.in | Cipla | CXRU1033787 | 40FT STD RF - Dual Machine Daikin with Anti Room + Heater | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | ARRANGING THIRD PARTY VENDOR OR TECHNICIAN |  | No | SUSPECTED TOP ROOF LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN029%2F25 | DAIKIN | DAIKIN LXE10E | M001107 | K31412141829 | DECOS 3F 2557 / 1 | used | NA | SHAHBUDDIN | Yes
JUN030/25 | 2025-06-07 16:49 | crm@crystalgroup.in | Cipla | CXRU1033344 | 40FT STD RF - Dual Machine Daikin with Anti Room | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | ARRANGING VENDOR OR TECHNICIAN O SITE |  | No | WATER LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN030%2F25 | DAIKIN | DAIKIN LXE10E | M001118 | K31411114078 | DECOS 3F 2609 / 1 | Used | NA | SHAHBUDDIN | Yes
JUN032/25 | 2025-06-07 16:53 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | CXRU1036019 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | BREAKDOWN - ALARM E1O1 | ARRANGING TECHNICIAN |  | No | ALARM E1O1 HIGH PRESSURE TRIPPING OFF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN032%2F25 | DAIKIN | DAIKIN LXE10E | M001044 | K31511115441 | DECOS 3F 2513 / 1 | used | NA | RAMIZ | Yes
JUN033/25 | 2025-06-09 13:08 | crm@crystalgroup.in | Crystal Yard | CICU1442256 | 40' Blast | NA | REPAIR | STOCK | NA | Internal Panel Delaminatd to Laminted Patch with foamQty 04 Nos | Internal Panel Delaminatd to Laminted Patch with foamQty 04 Nos |  | No | Foaming Work fo Internal Panel | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN033%2F25 | Thermoking | TK-MP4000 | EOG5003933 | 220916, 3.29.00 | NA | brand New | NA | SHAHBUDDIN | Yes
JUN034/25 | 2025-06-09 13:11 | crm@crystalgroup.in | Crystal Yard | MWCU5709930 | 20FT STD RF | Carrier | REPAIR | STOCK | NA | External Panel Welding | WELDING WORK |  | No | EXTERNAL PANEL CUT AND WELD TO THE PATCH | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN034%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN049/25 | 2025-06-12 16:23 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | MYRU4515260 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | Sensor are not working | EVP INLET SENSOR & EVP OUTLET SENSOR | EVP INLET SENSOR & EVP OUTLET SENSOR QTY 1 EACH | Yes | PM Service complete & sensor Required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN049%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | NA | RAMIZ | Yes
JUN051/25 | 2025-06-12 16:34 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | GRMU3707525 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | PM Service done & spares required | Spares required | KEYPAD 1 EIS SENSOR 2 FOS SENSOR 2 EXPANSION COIL 1 EXPANSION VALVE 1 FILTER DRIER 1 Brizing Set inclu Nitrogen & Vaccum 1 | Yes | PM Service Completed & spares required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN051%2F25 | Daikin | DAIKIN | NA | NA | NA | used | NA | RAMIZ | Yes
JUN050/25 | 2025-06-12 16:37 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | MYRU4515260 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | PM Service Complete & Some spares required | Spares Required | KEYPAD 1 NO Display 1 NO EVP Motor 2 Nos | Yes | PM Service done | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN050%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | NA | RAMIZ | Yes
JUN037/25 | 2025-06-13 12:31 | technician@crystalgroup.in | Land Flavor Gonda Factory | CXRU1043337 | 40" | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Temp. Not received at set point. | Suggest to replaced Reefer unit bu verendra | NA | No | Compressor faulty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN037%2F25 | Carr | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | Yes
JUN054/25 | 2025-06-13 16:57 | crm@crystalgroup.in | Lauras Lab Unit 1 | TITU9930011 | 40FT Spl RF | Thermoking TK 4000 | SERVICE-AT SITE | LEASE | FOC | Compressor Contactor Burned | Contactor burned, Transformer Not Working | Contactor 01 nos | Yes | Contactor burned, Transformer Not Working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN054%2F25 | Thermoking MP-4000 | TK-MP4000 | 14D8568HT | EOG1000566 | NA | Used | NA | RAMIZ | Yes
JUN059/25 | 2025-06-14 21:17 | technician@crystalgroup.in | Tata Advanced Systems Ltd | CZZU6009100 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Key pad Al E 406 | Need to replaced | Daikin key pad set | Yes | Key pad Defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN059%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | Yes
JUN058/25 | 2025-06-14 21:20 | technician@crystalgroup.in | Biocon | TRIU6681542 | 20FT STD RF With Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | Evp. Motor break down no.1NA | Need to replaced | Evaprator motor single phase carrier thin line | Yes | Found old model motor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN058%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN031/25 | 2025-06-16 16:56 | operation@crystalgroup.in | Crystal Yard | BMOU9788370 | 40FT STD RF | Daikin | REPAIR | STOCK | FOC | Machine Installation | NA |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN031%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No
JUN065/25 | 2025-06-17 17:13 | technician@crystalgroup.in | CIPLA UNIT - VI | CRIU4024028 | 40FT 2BAY RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | PM Due | Arrange pm & on the way tech. | NA | No | P. M Due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN065%2F25 | Thermoking | TK-MP4000 | CIM1051752 | NA | NA | New | NA | SHAHBUDDIN | Yes
JUN064/25 | 2025-06-17 17:19 | technician@crystalgroup.in | CIPLA UNIT - VI | CRIU4024012 | 40FT 2BAY RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | P M Due | Arrange tech. | NA | No | Due pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN064%2F25 | Thermoking | TK-MP4000 | CIM1048772 | NA | NA | New | NA | SHAHBUDDIN | Yes
JUN060/25 | 2025-06-17 17:32 | technician@crystalgroup.in | Quick supply Ril Haryana | TITU9927240 | 10"" | Thermoking mp 4000 | SERVICE-AT SITE | LEASE | FOC | Unit not working due to Power MOUDULE Defective | On the way spare | Tk mp 4000 power MOUDULE | Yes | Piwer issue fluctuations | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN060%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | RAJ KUMAR | Yes
JUN068/25 | 2025-06-23 22:04 | technician@crystalgroup.in | Swadesh milk barabanki UP | GESU9290991 | 40" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | No cooling | Temperley advise to check leak | R134a Gas/ N2/ Filter Drier ...if leak need brazing set& vacum pump | Yes | Suspected leak or Filter Drier choked | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN068%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes
JUN076/25 | 2025-06-24 12:32 | operation@crystalgroup.in | Crystal Yard (Dr. Reddy's Laboratories Ltd.) | SJKU4000038 | 40FT STD RF | NA | REFURBISHMENT OF CONTAINER | SALE | FOC | Container to be ready | - | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal Paint & logo | Yes | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN076%2F25 | - | CARRIER-PRIMLINE | - | - | - | Brand new | - | Thakur | No
JUN078/25 | 2025-06-25 17:40 | operation@crystalgroup.in | Crystal Yard (HQIDS) | CICU3780951 | 20GP | DRY CONTAINER | REFURBISHMENT OF CONTAINER | SALE | FOC | Logo ANC_ 5.5ft x 2.5ft | NA | Logo ANC_ 5.5ft x 2.5ft |  | Logo ANC_ 5.5ft x 2.5ft | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN078%2F25 | NA | DRY | NA | NA | NA | NA | NA | Thakur | No
JUN079/25 | 2025-06-25 17:45 | operation@crystalgroup.in | Crystal Yard (HQIDS) | FWRU0324937 | 20GP | NA | REFURBISHMENT OF CONTAINER | SALE | NA | Logo ANC_ 5.5ft x 2.5ft | NA | Logo ANC_ 5.5ft x 2.5ft | Yes | Logo ANC_ 5.5ft x 2.5ft | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN079%2F25 | NA | DRY | NA | NA | NA | NA | NA | Thakur | No
JUN043/25 | 2025-06-26 14:27 | operation@crystalgroup.in | Crystal Yard | MYRU4509035 | 40FT STD RF | NA | PREVENTIVE MAINTENANCE | STOCK | FOC | PTI Test | PTI | NA | No | PTI to be carried out | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN043%2F25 | Daikin | DAIKIN | 802602 | LXE10E136A | NA | Used | NA | Thakur | Yes
JUN082/25 | 2025-06-26 21:49 | technician@crystalgroup.in | DEVIS LAB | DC SEZ NO:4 | 40" | Carrier Thin Line | SERVICE-AT SITE | SALE | CHARGEABLE | Condenser coil Gas leak | Unit under N2 test | Condenser coil new | Yes | Gas leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN082%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN075/25 | 2025-06-27 11:15 | crm@crystalgroup.in | Tata Advance System | BM0U9788370 | 40 FT Reefer | Daikin | REFURBISHMENT OF CONTAINER | LEASE | FOC | Data Logger and Genset Installation | NA | Data Logger, Genset | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN075%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | No
JUN067/25 | 2025-06-27 14:26 | crm@crystalgroup.in | Crystal Yard | MSCU5621100 | 40 GP Dry | NA | REPAIR | STOCK | NA | NA | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN067%2F25 | NA | DRY | NA | NA | NA | Used | NA | Thakur | No
JUN083/25 | 2025-06-27 15:24 | crm@crystalgroup.in | ITC LIMITED, FOODS DIVISION | TRUL5253890 | 40 HC Dry | NA | SERVICE-AT SITE | LEASE | FOC | LEAKAGE FOUND | NA | NA | No | LEAKAGE FROM TOP | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN083%2F25 | NA | DRY | NA | NA | NA | USED | NA | RAJ KUMAR | No
JUN081/25 | 2025-06-27 17:27 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | TITU9930032 | 40FT Spl RF | Carrier | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | EVP Motor Noisy Bearing issue | BEARING TO BE REPLACED | BEARING | Yes | EVP MOTOR NOISY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN081%2F25 | Carrier Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN086/25 | 2025-07-01 10:06 | crm@crystalgroup.in | Qwik Supply | TCLU1130265 | 40FT STD RF | TK MP 3000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | EVP coil sensor and TK-MP-3000 return temp sensor | NA | EVP coil sensor and TK-MP-3000 return temp sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN086%2F25 | Thermoking | TK-MP3000 | NA | NA | NA | Refurbished | NA | RAMIZ | Yes
JUN080/25 | 2025-07-01 15:23 | crm@crystalgroup.in | Qwik Supply | CXRU1043912 | 40FT STD RF | Daikin | SERVICE-ON CALL | LEASE | FOC | PT and CT board Defective, Suspected - Controller and current transformer | NA |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN080%2F25 | Daikin | DAIKIN | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | NA | RAMIZ | Yes
JUN085/25 | 2025-07-01 18:21 | crm@crystalgroup.in | Qwik Supply | CICU2779909 | 10 ft reefer | TK MP 4000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Sensor not working | NA | Sensors required | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN085%2F25 | Thermoking | TK-MP4000 | E0GM030263 | ABC782800322010201 | NA | BrandNew | NA | RAMIZ | Yes
JUN084/25 | 2025-07-01 18:22 | operation@crystalgroup.in | Qwik Supply | CICU2779935 | 10 ft reefer | TK-MP-4000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Sensor nor working | Container under warranty |  | Yes | Sensor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN084%2F25 | Thermoking | TK-MP4000 | E0GM030274 | ABC782800322010476 | NA | BrandNew | NA | RAMIZ | Yes
JUN091/25 | 2025-07-02 10:41 | technician@crystalgroup.in | soft box | TITU8257288 | 40" | Thermoking mp 4000 | SERVICE-AT SITE | SALE | FOC | low Gas in system | Required Gas adding to system | R404A Gas- 3 KG | Yes | minar leak system need to chech | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN091%2F25 | TK MP 4000 | TK-MP4000 | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
JUN087/25 | 2025-07-02 10:46 | technician@crystalgroup.in | HETRO 5 | CXRU1186467 | 40" | DKN | SERVICE-AT SITE | SALE | FOC | PM service & Man trap & Hetro own sensor Instalation | PM & Instalation job under progress | .an trap light/switch/buttan/ silicon sealant/ Ins.tape/ nut bolts etc. | Yes | PM DUE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN087%2F25 | DKN | DAIKIN LXE10E | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes
JUL001/25 | 2025-07-02 10:52 | operation@crystalgroup.in | Avenue Supermarts LTD-Dmart | HDMU4698329 | 40FT | NA | REPAIR | LEASE | FOC | Door Gasket Issue | NA | Rubber Gasket | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL001%2F25 | NA | DRY | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN090/25 | 2025-07-05 15:30 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1326276 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | CHARGEABLE | Water lekage at back side of reefer container | NA |  | No | Water lekage at back side of reefer container | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN090%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
JUN092/25 | 2025-07-05 16:23 | crm@crystalgroup.in | Tata Advance | BMOU9788370 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | Container is on Auto defrosting mode | NA | No | No | Container is on Auto defrosting mode | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN092%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
JUL006/25 | 2025-07-07 17:12 | crm@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20FT STD RF | Daikin | SERVICE-AT SITE | SALE | FOC | The internal temperature has reached 21°C and the cooling unit is not functioning. | Call alined with Ajay Technician at our Yard |  | No | The internal temperature has reached 21°C and the cooling unit is not functioning. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL006%2F25 | Daikin | DAIKIN | LXIDEA33A | NA | NA | Used | NA | Thakur | Yes
JUL005/25 | 2025-07-08 17:53 | operation@crystalgroup.in | Qwik Supply Chain | CXRU1040322 | 40FT | Daikin | SERVICE-ON CALL | LEASE | FOC | Contactor connection burn | New Connection refix | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL005%2F25 | Daikin | DAIKIN | M001862 | K31403112957 | DECOS 3F / 2609 / 1 | Used | NA | RAJ KUMAR | Yes
JUL002/25 | 2025-07-08 18:34 | crm@crystalgroup.in | Sai Life Science | MYRU4507120 | 40 FT | Daikin | SERVICE-AT SITE | SALE | AMC | Comprassor chowk, Gas needs to refill | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL002%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No
JUN074/25 | 2025-07-11 10:45 | crm@crystalgroup.in | Dr Reddy | TITU9930114 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | TKMP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | Complaint attended | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN074%2F25 | Thermoking | TK-MP4000 | 14E219055 | EOG1000667 | NA | USED | NA | SHAHBUDDIN | Yes
JUL007/25 | 2025-07-12 12:21 | crm@crystalgroup.in | Hetero Labs Unit 3 | CXRU1550769 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor Grounded. | NA | Carrier Primeline comprassor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL007%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
JUL010/25 | 2025-07-15 10:29 | crm@crystalgroup.in | Sai Life Science | PCIU6008328 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | PTCT Board, IO Board and Controller not working. | NA | PT/CT BOARD CONTROLLER DECOS III D ( OLD MODEL) I/O BOARD- SUSPECTED | Yes | Instalation time wrong power supply connection with wrong harness PT/ CT Board fixed by sai Lab. Due to this reason PT/CT Board & container got damaged/ | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL010%2F25 | Daikin | DAIKIN | NA | NA | NA | used | JSGA622340291 | SHAHBUDDIN | Yes
JUL011/25 | 2025-07-15 12:21 | crm@crystalgroup.in | Qwik Supply Chain Pvt Ltd | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-AT SITE | LEASE | FOC | The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze. | NA |  | No | The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL011%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | AKSHAY | Yes
JUL008/25 | 2025-07-16 10:24 | crm@crystalgroup.in | OLD MUMBAI ICECREAM DAIRY | CCLU1030531 | 20FT | Daikin | INSTALLATION | SALE | CHARGEABLE | Display not working. | NA | Display | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL008%2F25 | Daikin | DAIKIN | NA | NA | NA | New | NA | SHAHBUDDIN | Yes
JUL012/25 | 2025-07-16 10:44 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd, | CXRU1030387 | 40FT STD RF with Anteroom | Carrier Primeline | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor not working | NA | Compressor- Carrier Primeline Filter Drier Compressor Gasket Compressor Oil Gas- 134a- 5kg's Vaccum pump | Yes | Need to change compressor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL012%2F25 | DAikin | CARRIER-PRIMLINE | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | NA | SHAHBUDDIN | Yes
JUL013/25 | 2025-07-18 16:54 | technician@crystalgroup.in | Quick supply Ril | CICU277991 | 10" | TK | SERVICE-AT SITE | LEASE | FOC | Internal Light not working. | repair will done by clints | Tube light / cable 10mt.( 2.5 two core) casing pati-1 & 16 A single pole MCB. ETC..... | Yes | Light wiring shirtage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL013%2F25 | TK | TK-MP4000 | na | na | na | New | na | RAJ KUMAR | No
JUL025/25 | 2025-07-22 17:49 | service@crystalgroup.in | ISKON | Site Cabin 64 | Customised Cabin | NA | REPAIR | SALE | CHARGEABLE | Floor Damage | Need to inspect the unit | NA | will confirm after inspection | Floor Damage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL025%2F25 | NO | NA | NA | NA | NA | NEW | NA | AKSHAY | Yes
JUL019/25 | 2025-07-22 18:09 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | Unit temp not maintaining | We've top-up 0.5kg gas by cleaning the condenser coil. | R-134a Gas 0.5Kg | Yes | Unit has condenser coil dusty & gas less | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL019%2F25 | DAIKIN | DAIKIN | LXIDEA33A | NA | NA | USED | JSGA623040170 | RAJ KUMAR | Yes
JUL024/25 | 2025-07-22 18:13 | service@crystalgroup.in | Royal Bhutan Army | CICU1799860 | 20RF | THERMOKING MP4000 | SERVICE-ON CALL | SALE | CHARGEABLE | Unit not working | Temporary runned in bypass mode, currently under observation | after observation | will confirm after observation. | Unit Not working due to power issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL024%2F25 | TK MP4000 | TK-MP4000 | NA | NA | NA | NEW | NA | SHAHBUDDIN | No
JUL026/25 | 2025-07-23 10:37 | service@crystalgroup.in | Sai Life Science | PCIU6008328 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Unit not working. | need to replace controller, display, also have to check the transformer. | Controller Decos 3d, Transformer & display | Yes | Unit not working due to controller & display defective. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL026%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | JSGA622340291 | RAMESH | Yes
JUL018/25 | 2025-07-23 16:45 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1026520 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | GAS NEEDS TO BE REFILED | NA | ONLY GAS REQURIED | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL018%2F25 | Daikin | DAIKIN | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | RAMESH | Yes
JUL003/25 | 2025-07-24 12:24 | operation@crystalgroup.in | Tianish | TRLU174160 | 40FT | Thermoking | SERVICE-AT SITE | SALE | FOC | Compressor making abnormal sound, found burn relay connection pin melt | Compressor to be replaced, Relay board to be replaced | 1)Compressor - 1 2)Relay Board -1 3) R404A 4 kg 4) Display -1 | Yes | Compressor making abnormal sound, found burn relay connection pin melt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL003%2F25 | Thermoking | TK-MP3000 | NA | NA | NA | USED | NA | SITARAM | Yes
JUL033/25 | 2025-07-25 10:39 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6034374 | 40FT STD RF | Daikin | SERVICE-AT SITE | SALE | CHARGEABLE | General Inspection done | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL033%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | RAMESH | No
JUL025/25 | 2025-07-28 14:06 | crm@crystalgroup.in | ISKON | Site Cabin 64 | 10FT | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL025%2F25 | NA | DRY | NA | NA | NA | NA | NA | AKSHAY | No
JUL061/25 | 2025-07-29 11:29 | crm@crystalgroup.in | Crystal Yard | PCIU6007065 | 40FT STD RF | DAIKIN | REPAIR | STOCK | CHARGEABLE | Evaporator motor stuck | NA | NA | REPAIR | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL061%2F25 | Daikin | DAIKIN | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | No
JUL062/25 | 2025-07-29 12:55 | crm@crystalgroup.in | Tianish | TRLU174160 | 40FT STD RF | Thermo King | SERVICE-AT SITE | LEASE | FOC | Spares requrierd on sites | NA | Compressor Rellay Board DISPLAY | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL062%2F25 | NA | TK-MP3000 | NA | NA | NA | USED | NA | SITARAM | Yes
JUL009/25 | 2025-07-30 12:36 | crm@crystalgroup.in | Orbittal Electromech Engg. Projects Pvt. Ltd | Site Cabin 59 | NA | NA | REPAIR | LEASE | FOC | LEAKAGE ISSUE FROM TOP | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL009%2F25 | NA | DRY | NA | NA | NA | NA | NA | THAKUR | No
JUL027/25 | 2025-07-30 12:57 | service@crystalgroup.in | EmCure | CICU1938143 | 20RF | THERMOKING MP3000 | SERVICE-AT SITE | SALE | CHARGEABLE | set point changing automatically | controller already sent with configuration | software version | software required | set point changing automatically | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL027%2F25 | THERMOKING MP-3000 | TK-MP3000 | NA | NA | NA | NEW | NA | SHAHBUDDIN | No
JUL038/25 | 2025-07-30 14:25 | service@crystalgroup.in | Dr. Reddy's FTO-9 | TRIU6616969 | 20RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | temp not maintaining | need to visit | - | will confirm after inspection | temp not maintaining | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL038%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA622340507 | SITARAM | Yes
JUL042/25 | 2025-07-30 17:47 | service@crystalgroup.in | Zepto | KKFU6711832 | 40RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | unit has evp contactor burnt | client will replace the contactor | - | No | unit has evp contactor burnt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL042%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA623040288 | SHAHBUDDIN | No
JUL058/25 | 2025-07-30 17:55 | service@crystalgroup.in | JUBILANT | GRMU3607418 | 20RF | DAIKIN | SERVICE-ON CALL | LEASE | FOC | as per customer temperature isn't falling | during observation on-call unit found working fine | na | No | during observation on-call unit found working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL058%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No
JUL060/25 | 2025-07-30 18:08 | service@crystalgroup.in | Dr reddy cto 3 | GSOU6384240 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | unit has evp motor defective (three phase), running in bypass mode | need to replace evp motor | Evp motor three phase | Yes | evp motor in bypass mode (three phase) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL060%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA622340472 | RAMESH | Yes
JUL082/25 | 2025-07-30 18:23 | service@crystalgroup.in | Lauras Lab Unit 2 | CXRU1036533 | 40RF | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | AMC | PM SERVICE DUE | PM DONE | NA | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL082%2F25 | DAIKIN | DAIKIN | M000451 | NA | NA | USED | JSGA623040306 | SITARAM | Yes
AUG002/25 | 2025-08-01 16:01 | crm@crystalgroup.in | CRYSTAL YARD | CRIU2024327 | 20FT STD RF | THERMOKING | NA | STOCK | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG002%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | No
AUG003/25 | 2025-08-01 16:04 | crm@crystalgroup.in | CRYSTAL YARD | CRIU2024311 | 20FT STD RF | THERMOKING | NA | STOCK | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG003%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | No
JUL087/25 | 2025-08-02 16:00 | service@crystalgroup.in | Balaji Enterprises | TRIU6616911 | 20RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | EVP MOTOR NOT WORKING | BYPASSED ONE EVP MOTOR & UNDER TROUBLESHOOTING |  | CONFIRMATION PENDING | EVP MOTOR NOT WORKING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL087%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | M3X60329564 | NA | Used | NA | SHAHBUDDIN | Yes
JUL059/25 | 2025-08-04 15:11 | service@crystalgroup.in | ITC Ltd | MYRU4519748 | 40RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | temperature not falling | NEED TO ARRANGE TECHNICIAN AT SITE | NA | WILL CONFIRM AFTER ATTENDANCE | TEMP NOT FALLING & WHITE DISPLAY NOT VISIBLE PROPERLY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL059%2F25 | DAIKIN | DAIKIN | M003143 | NA | NA | NA | JSGA623040176 | RAMESH | Yes
AUG007/25 | 2025-08-08 16:11 | service@crystalgroup.in | Qwik Supply Chain Private Limited | CICU3876591 | 10RF | THERMOKING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMP NOT FALLING | NAT | NA | No | Unit is working fine without any alarms | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG007%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | NA | NA | SHAHBUDDIN | No
AUG011/25 | 2025-08-11 15:35 | service@crystalgroup.in | PARLE | CXRU1041123 | 40FT STD RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | Unit has sheet key defective | instructed client to replace the sheet key | sheet key | Yes | unit has sheet key defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG011%2F25 | DAikin | DAIKIN | M002147 | K31408135759 | DECOS 3F / 2609 / 1 | Used | na | SHAHBUDDIN | No
JUL084/25 | 2025-08-11 17:35 | service@crystalgroup.in | PI Industries | CXRU1035856 | 40RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | EVP MOTOR DEFECTIVE | need to replace evp motor | EVP MOTOR | Yes | evp motor defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL084%2F25 | DAIKIN | DAIKIN | M000552 | K31412143316 | DECOS 3F 2553 / 1 | USED | NA | SHAHBUDDIN | Yes
AUG001/25 | 2025-08-12 11:22 | service@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | SEGU9511192 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | ICE FROSTING ON EVP COIL AND MOTOR | removed the ice. | na | No | ice frosting on evp coil and motor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG001%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | na | NA | NA | USED | NA | SHAHBUDDIN | Yes
AUG012/25 | 2025-08-12 11:35 | service@crystalgroup.in | MANTRA EVENTS AND PROMOTIONS PRIVATE LIMITED | CKLU2058158 OOLU1481295 WHLU0279473 TCKU2842760 | 20DV | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | INSPECTED & PURCHASED | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG012%2F25 | NA | DRY | NA | NA` | NA | USED | NA | AKSHAY | No
JUL088/25 | 2025-08-14 11:51 | service@crystalgroup.in | WOCKHARDT | JXLU517262 | 40RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | UNIT HAS CONTROLLER & SENSORS DEFECTIVE | NA | CONTROLLER DECOS 3D & SENSORS | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL088%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No
JUL083/25 | 2025-08-14 12:02 | service@crystalgroup.in | HETERO UNIT 5 | SUDU6218004 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | NEED TO INSTALL MAN TRAP ALARM | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL083%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | RAMESH | Yes
AUG014/25 | 2025-08-16 12:58 | operation@crystalgroup.in | Qwik Supply | MYRU45183545R1 | 40ft | Daikin | Breakdown | LEASE | FOC | MYRU45183545R1 | Replacement of Contactor | Contactor | Yes | Contactor burned | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG014%2F25 | Daikin | DAIKIN | MYRU45183545R1 | DCOZ3E | JSGA622180065 | used | M005086 | RAJ KUMAR | Yes
AUG015/25 | 2025-08-16 16:01 | operation@crystalgroup.in | Qwick Supply | TDRU7151675 | 40FT Spl RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG015%2F25 | Daikin | DAIKIN | RFG20R | NA | NA | RefurbiShed | JSGA622180053 | RAJ KUMAR | Yes
AUG016/25 | 2025-08-16 16:05 | operation@crystalgroup.in | Qwik Supply Chain Pvt Ltd | MYRU4518356 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG016%2F25 | Daikin | DAIKIN | M005086 | DCOZ3E | NA | Used | JSGA622180065 | RAJ KUMAR | Yes
AUG017/25 | 2025-08-16 16:08 | operation@crystalgroup.in | Qwik Supply Chain Pvt Ltd | TCLU1903088 | 20FT STD RF | NA | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG017%2F25 | Daikin | DAIKIN | RFG20R | NA | NA | Used | JSGA622180051 | RAJ KUMAR | Yes
AUG018/25 | 2025-08-16 16:26 | operation@crystalgroup.in | Luckhnow International Airport | TRIU6618581 | 20FT STD RF | NA | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG018%2F25 | Carrier - Thinline | DAIKIN | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | RFG20R | RAJ KUMAR | Yes
AUG013/25 | 2025-08-18 18:18 | service@crystalgroup.in | CIPLA | TRIU6681434 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | UNIT IS HAVING SENSOR ISSUES ( RETURN & SUPPLY SENSOR) | NEED TO REPLACE SENSORS | SUPPLY SENSOR -2 NOS & RETURN SENSOR - 01 NOS | Yes | SENSOR FAULTY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG013%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA623040304 | NEMICHAND | Yes
AUG043/25 | 2025-08-21 12:20 | service@crystalgroup.in | Navios Automation Pvt Ltd | CRIU2024311,CRIU2024327 | 20RF | THERMOKING MP4000 | INSTALLATION | SALE | CHARGEABLE | INSTALLATION OF 02 UNITS. | INSTALLATION OF 02 UNITS | - | No | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG043%2F25 | TK MP 4000 | TK-MP4000 | NA | NA | NA | NEW | NA | NEMICHAND | Yes
AUG010/25 | 2025-09-02 14:59 | service@crystalgroup.in | QWIK SUPPLY | TDRU7151504 | 40RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | RETURN SENSOR DEFECTIVE | NEED TO REPLACE RETURN SENSOR | Return Sensor | Yes | RETURN SENSOR DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG010%2F25 | THERMOKING | TK-MP3000 | NA | NA | NA | USED | NA | NEMICHAND | Yes
AUG035/25 | 2025-09-02 16:31 | service@crystalgroup.in | Divis labs | CGMU4984529 | 40RF | CARRIER THINLINE | PREVENTIVE MAINTENANCE | SALE | FOC | PM CARRIED OUT | NEED TO CARRYOUT PM | - | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG035%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | Yes
AUG055/25 | 2025-09-02 18:15 | service@crystalgroup.in | ITC | PCIU6007065 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | have to check | NA | No | unit not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG055%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | NEMICHAND | Yes
AUG045/25 | 2025-09-02 18:28 | service@crystalgroup.in | DIVIS LAB | APRU5390955 | 40RF | CARRIER | SERVICE-AT SITE | LEASE | FOC | ice frosting on evp coil areaa | need to remove the ice | screw and revit required | screw & revit required - 20-20 nos | ice frosting on evp coil area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG045%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
SEP017/25 | 2025-09-03 17:51 | service@crystalgroup.in | Crystal Depot | NA | NA | NA | NA | STOCK | NA | - | - |  | Yes | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP017%2F25 | NA | NA | NA | - | - | - | - | NO | No
AUG047/25 | 2025-09-06 14:52 | service@crystalgroup.in | Crystal Yard | PCIU6007065 | 40FT STD RF | DAIKIN | REPAIR | STOCK | CHARGEABLE | EVP MOTOR DEFECTIVE | NA | EVP MOTOR | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG047%2F25 | Daikin | DAIKIN | NA | NA | NA | Refurbished | NA | RAMESH | No
AUG050/25 | 2025-09-06 15:03 | service@crystalgroup.in | CRYSTAL DEPOT | NA | NA | TOYO AIR COMPRESSOR | NA | NA | NA | NA | NA | NEW AIR COMPRESSOR - TOYO BRAND | Yes | NEW AIR COMPRESSOR | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG050%2F25 | NA | NA | NA | NA | NA | NEW | NA | Shubham Tank | No
SEP001/25 | 2025-09-06 15:27 | service@crystalgroup.in | SWADESH MILK DAIRY | GESU9290991 | 40FT STD RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | UNIT HAS MULTIPLE LEAK FROM EVP COIL... | NEED TO REPLACE THE EVP COIL | EVP COIL | Yes | Unit i | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP001%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SITARAM | Yes
SEP002/25 | 2025-09-06 15:32 | service@crystalgroup.in | SWADESH MILK DAIRY | NYKU7932356 | 40FT STD RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | AMC | WORKING FINE | UNIT IS WORKING FINE | NO | No | UNIT IS WORKING FINE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP002%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SITARAM | Yes
SEP020/25 | 2025-09-06 15:38 | service@crystalgroup.in | SAI LIFE SCIENCE | PCIU6008328 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT NOT WORKING | REPLACEMENT OF REEFER UNIT | REEFER MACHINERY UNIT | MACHINERY UNIT SWAPPING | UNIT NOT WORKING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP020%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | JSGA622340291 | SHAHBUDDIN | Yes
SEP060/25 | 2025-09-22 10:11 | technician@crystalgroup.in | CELON LABORATORIES PRIVATE LIMITED | TRIU6616871 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Pm service due | Tech. On the way | Na | No | Pm due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP060%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes
SEP057/25 | 2025-09-23 12:21 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | temperature not maintaining | need to refill the gas | R-134a Gas Required 5kg, Vaccume Pump Required | R-134a Gas Required 5kg, Vaccume Pump Required | gas found contaminated | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP057%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | Yes
SEP034/25 | 2025-09-23 16:01 | service@crystalgroup.in | Quick supply chain PVT LTD | CICU3876544 | 10RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | unit has compressor ground | UNIT COVERS U/W & IT HAS COMPRESSOR GROUND | COMPRESSOR WILL BE PROVIDED BY KK TEAM | Yes | UNIT HAS COMPRESSOR GROUND | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP034%2F25 | Thermoking MP4000 | TK-MP4000 | NA | NA | NA | NEW | NA | SITARAM | Yes
SEP067/25 | 2025-09-25 18:07 | service@crystalgroup.in | Quick supply | SJKU4000022 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | unit has condenser motor noisy | need to repairs | bearing | bearing required | condenser motor noisy | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP067%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | SITARAM | Yes
SEP079/25 | 2025-09-27 11:52 | service@crystalgroup.in | Quick supply | CICU3876631 | 10FT STD RF | Thermoking MP 4000 | SERVICE-ON CALL | LEASE | FOC | unit wasn't working | resolved the error by rectifying the power supply issues | na | No | due to improper power supply | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP079%2F25 | Thermoking | TK-MP4000 | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New | NA | SITARAM | No
AUG046/25 | 2025-09-27 16:25 | service@crystalgroup.in | Qwik supply chain Pvt Ltd | APRU5066497 | 40RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | unit found to be working fine | NAT | NA | No | UNIT FOUND TO BE WORKING FINE WITHOUT ANY ISSUES. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG046%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | No
AUG057/25 | 2025-09-29 16:11 | service@crystalgroup.in | Qwik Supply Chain Pvt Ltd | MYRU45183545R1 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT IS IN OFF CONDITION | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD NEEDS TO REPLACE | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD. | Yes | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD NEEDS TO REPLACE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG057%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | Yes
SEP019/25 | 2025-09-29 16:32 | service@crystalgroup.in | Curia India Pvt.Ltd. | TRIU6680649 | 20RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | UNIT IS WORKING FINE AS PER CLIENT. | NAT | NA | No | UNIT IS WORKING FINE AS PER CLIENT. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP019%2F25 | CARRIER | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | No
SEP026/25 | 2025-09-29 17:30 | service@crystalgroup.in | UPS | SJKU4000110 | 40RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | SET TEMP ISSUE | SET TEMP WAS +20.0C & THE SAME WAS CHANGED TO +3.5C BY INCREASING THE DISPLAY BRIGHTNESS. | NO | No | SET TEMP ISSUE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP026%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
SEP035/25 | 2025-09-29 17:50 | service@crystalgroup.in | Aspiro pharma ltd | CAIU5422720 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT HAS SHEET KEY DEFECTIVE | NEED TO REPLACE THE SHEET KEY. | SHEET KEY | Yes | UNIT HAS SHEET KEY DEFECTIVE. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP035%2F25 | DAikin | DAIKIN | NA | NA | NA | Used | JSGA622340482 | SHAHBUDDIN | Yes
OCT017/25 | 2025-10-04 17:55 | crm@crystalgroup.in | Lauras lab unit 1 | CICU1442209 | 40-RF 2 bay unit | 2021 | SERVICE-ON CALL | SALE |  | Deforestation issue | NA |  | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT017%2F25 |  | TK-MP4000 | NA | Na | NA | Na | Na | SITARAM | No
SEP092/25 | 2025-10-06 17:20 | service@crystalgroup.in | ASPIRO PHARMA - KARKAPATLA | MWCU2991560 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | UNIT NOT WORKING | NEED TO REPLACE THE CAPACITOR | CONDENSER CAPACITOR | Yes | UNIT HAS CONDENSER CAPACITOR DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP092%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
SEP091/25 | 2025-10-06 17:22 | service@crystalgroup.in | ASPIRO PHARMA - KARKAPATLA | CAIU5422720 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT HAS SHEET KEY DEFECTIVE | NEED TO REPLACE SHEET KEY | SHEET KEY | Yes | USED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP091%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes
SEP094/25 | 2025-10-07 16:13 | crm@crystalgroup.in | Shivamrut | CXRU1032498_40RF | 40 feet | Daikin | SERVICE-ON CALL | NA | NA | display issue and sheet key issue ,need to change both | both need to be changed as soon as possible | 1)display 2)Sheet key |  | Display and key sheet not working properly | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP094%2F25 | NA | DAIKIN | NA | NA | NA | NA | NA | SITARAM | Yes
SEP056/25 | 2025-10-07 16:17 | crm@crystalgroup.in | Laurus Labs Limited-Unit 2 | GESU9454776 | 40 feet | Carrier | SERVICE-AT SITE | NA | NA | evaporator motor defective(single phase) | need to be changed | evaporator motor single phase | Yes | evaporator motor defective(single phase) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP056%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | NA | NA | SITARAM | Yes
OCT036/25 | 2025-10-07 16:23 | crm@crystalgroup.in | Quick supply | SJKU400002 | 40 feet | Carrier | SERVICE-ON CALL | NA | NA | Condensor motors bearing need to be replaced | need to be replaced | condensor motor bearing | Yes | condenser motor bearing issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT036%2F25 | 2016 | CARRIER-PRIMLINE | NA | NA | NA | NA | NA | SITARAM | Yes
OCT003/25 | 2025-10-07 16:28 | crm@crystalgroup.in | Lauras lab unit 2 | BMOU9782197 | 40FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Data recorder sensor and return sensor need tone replaced | need to be replaced | 1)Data recorder sensor 2)return sensor | Yes | Data recorder sensor and return sensor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT003%2F25 | DAikin | DAIKIN | NZ | DECOSIIIF/2553/1 | NA | Used | NA | SITARAM | Yes
OCT002/25 | 2025-10-07 16:31 | crm@crystalgroup.in | Lauras unit 2 | PGRU4958724 | 40 feet | Carrier | SERVICE-AT SITE | NA | NA | Heat termination thermostat (HTT) need to be replaced | need to be replaced | 1)Heat termination thermostat (HTT) | Yes | Heat termination thermostat (HTT) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT002%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Na | Na | SITARAM | Yes
OCT001/25 | 2025-10-08 13:48 | service@crystalgroup.in | Lauras unit 2 | CSRU6101910 | 40RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | UNIT HAS DISPLAY DEFECTIVE | NEED TO REPLACE THE DISPLAY | DISPLAY THERMOKING MP4000 | Yes | UNIT HAS DISPLAY DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT001%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | SITARAM | Yes
SEP096/25 | 2025-10-08 13:52 | service@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | BMOU9787239 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Unit has display & sheet key defective | NEED TO REPLACE THE DISPLAY & SHEET KEY | DAIKIN SHEET KEY & DISPLAY | Yes | UNIT HAS DISPLAY & KEYPAD DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP096%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | VIRENDRA | Yes
OCT052/25 | 2025-10-08 22:36 | technician@crystalgroup.in | Indradeep Infra India Private Limited | MYRU4513729 | 40FT STD RF | Daikin | SERVICE-ON CALL | NA | CHARGEABLE | Sensor issue | Sensor out of range | Inlet sensor Sheet key | Yes | Sensor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT052%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes
OCT053/25 | 2025-10-09 11:22 | crm@crystalgroup.in | GMR | CCLU1030439 | 20 feet reefer | Carrier (thin line) | SERVICE-AT SITE | SALE | CHARGEABLE | complete breakdown | part needs to be replaced and also the display | 1)Carrier controller (ml3) 2)Carrier Display | Yes | Carrier ml3 controller black out | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT053%2F25 | NA: CARRIER; NA: CARRIER-THINLINE; NO: SHAHBUDDIN; No: Yes
OCT054/25 | 2025-10-09 16:02 | service@crystalgroup.in | Apitoria | ACRU4530720 | 40RF | CARRIER | SERVICE-AT SITE | LEASE | FOC | unit has condenser capacitor defective | NEED TO REPLACE CONDENSER CAPACITOR | CONDENSER CAPACITOR | Yes | UNIT WAS DISPLAYING ALARM 25 | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT054%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | AVINASH | Yes
SEP015/25 | 2025-10-10 12:45 | technician@crystalgroup.in | ITC Ltd | MYRU4519748 | 40RF | Daikin | SERVICE-AT SITE | NA | NA | Unit not maintaining temperature | Need to fix | Inlet sensor Outlet sensor suction sensor | Yes | Unit not working properly due to sensor issu | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015%2F25 |  | DAIKIN LXE10E | Na | Na | Na | Na | Na | RAMESH | Yes
OCT051/25 | 2025-10-10 14:41 | service@crystalgroup.in | Switz International | TITU8259465 | 20RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | unit not working | NEED TO VISIT THE SITE | NA | WILL CONFIRM AFTER INSPECTION | COMPRESSOR IS GETTING OVERHEATED (SUSPECTED FAILURE) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT051%2F25 | Thermoking MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | Avinash | Yes
SEP068/25 | 2025-10-10 14:49 | service@crystalgroup.in | Sai Life Science | PCIU600832 845R1 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DOOR NOT CLOSING | NEED TO ALIGN FABRICATION TEAM | NA |  | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP068%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | JSGA622340291 | FABRICATION TEAM | Yes
SEP016/25 | 2025-10-10 17:41 | service@crystalgroup.in | ITC Ltd | TRIU8214763 | 40RF | CARRIER THINLINE | NA | LEASE | FOC | UNIT WAS HAVING ISSUES & CONTRACT HAS BEEN OVER SO CALLING BACK. | need to inspect the unit after callback |  | No | unit is calling back to depot as contract is over | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP016%2F25 | CARRIER THINLINE | CARRIER-THINLINE | 2308L36915 | MSB60272115 |  | USED | "JSGA623040194 " | Shubham | No
SEP015/25 | 2025-10-10 17:45 | service@crystalgroup.in | ITC Ltd | MYRU4519748 | 40RF | DAIKIN | NA | LEASE | FOC | UNIT'S CONTRACT IS OVER SO CALLING BACK | NEED TO INSPECT THE UNIT ONCE IT REACHES TO THE DEPOT | NA | No | NEED TO INSPECT THE UNIT ONCE IT REACHES TO THE DEPOT | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015%2F25 | DAIKIN | DAIKIN | M003143 | LXE10E136A | NA | USED | JSGA623040176 | SHUBHAM | No
SEP018/25 | 2025-10-10 17:52 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | TCLU1912006 | 20RF | DAIKIN | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPPING | UNIT IS WORKING FINE AS PER CUSTOMER | NA | No | UNIT TRIPPING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP018%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | No
OCT063/25 | 2025-10-10 18:26 | technician@crystalgroup.in | KIRLOSKAR | PCIU5822411 | 20FT STD RF | Daikin | SERVICE-ON CALL | NA | NA | Unit giving alaram 101, | Short-out on call, unit working properly | Na | No | Giving alaram 101, on call issues has been rectified, unit working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT063%2F25 | Daikin | DAIKIN | LXIDEA33A | Na | Na | Used | JSGA623040170 | SITARAM | No
OCT066/25 | 2025-10-11 15:33 | technician@crystalgroup.in | Tata Advanced Systems Ltd | CZZU6009100 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Evaporator motor defective need to change, Fan blade need to replace, Sheet key not working properly need to change Display not visible properly | Na | Evaporator motor Fan blade Sheet key Display | Yes | Repair required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT066%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes
OCT068/25 | 2025-10-11 15:41 | technician@crystalgroup.in | CHEMPLAST SANMAR LTD | HDMU5501938 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Evaporator motor defective need to change, Fan blade need to change User panel need to change Sheet key need to change | Na | Evaporator motor 01, Fan blade 01, Sheet key 01, User panel 01, | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT068%2F25 | Daikin | DAIKIN | Na | Na | Na | brand New | JSGA623040307 | SITARAM | Yes
OCT070/25 | 2025-10-11 15:43 | technician@crystalgroup.in | APITORIA | ARCU4530720 | 40FT STD RF | Na | SERVICE-AT SITE | NA | CHARGEABLE | Display not visible properly need to change | Na | Display | Yes | Display not visible | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT070%2F25 | Carrier - Thinline | CARRIER-THINLINE | 3403U01819 | JSL90656199 | Na | Used | Na | SITARAM | Yes
OCT069/25 | 2025-10-11 15:57 | technician@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | BMOU9787239 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Visited site found, both return sensor out of calibration need to replace, user panel need to change, Sheet key need to change | Na | Display, Sheet key, User panel Return sensor 2 no's | Yes | Same above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT069%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes
OCT076/25 | 2025-10-13 11:16 | technician@crystalgroup.in | Qwik Supply Chain Pvt Ltd | TRIU6618391 | 20FT STD RF | Na | SERVICE-AT SITE |  | FOC | I have checked and found, return sensor, condensor pressure transducer need to replace, 2kg gas top up, software configuration need | N | Return sensor 1 no's, condensor pressure transducer 1 no's, 2 kg gas R134a , software update | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT076%2F25 | Carrier - Thinline | CARRIER-THINLINE | Na | Na | Na | Used | Na | SITARAM | Yes
OCT077/25 | 2025-10-13 11:18 | technician@crystalgroup.in | Qwik Supply | TITU9927240 | 40FT Spl RF | 2018 | SERVICE-AT SITE | NA | FOC | Display not visible properly, battery need to change | Need replenishment | Display mp4000, battery mp4000 | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT077%2F25 | Thermoking MP-4000 | TK-MP4000 | Na | Na | Na | Used | Nan | SITARAM | Yes
OCT078/25 | 2025-10-13 15:30 | technician@crystalgroup.in | Qwik Supply | CICU3876631 | 10FT STD RF | 2023 | SERVICE-AT SITE | NA | NA | Battery need to change | Nan | Better mp 4000 | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT078%2F25 | Thermoking | TK-MP4000 | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New | Na | SITARAM | Yes
OCT081/25 | 2025-10-13 16:57 | technician@crystalgroup.in | Dr.Reddy Biologics | TITU9930114 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | Na | REPAIR | NA | NA | Compressor making noise Client need to replace | Y | 5 kg R134a gas, Filter drier, Vacuum, | Yes | Replacement | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT081%2F25 | Thermoking | DAIKIN | 14E219055 | EOG1000667 | Na | Na | JSGA622180063 ¦ JSGA622180011 | SHAHBUDDIN | Yes
OCT083/25 | 2025-10-14 09:47 | technician@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | MYRU4500887 | 40FT STD RF | Na | NA | NA | NA | Temperature not maintain due to ice frosting on floor , service required at side | Technician required at site |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT083%2F25 | Daikin | DAIKIN | Na | LXE10E136A | Na | Refurbished | Na | SHAHBUDDIN | Yes
OCT082/25 | 2025-10-14 09:50 | technician@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd -Kutthur | CXRU1030387 | 40FT STD RF with Anteroom | Na | NA | NA | NA | Temperature not maintain due to ice frosting on floor, service engineer required at site | Technician required at site for inspection |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT082%2F25 | DAikin | DAIKIN | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | Na | SHAHBUDDIN | Yes
SEP032/25 | 2025-10-14 12:39 | technician@crystalgroup.in | Transys Global Forwarding Private Limited-Sshamshabad | TITU8259378 | 20FT Spl RF with Wheels | Na | SERVICE-AT SITE | NA | NA | Temperature not maintain it set point | Need replacement | Evaporator coil sensor, 1 no's Supply sensor 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP032%2F25 | Thermo King MP-4000 | TK-MP4000 | Na | Na | Na | Used | Na | SHAHBUDDIN | Yes
OCT055/25 | 2025-10-14 12:42 | technician@crystalgroup.in | Dr.Reddy | SEGU9107489 | Na | Na | SERVICE-AT SITE |  |  | Door issue | Na | Na | No | Door issues has been rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT055%2F25 | Nan | DAIKIN | Na | Na | Na | Na | Na | Not required | No
OCT056/25 | 2025-10-14 12:49 | technician@crystalgroup.in | Dr.Reddy | SEGU9055868 | Na | Na | SERVICE-AT SITE | NA | NA | Door not close smoothly | Greasing required on door hinges | Greas and oil 1kg | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT056%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes
OCT057/25 | 2025-10-14 12:51 | technician@crystalgroup.in | Dr. Reddy | SEGU9569820 | Na | Na | SERVICE-AT SITE | NA |  | Door not operating smoothly need greasing | Greasing required on door hinges | Greas 1kg 300ml oil | Yes | Greasing required on door hinges | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT057%2F25 | Na | DAIKIN | Na | Nan | Na | Na | Na | SHAHBUDDIN | Yes
OCT058/25 | 2025-10-14 12:52 | technician@crystalgroup.in | Dr.Reddy | CXRU1309957 | Na | Nan | SERVICE-AT SITE | NA | NA | Door issues has been rectified | Rectified |  | No | Rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT058%2F25 | Na | DAIKIN | Na | Nan | Na | Na | Na | No need | No
OCT075/25 | 2025-10-14 14:35 | sitaramsaran65@gmail.com | Qwik Supply | MYRU4518356 | Na | Na | SERVICE-AT SITE | NA | NA | Compressor contractor burnt out need to replace, phase contractor need to replace, Sheet key not working need to replace, ambent and suction SENSOR out of calibration need to replace | Unit breakdown need repair | Compressor contractor 1 no's, Phase contractor 2 no's Suction SENSOR 1 no's Ambent sensor 1 no's Sheet key 1 no's | Yes | Same as above, unit breakdown | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT075%2F25 | Na | DAIKIN | Nan | Na | Na | Na | Nan | SITARAM | Yes
OCT074/25 | 2025-10-14 14:38 | technician@crystalgroup.in | Qwik Supply | TCLU1903088 | Na | Na | SERVICE-AT SITE | NA |  | Unit running with issue, Inlet ,outlet and supply sensor out of range need to replace | Repair immediate | Inlet sensor 1 no's , Outlet sensor 1 nos, Supply sensor 1 no's | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT074%2F25 | Na | DAIKIN | Nan | Na | Na | Na | Na | SITARAM | Yes
OCT073/25 | 2025-10-14 14:42 | technician@crystalgroup.in | Qwik Supply | TDRU7151675 | Na | Na | SERVICE-AT SITE | NA | NA | Unit running with issue, Inlet sensor , ambent sensor and return sensor out of calibration need replace. | Repair immediate | Inlet sensor 1 no's, Ambent sensor 1 no's, Return sensor 1 no's | Yes | Samme as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT073%2F25 | Na | DAIKIN | Na | Na | Nan | Na | Na | SITARAM | Yes
OCT079/25 | 2025-10-14 14:52 | technician@crystalgroup.in | Lauras Labs | CXRU1037308 | Na | Nan | SERVICE-AT SITE | NA | NA | Temperature not maintain, giving alaram e107, need service engineer at site to rectify actual issue | Arranging service engineer at site |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT079%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | VIRENDRA | Yes
OCT059/25 | 2025-10-14 15:00 | technician@crystalgroup.in | Dr.Reddy | SEGU9567638 | Na | Na | SERVICE-AT SITE | NA | NA | Unit working fine, door issues has been rectified | Rectified |  | No | Rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT059%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | No need | No
OCT084/25 | 2025-10-15 15:30 | technician@crystalgroup.in | Switz Intenational | TITU8259465 | 20FT Spl RF | 2013 | SERVICE-AT SITE | NA | NA | Technician visit and find out leakage from vapor injection valve need to replace, | Repair required | Vapor injection body valve 1 no's, Gas R404a - 4.5kg, N2 test required , Brizing work required , Filter drier 1 no's, Vacuum pump required, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT084%2F25 | Thermoking MP-4000 | TK-MP4000 | Na | Na | Na | Brand New | Na | Avinash | Yes
OCT085/25 | 2025-10-16 13:09 | crm@crystalgroup.in | Instakart Services Private Limited | APRU5093234 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, crystalSMART | LED Light, Strip Curtains, crystalSMART |  | Yes | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT085%2F25 | NO: THAKUR; No: No
OCT026/25 | 2025-10-16 13:15 | crm@crystalgroup.in | Instakart Services Private Limited | EMCU5305503 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal paint & logo, Dual Machine | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal paint & logo, Dual Machine |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT026%2F25 | NA: Carrier; -: USED; NO: THAKUR; No: No
OCT025/25 | 2025-10-16 13:17 | crm@crystalgroup.in | Instakart Services Private Limited | APRU5091340 | 40FT | Daikin | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal paint & logo & Dual Machine | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal paint & logo & Dual Machine |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT025%2F25 | Daikin |  | 1106L0930 | KSU60108845 |  | Used |  | THAKUR | No
OCT024/25 | 2025-10-16 13:20 | crm@crystalgroup.in | Instakart Services Private Limited | HDMU5537036 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT024%2F25 | NA: Carrier; -: Used; NO: THAKUR; No: No
OCT023/25 | 2025-10-16 13:21 | crm@crystalgroup.in | Instakart Services Private Limited | APRU5093234 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT023%2F25 | NA: Carrier - Thinline; NO: THAKUR; No: No
OCT022/25 | 2025-10-16 13:23 | crm@crystalgroup.in | Instakart Services Private Limited | CXRU1041571 | 40FT | Daikin | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT022%2F25 | DAikin |  | M002249 | K31408135738 | DECOS 3F / 2609 / 1 | Used |  | THAKUR | No
OCT021/25 | 2025-10-16 13:25 | crm@crystalgroup.in | Instakart Services Private Limited | CXRU1327020 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT021%2F25 | NA: Carrier; NO: THAKUR; No: No
OCT020/25 | 2025-10-16 13:26 | crm@crystalgroup.in | Instakart Services Private Limited | BMOU9728663 | 40FT | Daikin | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar | LED Light, Strip Curtains, Anti-Room Internal, Pallet, Man Trap, IP 65 lights, panic bar |  |  | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT020%2F25 | NA: Daikin; -: USED; NO: THAKUR; No: No
OCT071/25 | 2025-10-16 14:52 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6032622 | 40FT | Na | SERVICE-AT SITE | NA | NA | Door not closing | Immediate | Na | No | Door issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT071%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes
OCT080/25 | 2025-10-16 14:55 | technician@crystalgroup.in | TGF world | TITU8259378 | 20FT | Na | SERVICE-AT SITE | NA | NA | Compressor noisy need to replenishment, evaporator sensor defective need to replenishment, supply sensor defective need to replenishment | Immediate | Compressor mp4000 Gas R404 - 4.5kg Oil 2kg Evaporator sensor 1 no's Supply sensor 1 no's Vacuum pump required Filter drier 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT080%2F25 | Na | TK-MP4000 | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes
OCT065/25 | 2025-10-16 15:08 | technician@crystalgroup.in | Reliance | CCLU1031918 | 20FT | Na | SERVICE-ON CALL | NA | NA | Compressor grounded need to replenishment | Immediate | Compressor thin line 1 no's Oil 3.5 ltr, Gas 5kg R134a, Gas kit suction 1 no's Gas kit discharge 1 no's Filter drier 1 no's Compressor terminal kit 1 no's, Compressor contractor 30A 1 no's, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT065%2F25 | Na | CARRIER-THINLINE | Nan | Na | Na | Na | Na | Avinash | Yes
OCT087/25 | 2025-10-16 16:05 | technician@crystalgroup.in | Quick supply | CICU3876605 | 10FT STD RF | 2023 | SERVICE-AT SITE | NA | NA | Controller hang after 5,6 hours need to replenishment, power modul also suspected, battery need to replace | Immediate | Controller mp 4000, Power module mp 4000, Battery mp4000 | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT087%2F25 | Thermoking | TK-MP4000 | E0GM031489 | 0422GM031489 | ABC782800322110158 | Brand New | Na | SITARAM | Yes
OCT086/25 | 2025-10-16 18:24 | technician@crystalgroup.in | Kirloskar | MYRU4515260 | 40FT STD RF | Nan | SERVICE-ON CALL | NA | NA | Evp Motor need to replace | Immediate | Evaporator motor 1 no's decos III D model | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT086%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | Na | Avinash | Yes
OCT103/25 | 2025-10-17 15:54 | technician@crystalgroup.in | Kirloskar | MYRU4515260 | 40FT STD RF | 2012 | SERVICE-ON CALL | NA | NA | Motor getting heat. Evaporator motor defective need to change | Immediate | Evaporator motor old model type 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT103%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | Na | Avinash | Yes
OCT061/25 | 2025-10-18 12:12 | crm@crystalgroup.in | ASPIRO PHARMA SPECIALITIES PVT LTD | GESU6769548 | 20ft | Carrier Prime-line | READINESS OF CONTAINER |  |  | General inspection | Full pit pass |  | No | General inspection | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT061%2F25 | NO: THAKUR; No: No | NA
OCT062/25 | 2025-10-18 12:15 | crm@crystalgroup.in | Emballiso India Packaging Private Limited | TITU8259655 | 20 RF | tk-4000 | READINESS OF CONTAINER |  |  | General inspection | New machine installed | 1) tubelight 2) Strip curtain 3) Mantrap | Yes | General inspection | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT062%2F25 | NO: THAKUR; No: No | NA
OCT102/25 | 2025-10-18 12:18 | crm@crystalgroup.in | Parle Biscuits Pvt Ltd | MYRU4509035 | 40FT | Daikin | READINESS OF CONTAINER |  |  | Roof patch required | Patch to be fixed |  | NA | Patch | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT102%2F25 | NA: Daikin; NO: THAKUR; No: No | NA
OCT105/25 | 2025-10-18 15:51 | technician@crystalgroup.in | Quick supply | TDRU7151675 | 40FT Spl RF | Compressor not working, unit breakdown | SERVICE-AT SITE | NA | NA | Compressor need to replace | Immediate | Compressor daikin 1 no's, Compressor oil 3 ltr, Filter drier 1 no's, R134a gas 5 kg, Vacuum pump | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT105%2F25 | Daikin | DAIKIN | Na | Na | Na | Na | JSGA622180053 | SITARAM | Yes | Compressor internally damage not pumping need to replace
OCT109/25 | 2025-10-22 08:14 | service@crystalgroup.in | Adhya Dairy-ITC | KKFU5706142 | 40RF | Carrier | SERVICE-AT SITE | NA | NA | supply sensor and defrost sensor need to replace | need repair | supply sensor 2 nos , defrost sensor 1 nos | Yes | same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT109%2F25 | na | CARRIER-THINLINE | na |  |  | na | na | other | Yes | Supply sensor issue
OCT108/25 | 2025-10-22 08:16 | technician@crystalgroup.in | Adhya Dairy-ITC | CXRU1033719 | 40FT | Daikin | SERVICE-AT SITE | NA | FOC | Return sensor need to replace | Repair needed | Rerun sensor 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT108%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Other | Yes | Return sensor issue
OCT107/25 | 2025-10-22 08:18 | technician@crystalgroup.in | Adhya Dairy-ITC | BMOU9729398 | 40FT | 2012 | SERVICE-AT SITE | NA | NA | Display not visible properly and sheet key not working need to replace | Repair needed | Display 1 no's, Sheet key 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT107%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Other | Yes | DISPLAY NOT VISIBLE
OCT095/25 | 2025-10-22 08:25 | technician@crystalgroup.in | RELIANCE | CCLU1031918 | 20FT | 2009 | SERVICE-AT SITE | NA | NA | Pm | Pm | Na | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT095%2F25 | Pm | CARRIER-THINLINE | Na | Na | Na | Na | Na | A | No | Preventive Maintenance
OCT110/25 | 2025-10-22 09:34 | technician@crystalgroup.in | Qwik SUpply Chain | APRU5066497 | 40FT STD RF | 2011 | SERVICE-ON CALL | NA | NA | Compressor need to replace | Immediate repair | Compressor thin line 1 no's Oil 3.5 ltr, Gas 5kg R134a, Gas kit suction 1 no's Gas kit discharge 1 no's Filter drier 1 no's Compressor terminal kit 1 no's, Compressor contractor 30A 1 no's, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT110%2F25 | Carrier - Thinline | CARRIER-THINLINE | Na | Na | Na | Na | JSGA623040296 | Avinash | Yes | Compressor ground need to replace
OCT104/25 | 2025-10-23 15:25 | service@crystalgroup.in | Qwik Supply | MYRU4519753 | 40FT | 2012 | SERVICE-ON CALL | NA | NA | Controller configuration | On call resolved | Na | No | Controller configuration required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT104%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Na | No | Machine isnt switching on
OCT121/25 | 2025-10-23 17:50 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | HDMU5542114 | 40FT | 2011 | SERVICE-AT SITE | NA | NA | Display defective, Heter contractor defective | Immediate repair | Heter contractor 12A, display | Yes | Running with issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT121%2F25 | Na | CARRIER-THINLINE | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Running with issue
OCT119/25 | 2025-10-23 17:53 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6032622 | 40FT | Na | SERVICE-AT SITE | NA | NA | Door issues, display dmg | Immediate repair | Display 1 no's | Yes | Need to replace display | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT119%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Running with issue
OCT111/25 | 2025-10-23 17:55 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6008328 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Door issues | Na | Na | No | Repaired | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT111%2F25 | Daikin | CARRIER-THINLINE | NA | NA | NA | used | JSGA622340291 | SHAHBUDDIN | No | Door issues
OCT123/25 | 2025-10-23 17:57 | technician@crystalgroup.in | Offshore Canning | MCRF4907002 | 20 | 2009 | SERVICE-ON CALL | NA | NA | Hp switch not connected | Immediate repair | Hp switch | Yes | Hp switch need to install | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT123%2F25 | Na | CARRIER-THINLINE | Na | Na | Na | Na | Na | Na | No | ALARM CODE VISIBLE
OCT072/25 | 2025-10-24 08:30 | service@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6034374 | 40FT | na | SERVICE-AT SITE | NA | NA | no issue | na | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT072%2F25 | na | DAIKIN | na | na | na | na | ns | SHAHBUDDIN | No | DISPLAY NOT VISIBLE
SEP061/25 | 2025-10-30 16:40 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | APRU5091041 | 40FT | 2008 | MACHINE INSPECTION | NA | NA | temprature not meet setpoint | technician need at site for observation | na | No | temprature not meet set point | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP061%2F25 | Carrier-Primeline | DAIKIN | KSU60094860 | 541308SN | na | Used | JSGA623040287 | SHAHBUDDIN | Yes | SERVICING, keypad required
OCT124/25 | 2025-10-30 16:45 | service@crystalgroup.in | Lupin | CCLU1036859 | 20FT | 2008 | MACHINE INSPECTION | NA | NA | compressor makig abnormal sound, technician at site for observation | technican need at site | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT124%2F25 | na | CARRIER-THINLINE | na | na | na | na | na | aman | Yes | COMPRESSOR MAKING NOISE
OCT064/25 | 2025-10-30 17:12 | service@crystalgroup.in | QWIK SUPPLY CHAIN PRIVATE LIMITED | CICU2779940 | 10FT | 2024 | SERVICE-ON CALL | NA | NA | door gas kit need to fix | technician need to visit | na | No | door gaskit need to refix | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT064%2F25 | na | TK-MP4000 | na | na | na | na | na | other | Yes | NA
AUG049/25 | 2025-10-30 17:15 | service@crystalgroup.in | Qwik Supply | CXRU1042578 | 40FT | na | SERVICE-ON CALL | NA | NA | as per customer unit working fine | na | na | No | unit working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG049%2F25 | Daikin | DAIKIN | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032 | na | No | Cooling Problem
OCT047/25 | 2025-10-30 17:20 | service@crystalgroup.in | INTERNATIONAL SOCIETY FOR KRISHNA CONSCIOUSNES | TRIU6637874 | 20FT | na | READINESS OF CONTAINER | NA | NA | no ssue found, sound condition | na | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT047%2F25 | Carrier | CARRIER-THINLINE | na | na | na | USed | na | na | No | NA
OCT136/25 | 2025-10-30 17:30 | service@crystalgroup.in | ZENFOLD PHARMA PVT.LTD. | TRIU6618637 | 20FT | na | SERVICE-AT SITE | NA | NA | sensor out of calibration need to replace | ned to replace | supply sensor 2 nos, key pad 1 nos, internal tube light 1 nos | Yes | sensor out of range | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT136%2F25 | na | CARRIER-THINLINE | na | na | a | na | na | SHAHBUDDIN | Yes | Sensors need to be replaced
OCT135/25 | 2025-10-30 17:34 | service@crystalgroup.in | BEJAPURI DAIRY | MYRU4503459 | 40FT | na | SERVICE-AT SITE | NA | NA | spare need to change | na | sheet key 1 nos, condensor fan grill (daikin) low side cap 1 nos | Yes | need to change | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT135%2F25 | na | DAIKIN | na | na | na | na | na | SHAHBUDDIN | Yes | Pan grill needs to be replaced
OCT134/25 | 2025-10-30 17:40 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | PCIU6016370 | 40FT | na | SERVICE-AT SITE | NA | NA | sensor out of range | need to replace | temprature sensor daikin 4 nos, inlet sensor 1 nos, outlet sensor 1 nos | Yes | sensor out of range | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT134%2F25 | na | DAIKIN | na | na | na | na | a | SHAHBUDDIN | Yes | Sensors need to be replaced
OCT133/25 | 2025-10-30 17:49 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | APRU5091041 | 40FT | na | SERVICE-AT SITE | NA | NA | keypad not working | need to visit | keypad 1 nos, silicone sealant 1 nos | Yes | keypd need to replce | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT133%2F25 | na | CARRIER-THINLINE | na | na | na | na | na | SHAHBUDDIN | Yes | KEYPAD NOT WORKING
OCT132/25 | 2025-10-30 18:00 | service@crystalgroup.in | GMR Airport | TITU9930006 | 40FT | na | SERVICE-AT SITE |  |  | display need to replac | need to replace | mp4000 display | Yes | display issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT132%2F25 | na | TK-MP4000 | na | na | na | na | na | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE
OCT130/25 | 2025-10-30 18:05 | service@crystalgroup.in | Swiggy | CRIU4023021 | 40FT | na | SERVICE-ON CALL | NA | NA | door gaskit need to refix | need to fix |  | No | door gaskit issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT130%2F25 | na | TK-MP4000 | na | na | na | na | na | other | Yes | Freezer rubber volve is not fitting into the door. Due to this air is released out temp will not be maintained.
OCT131/25 | 2025-10-30 18:12 | service@crystalgroup.in | Swadesh Milk | GESU9290991 | 40FT | na | SERVICE-AT SITE | NA | NA | coil need to replace | urjent replace | evporator coil 1 nos, filter drier 1 nos | Yes | coil need replace | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT131%2F25 | na | CARRIER-THINLINE | nna | na | na | na | na | NEMICHAND | Yes | Evaporator coil leakage
OCT138/25 | 2025-10-30 19:02 | service@crystalgroup.in | ASPIRO PHARMA | CAIU5422720 | 40FT | na | SERVICE-AT SITE | NA | NA | leak found from filter line | need repair | R134a gas 4.5kg, filter drier 1 nos, discharge sensor 1 nos, | Yes | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT138%2F25 | na | DAIKIN | na | na | na | na | na | SHAHBUDDIN | Yes | Switch tripping
OCT122/25 | 2025-10-31 16:38 | technician@crystalgroup.in | Qwik Supply | TRIU6680335 | 20FT | 2011 | SERVICE-AT SITE | NA | NA | compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | Running with issue | Compressor daikin, Gas R134a 5 kg Filter drier, Ambent sensor, Supply sensor 2 nos, Vacuum pump required | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT122%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | NEMICHAND | Yes | COMPRESSOR MAKING NOISE
OCT140/25 | 2025-10-31 17:57 | service@crystalgroup.in | Flipkart | HDMU5537036 | 40FT STD RF + Dual Machine + Anteroom | 2011 | SERVICE-ON CALL | NA | NA | tmprature not meet setpoint, evporator motor giving alaram | need technicia at site | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT140%2F25 | Carrier | DAIKIN | nna | n | na | used | na | aman | Yes | tmprature not meet setpoint, evporator motor giving alaram
NOV010/25 | 2025-11-02 14:20 | service@crystalgroup.in | SWITZ INTERNATIONAL | TITU8259465 | 20FT Spl RF | NA | SERVICE-AT SITE | NA | NA | LEAK | NA | GAS TOP-UP 5KG | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV010%2F25 | Thermoking MP-4000 | TK-MP4000 | NA |  | NA | Brand New | NA | AVINASH | Yes | BREAKDOWN
NOV011/25 | 2025-11-02 14:38 | service@crystalgroup.in | QWIK SUPPLY | APRU5066497 | 40FT STD RF | NA | SERVICE-AT SITE | NA | NA | SAME | IMMEDIATE |  | GAS R134A | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV011%2F25 | Carrier - Thinline | CARRIER-THINLINE | na: JSGA623040296; na: AVINASH; No: Yes; NA: GAS NEED TO ARRAGE FOR REPAIR
NOV012/25 | 2025-11-04 16:45 | technician@crystalgroup.in | Bamfood | TDRU7155407 | 40FT STD RF | 2011 | SERVICE-ON CALL | SALE | AMC | Compressor need to change | Immediate | Compressor daikin 1 n'os Compressor contractor 1 no's Supply sensor 2 no's Filter drier 1 no's Gas 5 kg R134a Vacuum pump required | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV012%2F25 | Daikin | DAIKIN | Na | Na | Na | USed | Na | AMAN | Yes | Compressor not working
NOV012/25 | 2025-11-04 16:48 | technician@crystalgroup.in | Bamfood | TDRU7155407 | 40FT STD RF | 20009 | SERVICE-ON CALL | SALE | AMC | Compressor need to replace | Immediately | Compressor 1 nos daikin Supply sensor 2 no's Gas R134a 5kg Vacuum pump required Filter drier 1 no's | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV012%2F25 | Daikin | DAIKIN | Na | Na | Na | USed | Na | AMAN | Yes | Compressor issue
OCT139/25 | 2025-11-05 11:00 | pc@crystalgroup.in | MAPRO GARDEN LLP | DFSU6656730 |  | na | NA | NA | NA | na | na | ply broken to repair 4 x 2 before loading. | ply broken to repair 4 x 2 before loading. | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT139%2F25 | na | NA | na: AJAY THAKUR; No: No; NA: ply broken to repair 4 x 2 before loading.
OCT106/25 | 2025-11-05 15:06 | service@crystalgroup.in | Devyani Food Industries Ltd | KKFU6712675 | NA | NA | SERVICE-ON CALL | NA | NA | RUNNING WITH ISSUE SOME SENSOR AND MOTOR NEED TO REPLACE | NEED REPAIR | DISCHARGE VALVE AND SUCTION VALVE 1 NOS, KING VALVE 1 NOS, COMPRESSOR HEAD CENTER AND SIDE GAS KIT, VALVE PLATE GAS KIT, CONTRACTOR 30A AND 12A 1 NOS, EVP MOTOR SINGL PHASEAĀ | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT106%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | NA | NA | NA | No | MOTOR MAKING NOISE
OCT137/25 | 2025-11-05 15:10 | service@crystalgroup.in | QWIK SUPPLY CHAIN PRIVATE LIMITED | CRIU1025041 | 10FT | NA | READINESS OF CONTAINER | STOCK | NA | NA | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT137%2F25 | NA | MP5000 | NA | A | NA | NEW | NA | NA | No | light & strip curtain to install
OCT048/25 | 2025-11-05 15:13 | service@crystalgroup.in | ELINWG INDIA PVT LTD | ARCU4530736 | 40FT | NA | READINESS OF CONTAINER | STOCK | NA | MECHNINE CANBLISED | NEED TO INSTALL URJENT | UNIT DAIKIN | Yes | MACHINE REQUIRED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT048%2F25 | Carrier - Thinline | DAIKIN |  | JSL90656195 |  | used |  | NA | No | NA
NOV019/25 | 2025-11-06 19:19 | service@crystalgroup.in | Amul Dairy | TRIU6644889 | 20FT | 2011 | SERVICE-ON CALL | NA | NA | gas leakage not found. unit maintain only plus 5C temprature. need to N2 test and gas charge | allign technician after complete lucknow | gas R134a 5 kg, N2 test require, Vacume required, if leak found brizing required | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV019%2F25 |  | CARRIER-THINLINE | na: NEMICHAND; No: Yes; NA: TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE
NOV020/25 | 2025-11-06 19:23 | service@crystalgroup.in | Tata Advance | CBHU2811760 | 40FT | na | SERVICE-ON CALL | NA | NA | as discussed with clint unit working fine , no issue found | not required |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV020%2F25 |  | CARRIER-THINLINE | na: na; No: No; NA: TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE
NOV025/25 | 2025-11-06 19:27 | service@crystalgroup.in | Qwik Supply | CXRU1033719 |  | na | SERVICE-ON CALL |  |  | technician need to visit site | arranging technician to visit site |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV025%2F25 |  | CARRIER-THINLINE | na: na; No: No; NA: COMPRESSOR MAKING NOISE
NOV024/25 | 2025-11-06 19:29 | service@crystalgroup.in | Michelin | KKFU6706142 | 40FT | na | SERVICE-ON CALL |  |  | clint request to visit technician at site , | working on it |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV024%2F25 |  | DAIKIN | na: na; No: Yes; NA: COMPRESSOR MAKING NOISE
NOV029/25 | 2025-11-08 12:40 | technician@crystalgroup.in | QWIK SUPPLY | APRU5066497 | 40FT STD RF | Na | SERVICE-ON CALL | NA | NA | Compressor need to change , | Arranging compressor | Compressor thin line 1 nos, Gas R134a 5kg, vacume pump, Hp switch, Compressor contractor 30A, Filter drier 1 nos | Yes | Due to electricity fluctuation | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV029%2F25 | Carrier - Thinline | CARRIER-THINLINE | na: JSGA623040296; na: NEMICHAND; No: Yes; NA: Compressor not working
NOV021/25 | 2025-11-08 22:31 | service@crystalgroup.in | Tata Advance | CZZU6009100 | 40FT | na | SERVICE-AT SITE | NA | NA | motor by pass | arranging spare | evp motor with blade, sheet key, display | Yes | mtor not norking | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV021%2F25 |  | DAIKIN | na: SHAHBUDDIN; No: Yes; NA: DISPLAY NOT VISIBLE
NOV013/25 | 2025-11-08 22:33 | technician@crystalgroup.in | Qwik Supply | SJKU4000022 | 40FT STD RF | Na | SERVICE-AT SITE | NA | FOC | Na | Na |  | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV013%2F25 | Carrier-Primeline | CARRIER-PRIMLINE | na: JSGA623040175; na: Na; No: No; NA: Na
NOV002/25 | 2025-11-08 22:36 | service@crystalgroup.in | Kiaranakart Wholesale Private Limited | TITU9928040 | 40FT Spl RF | na | SERVICE-AT SITE | NA | CHARGEABLE | na | na |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV002%2F25 | Thermoking MP-4000 | DAIKIN | USed: Used; na: SHAHBUDDIN; No: No; NA: na
OCT120/25 | 2025-11-09 12:29 | service@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6031328 | 40FT | na | SERVICE-AT SITE | NA | NA | na | pm |  | No | pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT120%2F25 |  | DAIKIN | na: SHAHBUDDIN; No: No; NA: Preventive Maintenance
OCT112/25 | 2025-11-09 12:31 | service@crystalgroup.in | Sai Life Science Pvt Ltd | CRLU3604920 |  | na | SERVICE-AT SITE | NA | NA | supply sensor need to chnge | ys | supply sensor 2 nos | Yes | need to change | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT112%2F25 |  | DAIKIN | na: AVINASH; No: Yes; NA: AMC
NOV022/25 | 2025-11-09 12:43 | service@crystalgroup.in | Qwik Supply | CISU1442240 |  | na | PREVENTIVE MAINTENANCE | NA | NA | pm | pm |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV022%2F25 |  | DAIKIN | na: SHAHBUDDIN; No: No; NA: Preventive Maintenance
MAY017/25 | 2025-05-10 16:40 | service@crystalgroup.in | LUPIN LIMITED | TRIU6681882 | 20 ft | carrier thin line | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor tripping issue | Filter Drier replacement, refrigerant top up | Filter Drier 01 nos. Refrigerant | Yes | FILTER DRIER CHOKED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY003%2F25 | 20 ft Reefer | CARRIER-THINLINE | 0 | 0 | Advance | USED | 0 | VIRENDRA | Yes