## Sheet1
Job Order No. | Timestamp | Email Address | Client Name | Contact Person Name | Contact Person Number | Contact Person Designation | Container Number | What's the complaint? | Remarks | Client Email ID | Client Location | Machine Status | Description of complaint | Contacted method | Call Attended By | Timestamp | Email Address | Client Name | Container No | Container Size | Machine Make | Work Type | Client Type | Job Type | Issue(s) found | Remedial Action | List of Spares Required | Spares Required | Reason / Cause | Form Link | Reefer Unit | Reefer Unit Model Name (Thinline / MP) | Reefer Unit Serial No | Controller Configuration Number | Controller Version | Brand new / Used | Crystal Smart Sr No. | Technician Name | Technician Required at Client Site | What's the complaint? | Timestamp | Email Address | Indent Required ? | Indent No | Indent Date | Indent Type | Client Name | Client Location | Container No | Where to Use | Billing Type | Container Make & Model | Timestamp | Email Address | Spares Required ? | Indent No | Required Material Arranged ? | PO | Material arranged from | Timestamp | Email Address | Spares Required ? | Indent No | Required Material Sent Through | Courier Docket Number | Courier Name | Technician Name | Courier Receipt Note (Upload Courier Tracking number) | Courier Contact Number | Timestamp | Complaint Attended Date | Service Type | Complaint Received By | Client Name | Client Location | Container Number | Contanier size | Call Attended Type | Issue/Complaint Logged | Reefer Make & Model | Set / Operating Temperature | Contanier Condition | Condenser Coil | Condenser Coil Image | CondenserMotor | Evaporator Coil | Evaporator Motor | Compressor Oil | Compressor Oil2 | Refrigerant Gas | Refrigerant Gas2 | Controller Display | Controller Display2 | Controller keypad | Controller keypad2 | Power cable | Power cable2 | Machine main braker | Compressor contactor | Compressor contactor2 | EVP/COND contactor | EVP/COND contactor2 | Customer main MCB | Customer main cable | FLP scoket condition | Alarm lisit clear | Filter drier | Filter drier2 | Pressure | Comp current | Main Voltage | PTI | Observations | Work Description/Technician Comments | Required spare part(s)/Consumable(s) | Sign JOB ORDER (front) | Sign JOB ORDER (back) | Sign JOB ORDER | Trip No | Any Pending Job? | Next Service Call Required | Next Service - Urgency | List down the pending job | List of Spares | Email Address | Type of Container
JUL001 | 2024-07-11 22:22 | pravin.shinde@crystalgroup.in | BPCL | Mohsin | 9995814821 | Supervisor | CXRU1043337 | Installation request | Visit |  |  | Installation |  |  |  | 2024-07-11 11:14 | pravin.shinde@crystalgroup.in | Bharat Petroleum | CXRU1043337 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | NA | Installation & Training provided | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL001 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | SHAHBUDDIN |  | Installation request | 2024-07-11 11:39 | pravin.shinde@crystalgroup.in | NO | [9 empty] | 2024-07-11 11:50 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-11 11:52 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-08-07 04:35 | 2024-07-01 | Lease | Regular Visit | BPCL | Kerala | CXRU1043337 | 40FT | SERVICE-AT SITE | Installation & Training provided | Daikin | +15 C to +20 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 and 140 | R- 9.6 Y- 9.5 B- 9.6 | L1- 440 L2- 440 L3- 440 | Not done | Installation unit, Traning for technical staff, General checked with operatiokn | Installation point checked and satisfied, Training done with tech staff & checked unit with operation, main wall and checked gas level and electrical wire unit working as normal and used for operation | NA |  |  | https://drive.google.com/open?id=1prk4-ZJov2PqOsbUSHluJ9vdjM0iTmOX
JUL002 | 2024-07-11 22:26 | pravin.shinde@crystalgroup.in | Cipla | Kiran | 9146012098 | Supervisor | TITU9231009 | Not maintaining temperature | Pravin |  |  | Running with issues |  |  |  | 2024-07-11 11:15 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9231009 | 40-SUPERSTORE | DAIKIN | SERVICE-ON CALL | LEASE | FOC | Due to power fluctuation container not working | Reset the unit and found working | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL002 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | RAMIZ |  | Not maintaining temperature | 2024-07-11 11:39 | pravin.shinde@crystalgroup.in | NO | [9 empty] | 2024-07-11 11:50 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-11 11:52 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-08-07 05:00 | 2024-07-05 | Paid | EMAIL | Cipla | Goa | TITU9231009 | 40FT | SITE INSPECTION | Display not working | Daikin | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/190 | R-9.9 B- 9.8 Y- 9.8 | L1- 402 L2 - 401 L3 - 401 | Short | Unit not working Display issuse | Display and sheetkey need to replace | Display-1 sheetkey-1 |  |  | https://drive.google.com/open?id=1XphQmvReCeCI-M5qrUtH-PEUmctjQ1Tu
JUL010 | 2024-07-11 22:30 | pravin.shinde@crystalgroup.in | Quick supply chain PVT LTD | Pramod rane | 8865021446 | Supervisor | TITU7263521 | Compressor noisy | Vinit |  |  | Running with issues |  |  |  | 2024-07-11 11:30 | pravin.shinde@crystalgroup.in | Qwik Supply | TITU7263521 | 20-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | COMPRESSOR NOISY | NEE TO TOP UP GAS AND OIL | REFRIGERANT GAS 2 KGS COMPRESSOR OIL 1 LTR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL010 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH |  | Compressor noisy | 2024-07-17 03:30 | pravin.shinde@crystalgroup.in | YES | JUL064 | 7.7.24 |  | QWICK SUPPLY | HAPUR | TITU7263521 | SITE | FOC |  | 2024-07-17 09:42 | pravin.shinde@crystalgroup.in | YES | JUL064 | YES |  |  | 2024-08-07 05:04 | support@crystalgroup.in | YES | JUL075 | COURIER | [5 empty] | 2024-08-07 05:28 | 2024-07-18 | Free of Cost | EMAIL | Quick supply | Hapur | TITU7263521 | 40FT | SITE INSPECTION | Breakdown | Daikin | -30 C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 180/1690 | R-10.1 B-10.1 Y-10.1 | L1- 401 L2 - 401 L3 - 401 | Short | Checked and found compessor heavy sound due to low oil level need to replace oil and gas then need to check sound again and leakage from ESV/ISV | Container Breakdown(please don't use) | Compessor oil 3L Gas- 4.5 Gaskit - 2 Compessor contactor - 1 ESV-1 ISV-1 vacumm 2 Fliter- 1 |  |  | https://drive.google.com/open?id=1BwqlUbDo7MtyllxWCx50JBDl4AHsib7F
JUL009 | 2024-07-11 22:28 | pravin.shinde@crystalgroup.in | Symbiotic | Mr | 9 | Supervisor | TCLU1904607 | Not working | Vinit |  |  | Running with issues |  |  |  | 2024-07-11 11:28 | pravin.shinde@crystalgroup.in | Symbiotech | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-ON CALL | SALE | FOC | EVP COIL RUSTY | NEED TO REPLACED | DAIKIN EVP COIL - 1 NO DAIKIN STAINER - 1 NO REFRIGERANT GAS - 5 KGS BRAZING SET - 1 SET VACUUM PUMP - 1 NO NITROGEN - 1 NO BRAZING ROD - 15 NOS |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL009 | Daikin | Daikin |  |  |  | Used |  | UMESH |  | Not working | 2024-07-17 03:28 | pravin.shinde@crystalgroup.in | YES | JUL063 | 7.7.24 |  | SYMBIOTECH | PUNJAB | TCLU1904607 | SITE | PAID |  | 2024-08-27 00:16 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-08-30 01:52 | 2024-07-08 | Lease | Phone | SYMSIOTIC | PUNJAB | TCLU1130265 | 40FT | SERVICE-AT SITE | PM services | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Need to replace |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | CONTAINER BREAKDOWN | EVP COIL LECKAGE AND ALL ER PIPES NEED TO REPLACE | EVP COIL, COPPER WIRE ( EXTERNAL ), GAS R 134A, N2, BREZING SET , BREZING ROD, VACCUM PUMP, SENSOR |  |  | https://drive.google.com/open?id=18ROJPY3EyOzvTBJXHQ_VPr1axi30ldKZ
JUL012 | 2024-07-11 22:32 | pravin.shinde@crystalgroup.in | Quick supply chain PVT LTD | Mr | 8884266284 | Manager | TRIU6681440 | Not working | Virendra |  |  | Running with issues |  |  |  | 2024-07-11 11:33 | pravin.shinde@crystalgroup.in | Qwik Supply | TRIU6681440 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | DISPLAY, KEYPAD, AMBIENT & SUPPLY SENSOR, CONTACTOR, FILTER REQ | NEED PARTS | CARRIER THINLINE DISPLAY - 1 NO CARRIER THINLINE KEYPAD - 1 NO CARRIER AMBIENT SENSOR - 1 NO CARRIER SUPPLY SENSOR - 1 NO CARRIER COMPRESSOR CONTACTOR 30A - 1 NO LIQUID FILTER - 1 NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL012 | Carrier - Transcold | Transcold |  |  |  | Used |  | UMESH |  | Not working | 2024-07-17 03:32 | pravin.shinde@crystalgroup.in | YES | JUL065 | 7.7.24 |  | QWICK SUPPLY | TALOJA | TRIU6681440 | SITE | FOC |  | 2024-08-27 00:17 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:29 | DEC016 | NO | [7 empty] | 2024-08-30 02:25 | 2024-07-10 | Lease | Phone | QWIK SUPPLY | TALOJA | TRIU6681440 | 20FT | SERVICE-AT SITE | BREAKDOWN | Carrier | -28* | Dirty | Clean |  |  | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0/ 14 | 2012-12-12 | 414 / 414 / 414 | Short | DISPLAY, KEYPAD, AMBIENT & SUPPLY SENSOR, CONTACTOR, FILTER REQ | NEED TO WORK ASAP | DISPLAY, KEYPAD, AMBIENT SENSOR & SUPPLY SENSOR, CONTACTOR, FILTHER DRIVER. |  |  | https://drive.google.com/open?id=1NNJWxRCi3uSalROtDZB87lhF4cVRGSxf
JUL014 | 2024-07-11 22:33 | pravin.shinde@crystalgroup.in | Jubliant Consumer Pvt Ltd | Mr | 9 | Supervisor | GRMU3607418 | Not working | Vinit |  |  | Running with issues |  |  |  | 2024-07-16 22:41 | support@crystalgroup.in | Jubilant Consumer | GRMU3607418 | NA | NA | NA | NA | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL014 | Daikin |  |  |  |  | Used |  | UMESH |  | Not working | 2024-08-26 23:51 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-07-17 09:43 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-17 10:04 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-08-30 02:53 | 2024-06-24 | Lease | Phone | Jubilant Consumer | NODIA | GRMU3607418 | 40FT | SERVICE-ON CALL | LOW TEMP | Daikin | -25* / -18* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | TEMP. ISSUE | HIGH TEMP, LOW PRESSURE, FILTER CHOCKED | R134A, FILTER DRIVER, INTEL DRIVER. |  |  | https://drive.google.com/open?id=1DdRKkniS75uufO2g8D-xD0tfSXYmgvNs
JUL003 | 2024-07-11 23:15 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | Na | Na | Na | APRU5091606 | PREVENTIVE MAINTENANCE | Vinit |  |  | Preventive Maintenance |  |  |  | 2024-07-11 11:17 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | APRU5091606 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Evaporator motor and contactor defective | need to replaced part currently container not working | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL003 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-07-17 03:13 | pravin.shinde@crystalgroup.in | YES | JUL059 | 7.7.24 |  | EARL CORVUS | KERALA | APRU5091606 | SITE | PAID |  | 2024-07-17 09:40 | pravin.shinde@crystalgroup.in | YES | JUL059 | YES |  |  | 2024-08-09 00:39 | support@crystalgroup.in | YES | JUL059 | TECHNICIAN | [5 empty] | 2024-08-09 02:32 | 2024-07-02 | Free of Cost | EMAIL | Earl corvus | Kerala | APRU5091606 | 40FT |  | PM/visit | Thermo king | -20 C | Clean | Clean |  | Okay | Rusty | Need to replace | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Need to replace |  | Okay | Okay | Okay | Done | Clean |  | 0.2/170 | R-12.3 B-12.4 y-12.3 | L1-410 L2-410 L3-410 | Full | PM service Temp issue EVP not working | Evaporater motor left and right need to replace, Display not working | Evaporater motor (single phase)-02 Evaporater contactor |  |  | https://drive.google.com/open?id=1VhMsoTGqRMYg_u6P4n3nzgoaOMyf9Tw1
JUL007 | 2024-07-11 23:16 | pravin.shinde@crystalgroup.in | Crystal | NA | NA | NA | PCIU6010243 | PREVENTIVE MAINTENANCE | Pravin |  |  | Preventive Maintenance |  |  |  | 2024-07-11 11:23 | pravin.shinde@crystalgroup.in | Crystal Yard-Chennai | PCIU6010243 | 40-REEFER | DAIKIN | SERVICE-AT SITE | STOCK | FOC | DISPLAY, SHEETKEY, FILTER REQU | REPLACED ALL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL007 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-07-11 11:40 | pravin.shinde@crystalgroup.in | NO | [9 empty] | 2024-07-11 11:51 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-11 11:52 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-08-09 03:11 | 2024-07-08 | Free of Cost | Phone | Crystal | Chennai | PCIU6010243 | 20FT | SITE INSPECTION | Display and filter drive failure | Daikin | -18 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 201/1766 | R-11.3 B-10.7 Y-10.9 | 415/411/413 | Short | We have attended display , sheet key failure, fliter drive rusted | we have replace fliter drive, sheet key failure, container short PTI | Display-01 Sheet key-01 Filter Drive-01 |  |  | https://drive.google.com/open?id=1WNnMc05-ItAipvvlUTLau7eIxtwY4y3Q
JUL008 | 2024-07-11 23:17 | pravin.shinde@crystalgroup.in | Quick supply chain PVT LTD | Na | Na | Na | CICU2779940 | PREVENTIVE MAINTENANCE | Vinit |  |  | Preventive Maintenance |  |  |  | 2024-07-11 11:24 | pravin.shinde@crystalgroup.in | Qwik Supply | CICU2779940 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR CONTACTOR FAULTY | NEED TO REPLACED | Compressor Contactor - 1 NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL008 | Thermoking | Magnum Plus | E0GM030268 | ABC782800322010065 |  | BrandNew |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-07-17 03:25 | pravin.shinde@crystalgroup.in | YES | JUL062 | 7.7.24 |  | QWICK SUPPLY | COCHIN | CICU2779940 | SITE | FOC |  | 2024-08-03 00:19 | support@crystalgroup.in | YES | JUL062 | YES |  |  | 2024-08-09 03:20 | support@crystalgroup.in | NO | [7 empty] | 2024-08-30 01:40 | 2024-07-03 | Lease | Phone | QWIK SUPPLY | KERALA | CICU2779940 | 10FT | SERVICE-AT SITE | PM SERVICES | Thermo king | 39*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4 / 19 B | 9.4 / 9.4 / 9.5 | 401/ 402/ 401 | Short | PM SERVICES | CHECKED CONDERSOR COIL, VOLTAGE CHECK OF ALL MOTORS, ROTATIONS , SENSORS, ELECTRICAL WIRING AND CONNECTIONS , GAS LEVEL. COMPRESSOR CONTRATORS COIL FOUND NOISY. | COMPRESSOR CONTRATORS 30 A |  |  | https://drive.google.com/open?id=1eJ8lFVCtVd0Q_A403LnEkaE4jAMh9_qy
JUL013 | 2024-07-11 23:18 | pravin.shinde@crystalgroup.in | Crystal JNPT | Na | Na | Na | GESU9379498 | PREVENTIVE MAINTENANCE | Pravin |  |  | Preventive Maintenance |  |  |  | 2024-07-16 22:32 | support@crystalgroup.in | Crystal Yard-JNPT | GESU9379498 | 40-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | NA | NA | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL013 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-26 23:50 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:17 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:30 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-08-30 02:43 | 2024-07-11 | Lease | Phone | CRYSTAL YARD | JNPT | GESU9379498 | 40FT | REPAIR | INSPECTION | Carrier | -18* | Clean | Clean |  |  | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | POWER CABLE IS MISSING, CURTAIN DAMAGE, LIGHT MISSING, R/S DOOR FIBER AND GASLET DAMAGE | NEED SPARES | POWER CABLE 440, T50 POWER PLUG, CURTAIN, LED LIGHTS, CROSSING PATTI, R/S DOOR FIBER AND GASLET |  |  | https://drive.google.com/open?id=1L20Rv0mVomlotPxpbsA0o_QZUwo9R7uP
JUL017 | 2024-07-13 07:43 | pravin.shinde@crystalgroup.in | RELIANCE | Gopal | 6307373723 | Operator | Daikin | Not working | Pravin |  |  | Running with issues |  |  |  | 2024-07-16 23:10 | support@crystalgroup.in | Qwik Supply | MYRU4518356 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | CONTROL PANEL BURN | Need spares | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL017 | Daikin | LXE10E136 A2 | M005086 | DCOZ3E |  | Used | JSGA622180065 | UMESH |  | Not working | 2024-07-17 03:44 | pravin.shinde@crystalgroup.in | YES | JUL067 | 13.7.24 |  | QWICK SUPPLY | LUCKNOW | MYRU4518356 | SITE | FOC |  | 2024-07-17 09:46 | pravin.shinde@crystalgroup.in | YES | JUL067 | YES |  |  | 2024-07-17 10:05 | pravin.shinde@crystalgroup.in | YES | JUL067 | TECHNICIAN | [5 empty] | 2024-09-01 21:34 | 2024-07-13 | Lease | Phone | QWIK SUPPORT | LUCKNOW | MYRU4518356 | 40FT | SERVICE-ON CALL | BREAKDOWN | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | NEED TO CHECK WAIRING | CHECKED AND FOUND SHORT CIRCUIT IN CONTAINER, NEED TO REPLACED THE CONTACTOR. | YES |  |  | https://drive.google.com/open?id=1qZud9LDwjJjWvieLLPLk5jpq2uktIKoW
JUL021 | 2024-07-13 11:02 | vinit.mewada@crystalgroup.in | APL - NELLORE | POPATRAO JADHAV | 9642814421 | ENGINEERING | CXRU1032327, PCIU6007065, APRU5093234 | INSTALLATION DONE BUT SPARES REQUIRED. | VINIT |  |  | Installation |  |  |  | 2024-07-16 23:29 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6706142 | 40-REEFER | CARRIER-THINLINE | PREVENTIVE MAINTENANCE | LEASE | FOC | Coil dirty, supply sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL021 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040294 | VIRENDRA |  | INSTALLATION DONE BUT SPARES REQUIRED. | 2024-07-17 08:43 | pravin.shinde@crystalgroup.in | YES | JUL071 | 15.7.24 |  | AJINOMOTO BIO | VISAKHAPATNAM | KKFU6706142 | SITE | FOC |  | 2024-08-03 00:27 | support@crystalgroup.in | YES | JUL071 | YES |  |  | 2024-08-27 01:33 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-11 23:25 | 2024-07-13 | Lease | Phone | Ajinomoto Bio Pharma | Visakhapatnam | KKFU6706142 | 40FT | SERVICE-AT SITE | PM SERVICES | Carrier | +20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 4.7 b / 13.1 B | 10.0 A / 9.9 A / 9.7 A | 413 V/410 V /411 V | Not done | Coil dirty, supply sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Carrier Supply Sensor |  |  | https://drive.google.com/open?id=1HJWjhOuAQ2PD3a_Wcu3p0nafLRSUl5KZ
JUL004 | 2024-07-17 09:58 | support@crystalgroup.in | Cipla Unit 1 | NA | NA | NA | TITU9230980 | Not maintening temp | Tanaya Jadhav |  |  | Running with issues |  |  |  | 2024-07-11 11:19 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9230980 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Condenser coil leak and keypad, display required | need parts | Condenser coil - 1 no keypad - 1 no display - 1 no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL004 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | SHAHBUDDIN |  | Not maintening temp | 2024-07-17 03:15 | pravin.shinde@crystalgroup.in | YES | JUL060 | 7.7.24 |  | CIPLA UNIT1 | GOA | TITU9230980 | SITE | FOC |  | 2024-07-17 09:41 | pravin.shinde@crystalgroup.in | YES | JUL060 | YES |  |  | 2024-07-17 10:01 | pravin.shinde@crystalgroup.in | YES | JUL060 | TECHNICIAN | [5 empty] | 2024-08-09 05:06 | 2024-07-16 | Free of Cost | EMAIL | Cipla Unit 1 | GOA | MYRU4518356 | 40FT | NA | Repair | Daikin | +35 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9/180 | 9.8/9.9/9.8 | 410/410/410 | Short | TEMP issue, condonser coil leak,Display shortkey | Pull out leaking coil | Maintain set temp |  |  | https://drive.google.com/open?id=1mIwRwXRHIVwLUv5GRzKWpbcfVy5dCJsl
JUL005 | 2024-07-17 09:59 | support@crystalgroup.in | Cipla Unit 1 | NA | NA | NA | TITU9231009 | Display not working | Tanaya Jadhav |  |  | Running with issues |  |  |  | 2024-07-11 11:20 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9231009 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Display & Keypad defective | need parts | Display - 1 no Keypad - 1 no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL005 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | SHAHBUDDIN |  | Display not working | 2024-07-17 03:18 | pravin.shinde@crystalgroup.in | YES | JUL061 | 7.7.24 |  | CIPLA UNIT1 | GOA | TITU9231009 | SITE | FOC |  | 2024-07-17 09:41 | pravin.shinde@crystalgroup.in | YES | JUL061 | YES |  |  | 2024-07-17 10:02 | pravin.shinde@crystalgroup.in | YES | JUL061 | TECHNICIAN | [5 empty] | 2024-08-30 00:45 | 2024-06-30 | Lease | Phone | CIPLA UNIT 1 | GOA | TITU9231009 | 40FT | SERVICE-AT SITE | Display not working | Daikin | +4*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8 / 190 | R- 9.9/ B- 9.8 / Y - 9.8 | L1- 401 / L2- 401 / L3 - 401 | Short | UNIT NOT WORKING AND DISPLAY ISSUE | UNIT RUN AND OBSERVE - CHECKED WIRE, GAS LEVEL PARAMATERS AD FOUD DISPLAY IS NOT WORING. | DISPLAY AND SHEET KEY |  |  | https://drive.google.com/open?id=1L7LmcKLXC7jwbwwizKKzTvLOUfOs3yM5
JUL006 | 2024-07-17 10:01 | support@crystalgroup.in | Andabar | NA | NA | NA | TRIU6616531 | Not working | Tanaya Jadhav |  |  | Running with issues |  |  |  | 2024-07-11 11:21 | pravin.shinde@crystalgroup.in | Andabar | TRIU6616531 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | SALE | FOC | Brazing not done properly | doing rework of brazing and working well | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL006 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Used |  | VIRENDRA |  | Not working | 2024-07-11 11:40 | pravin.shinde@crystalgroup.in | NO | [9 empty] | 2024-07-11 11:50 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-11 11:52 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-08-30 01:00 | 2024-06-22 | Lease | Phone | ANDABAH | CHENNAI | TRIU6616531 | 20FT | SERVICE-AT SITE | TEMP ISSUE | Carrier | -18* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | DISCHARGE - 200 | R-12..0A/ Y- 12.3A / B- 12.5 A | 415V / 411 V/ 413 V | Full | COOLOING ISSUE | BLEZING , LEAKAGE , GAS LEVEL CKECKED, NEED 4 KG OF GASES TO REFILL, DONE FULL PTI, TEMP. MAINTAINED, WORKING WELL. | BLEZING ROD, R-134A |  |  | https://drive.google.com/open?id=1veIGhOllyLwJ46McBeiJppm4zycW_8Vl
JUL011 | 2024-07-17 10:03 | support@crystalgroup.in | Qwik Supply | NA | NA | NA | TRIU6681440 | NOT WORKING | Tanaya Jadhav |  |  | Running with issues |  |  |  | 2024-07-11 11:31 | pravin.shinde@crystalgroup.in | Qwik Supply | TRIU6681440 | 20-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | NOT ABLE TO IDENTIFY ON CALL | NEED TO ATTEND PHYSICALLY | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL011 | Carrier - Transcold | Transcold |  |  |  | Used |  | UMESH |  | NOT WORKING | 2024-07-11 11:40 | pravin.shinde@crystalgroup.in | NO | [9 empty] | 2024-07-11 11:51 | pravin.shinde@crystalgroup.in | NO |  |  |  |  | 2024-07-11 11:53 | pravin.shinde@crystalgroup.in | NO | [7 empty] | 2024-11-20 23:08 | 2024-07-09 |  |  |  |  | TRIU6681440 |  |  |  | Carrier | [33 empty] | NOT ABLE TO IDENTIFY | NEED TO ATTEND |  |  |  | NA | No | No | Can be done on next PM | NA
JUL015 | 2024-07-17 10:05 | support@crystalgroup.in | Jubliant Consumer Pvt Ltd | NA | NA | Na | GRMU3607418 | NOT WORKING | Tanaya Jadhav |  |  | Running with issues |  |  |  | 2024-07-16 22:47 | support@crystalgroup.in | Jubilant Consumer | GRMU3607418 | NA | NA | SERVICE-AT SITE | NA | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL015 | Daikin |  |  |  |  | Used |  | UMESH |  | NOT WORKING | 2024-08-26 23:51 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-03 00:30 | support@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-08-30 03:08 | 2024-06-26 | Lease | Phone | JUBILENT FOOD | NOIDA | GESU9379498 | 40FT | REPAIR | TEMP ISSUE | Daikin | -18* / SET TEMP. - 25* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | MIX UP OIL AND MOISTURE IN R 134A GAS | GAS FLUSH OUT, VACCUM FULL SYSTEM, N2 FILL OUTTO MAINTAIN THE PRESSURE AND REFILL THE N2 AD R 134 A | R 134 A , N2 TEST, VACCUM PUMP |  |  | https://drive.google.com/open?id=13KAw5OlCkM5bevikSco1EJjSqtQRWkiE
JUL016 | 2024-07-17 10:08 | support@crystalgroup.in | Crystal Yard-Vizag | NA | NA | NA | KKFU6712802 | PREVENTIVE MAINTENANCE | Tanaya Jadhav |  |  | Preventive Maintenance |  |  |  | 2024-07-16 22:54 | support@crystalgroup.in | Crystal Yard-Vizag | KKFU6712802 | 40-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | no gas in system, filter need to repair, need to check leak in gas and supply sensor req, ISO plug & Gas required | Need spares | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL016 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | TP-FLAGSHIP DEPOT |  | PREVENTIVE MAINTENANCE | 2024-07-17 03:42 | pravin.shinde@crystalgroup.in | YES | JUL066 | 7.7.24 |  | CRYSTAL YARD | VISAKHAPATNAM | KKFU6712802 | DEPOT | FOC |  | 2024-07-17 09:44 | pravin.shinde@crystalgroup.in | YES | JUL066 | YES |  |  | 2024-07-17 10:04 | pravin.shinde@crystalgroup.in | YES | JUL066 | ARRENGING AT SITE | [5 empty] | 2024-08-30 03:39 | 2024-07-11 | Lease | EMAIL | Crystal Yard-Vizag | Visakhapatnam | KKFU6712802 | 40FT | REPAIR | PRE MAINTAINACE | Carrier | NA | Clean | Clean |  |  | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Need to replace |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | NA | NA | NA | Not done | NEED TO REPLACE THE GAS, PLUG IN , FILTER AND SUPPLY RECORDER | WE SUGGEST FOR LEAK TEST TO THE CLIENT AFTER THAT INFORM THE SAME FOE FURTHER PROCESSING. | SUPPLY RECORDER SENSOR, LIQUID FILTER, ISO PLUGIN, REFRIGENETOR GAS |  |  | https://drive.google.com/open?id=1rm02nR1SvrtwyTIX0wu_N3p8CQdp0o5T
JUL018 | 2024-07-17 10:10 | support@crystalgroup.in | APL Health Care | NA | NA | NA | APRU5093234 | INSTALLATION | Tanaya Jadhav |  |  | Installation |  |  |  | 2024-07-16 23:15 | support@crystalgroup.in | APL Health | APRU5093234 | 40-REEFER | CARRIER-THINLINE | INSTALLATION | LEASE | FOC | Condenser coil leak, EVP motor heavy sound, strip curtain req | Need to close leak and required motor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL018 | Carrier - Thinline | Thinline | [5 empty] | VIRENDRA |  | INSTALLATION | 2024-07-17 03:50 | pravin.shinde@crystalgroup.in | YES | JUL068 | 15.7.24 |  | APL | Chennai | APRU5093234 | SITE | FOC |  | 2024-08-03 00:32 | support@crystalgroup.in | YES | JUL068 | YES |  |  | 2024-08-27 01:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-01 23:29 | 2024-07-12 | Lease | Phone | APL HEALTHCARE | MENAKURU | APRU5093234 | 40FT | SERVICE-AT SITE | NA | Carrier | +20* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | DISCHARGE :13.6 H | 11.0 A / 10.9 A / 10.7 A | 415 V / 411V / 413 V | Short | CONDENSOR COIL LEAKAGE, EVP MOTOR NEED TO REPLACE DUE TO HEAVY SOUND | DISPLAY REPLACED AND CONTAINER WORKING WELL | YES |  |  | https://drive.google.com/open?id=1kfpo1udxbGlNKFI0jdHMta1Eu41miSK6
JUL019 | 2024-07-17 10:11 | support@crystalgroup.in | APL Health Care | NA | NA | NA | CXRU1032327 | INSTALLATION | Tanaya Jadhav |  |  | Installation |  |  |  | 2024-07-16 23:20 | support@crystalgroup.in | APL Health | CXRU1032327 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | Sheetkey not working well and suction gas sensor required | required part | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL019 | DAikin | LXE10E147F2 | M000737 | K31405125030 | DECOS 3F 2553 / 1 | Used | JSGA622340153 | VIRENDRA |  | INSTALLATION | 2024-07-17 08:35 | pravin.shinde@crystalgroup.in | YES | JUL069 | 15.7.24 |  | APL | CHENNAI | CXRU1032327 | SITE | FOC |  | 2024-08-03 00:34 | support@crystalgroup.in | YES | JUL069 | YES |  |  | 2024-08-27 01:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-11 22:51 | 2024-07-12 | Lease | Phone | APL Health | Chennai | CXRU1032327 | 40FT | SERVICE-AT SITE | INSTALLATION | Daikin | +20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 207 KPA/ 403 KPA | 11.0 A/ 10.9 A / 10.7 A | 414 V / 411 V/ 413 V | Short | Sheet key not working well and suction gas sensor required | required part | Daikin Suction Gas Sensor |  |  | https://drive.google.com/open?id=1lhrL4U-uz204wKFCSHAJtWh850y21_2u
JUL020 | 2024-07-17 10:14 | support@crystalgroup.in | APL Health Care | NA | NA | NA | PCIU6007065 | INSTALLATION | Tanaya Jadhav |  |  | Installation |  |  |  | 2024-07-16 23:24 | support@crystalgroup.in | APL Health | PCIU6007065 | 40-REEFER | DAIKIN | INSTALLATION | LEASE | FOC | display, led light, filter, strip curtain required | required part | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL020 | Daikin |  |  |  |  | Refurbished |  | VIRENDRA |  | INSTALLATION | 2024-07-17 08:42 | pravin.shinde@crystalgroup.in | YES | JUL070 | 15.7.24 |  | APL | CHENNAI | PCIU6007065 | SITE | FOC |  | 2024-08-03 00:35 | support@crystalgroup.in | YES | JUL070 | YES |  |  | 2024-08-27 01:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-11 23:15 | 2024-07-12 | Lease | Phone | APL Health | Chennai | PCIU6007065 | 40FT | SERVICE-AT SITE | INSTALLATION | Daikin | +20*c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 171KPA / 177.6 KPA | 12.9 A /12.7 A / 12.5 A | 401 V / 405 V/ 400 V | Short | display, led light, filter, strip curtain required | required part | Daikin Display, Liquid Filter, LED Light 20W, Curtain set for 40ft [Model - Frigus] L&T MCB 16 AMP X 2P, Polycab Flexible Cable 1.5 sq mm X 2 Core, Insulation Tape RIVIT, CABLE TIE 12 INCH BLACK, RIVIT GUN, Drill Machine, CASING PATTI 1 INCH |  |  | https://drive.google.com/open?id=1jfmniw4SHKx3_TbWdz0Kr_k_C1O0s6XS
JUL022 | 2024-07-17 10:33 | support@crystalgroup.in | Ajinomoto Bio Pharma | NA | NA | NA | BMOU9766180 | PREVENTIVE MAINTENANCE | Tanaya Jadhav |  |  | Preventive Maintenance |  |  |  | 2024-07-16 23:34 | support@crystalgroup.in | Ajinomoto Bio Pharma | BMOU9766180 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty, return sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL022 | Daikin |  |  |  |  | used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-07-17 08:51 | pravin.shinde@crystalgroup.in | YES | JUL072 | 15.7.24 |  | AJINOMOTO BIO | VISAKHAPATNAM | BMOU9766180 | SITE | FOC |  | 2024-08-27 00:18 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:33 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-11 23:33 | 2024-07-13 | Lease | Phone | Ajinomoto Bio Pharma | Visakhapatnam | BMOU9766180 | 40FT | SERVICE-AT SITE | PM SERVICES | Daikin | 4.8*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 74 KPA / 919 KA | 8.5 A / 8.1 A / 8.3 A | 410 V / 407 V / 409 V | Not done | Coil dirty, return sensor defective | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Daikin Return Temperature Sensor |  |  | https://drive.google.com/open?id=14L0yUh42xOsK-NhhbOV9XFw0jcn-qWXq
JUL023 | 2024-07-17 10:34 | support@crystalgroup.in | Ajinomoto Bio Pharma | NA | NA | NA | KKFU6994964 | PREVENTIVE MAINTENANCE | Tanaya Jadhav |  |  | Preventive Maintenance |  |  |  | 2024-07-16 23:36 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6994964 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Coil dirty, supply sensor defective & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL023 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-07-17 09:30 | pravin.shinde@crystalgroup.in | YES | JUL073 | 15.7.24 |  | AJINOMOTO BIO | VISAKHAPATNAM | KKFU6994964 | SITE | FOC |  | 2024-08-27 00:18 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:36 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-12 23:34 | 2024-07-13 | Lease | Phone | Ajinomoto Bio Pharma | Visakhapatnam | KKFU6994964 | 40FT | SERVICE-AT SITE | PM SERVICES | Carrier | =20* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | 4.0 b / 14.6 b | 11.3 A / 11.1 A / 10.0 A | 406 V/ 403 V/ 405 A | Not done | Coil dirty, supply sensor defective & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change sensor | NA |  |  | https://drive.google.com/open?id=1R6fym1C1jaM_H0bLgDhTBRFBAw_R_KZV
JUL024 | 2024-07-17 10:35 | support@crystalgroup.in | Ajinomoto Bio Pharma | NA | NA | NA | KKFU6712079 | PREVENTIVE MAINTENANCE | Tanaya Jadhav |  |  | Preventive Maintenance |  |  |  | 2024-07-16 23:40 | support@crystalgroup.in | Ajinomoto Bio Pharma | KKFU6712079 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | Coil dirty, supply battery pack & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL024 | Carrier - Thinline | Thinline |  | 69NT40541321 |  | brand New | JSGA623040320 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-07-17 09:32 | pravin.shinde@crystalgroup.in | YES | JUL074 | 15.7.24 |  | AJINOMOTO BIO | VISAKHAPATNAM | KKFU6712079 | SITE | FOC |  | 2024-08-27 00:19 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:36 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-12 23:46 | 2024-06-13 | Lease | Phone | Ajinomoto Bio Pharma | Visakhapatnam | KKFU6712079 | 40FT | SERVICE-AT SITE | PM SERVICES | Carrier | +20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | 4.0 B / 15.0 B | 10.9 A / 11.3 A/ 11.0 A | 406 V/ 401 V/ 403 V | Not done | Coil dirty, supply battery pack & filter req | coil cleaned with water, checked settings all found okay, checked all parameters, need to change parts | BATTERY PACK AND FILLTER |  |  | https://drive.google.com/open?id=1b-2-j7auhgBFNmiDh1WZPIsRyjU-_21D
JUL025 | 2024-07-25 16:44 | pravin.shinde@crystalgroup.in | Jubliant Consumer Pvt Ltd | NA | NA | NA | GRMU3607418 | BREAKDOWN | VINIT |  |  | Complete Breakdown |  |  |  | 2024-07-28 10:32 | pravin.shinde@crystalgroup.in | Jubilant Consumer | GRMU3607418 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EVP INLET SENSOR FAULTY | REPLACED AND FOUND OKAY | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL025 | Daikin |  |  |  |  | Used |  | UMESH |  | BREAKDOWN | 2024-08-02 23:29 | support@crystalgroup.in | NO | [9 empty] | 2024-08-03 01:48 | support@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 00:12 | 2024-07-14 | Lease | Phone | Jubilant Consumer | NOIDA | GRMU3607418 | 40FT | SERVICE-AT SITE | EVP INLET SENSOR FAULTY | Daikin | -25*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 234 / 192.6 | 9.9 A / 9.9 A / 9.9 A | 414 V / 414 V / 414 V | Not done | EVP INLET SENSOR FAULTY | REPLACED AND FOUND OKAY | NA |  |  | https://drive.google.com/open?id=1cxDZ4zWsmZY9gyQuVQUKI-cvIXwhoB0n
JUL046 | 2024-07-25 16:57 | pravin.shinde@crystalgroup.in | Crystal JNPT | NA | NA | NA | WNGU3021858 | BODY REPAIR | KSHIROD |  |  | Running with issues |  |  |  | 2024-07-29 00:03 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | WNGU3021858 | 20-DRY GP | NA - DRY | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL046 | [7 empty] | KSHIROD |  | BODY REPAIR | 2024-08-26 23:59 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-03 01:50 | support@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:51 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-20 23:12 | 2024-07-26 |  |  |  |  | WNGU3021858 | [36 empty] | BODY REPAIR | WORK DONE | NA |  |  |  | NA | No | No | Can be done on next PM | NA
JUL047 | 2024-07-25 16:58 | pravin.shinde@crystalgroup.in | Crystal JNPT | NA | NA | NA | HDMU2595002 | BODY REPAIR | KSHIROD |  |  | Running with issues |  |  |  | 2024-07-29 00:04 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | HDMU2595002 | 20-DRY GP | NA-DRY | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL047 | [7 empty] | KSHIROD |  | BODY REPAIR | 2024-08-27 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-03 01:52 | support@crystalgroup.in | YES | JUL077 | YES |  |  | 2024-08-27 01:51 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-20 23:20 | 2024-07-05 |  |  |  |  | HDMU2595002 |  |  |  | Carrier | [32 empty] | BODY REPAIR | WORK DONE | NA |  |  |  | NA | No | No | Can be done on next PM | NA
JUL043 | 2024-07-25 16:46 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | NA | NA | NA | APRU5091606 | REPAIR | VINIT |  |  | Running with issues |  |  |  | 2024-07-28 23:55 | pravin.shinde@crystalgroup.in | Earl Corvus Habitat | APRU5091606 | 40-REEFER | CARRIER-THINLINE | REPAIR | LEASE | FOC | MOTORS DEFECTIVE | MOTOR CHANGED AND GAS FILL NOW WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL043 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | SHAHBUDDIN |  | REPAIR | 2024-08-02 23:32 | support@crystalgroup.in | NO | [9 empty] | 2024-08-03 01:54 | support@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:48 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:25 | 2024-07-21 | Lease | Phone | Earl Corvus Habitat | Kerala | APRU5091606 | 40FT |  | MOTOR MAKING NOISE |  | 2.5 | Clean | Clean |  | Need to replace | Clean | Need to replace | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4 / 180 | 12.3 / 12.3 / 12.4 | 405 / 405/ 405 | Short | MOTORS DEFECTIVE | MOTOR CHANGED AND GAS FILL NOW WORKING WELL | NA |  |  | https://drive.google.com/open?id=1vYhUI5mqXKpDj-JBG14T_syu5w3IJmlJ
JUL044 | 2024-07-25 16:47 | pravin.shinde@crystalgroup.in | Kiranakart | NA | NA | NA | GESU9460634 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 23:58 | pravin.shinde@crystalgroup.in | Kiranakart | GESU9460634 | 40-REEFER | CARRIER-ELITLINE | REPAIR | LEASE | FOC | AL-66 &AL-24 OBSERVED | VALVE CHANGED GAS REFILL AND NOW WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL044 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:33 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:26 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:50 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:32 | 2024-07-21 | Lease | Phone | Kiranakart | Haryana | GESU9460634 | 40FT | SERVICE-AT SITE | PM | Carrier | +0.0*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | DISCHARGE -20 | 2011-11-11 | 401 / 401/ 401 | Not done | AL-66 &AL-24 OBSERVED | VALVE CHANGED GAS REFILL AND NOW WORKING WELL | NA |  |  | https://drive.google.com/open?id=1WSum5FJjAB_Ll2YcIyJSKj0RVOzKsLet
JUL045 | 2024-07-25 16:48 | pravin.shinde@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | NA | NA | NA | CXRU1030387 | ICE FORMATION | VINIT |  |  | Running with issues |  |  |  | 2024-07-29 00:01 | pravin.shinde@crystalgroup.in | Heterp Plasma | CXRU1030387 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | ICE FORMATION ON COMPRESSOR | SUGGEST TO DO NOT CHANGE OVER DIRECTLY FIRST DO THE DEFROST AND THEN CHANGE THE SAME | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL045 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | VIRENDRA |  | ICE FORMATION | 2024-08-26 23:59 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:27 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:50 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:37 | 2024-07-21 | Lease | Phone | Heterp Plasma | Hyderabad | CXRU1030387 | 40FT | SERVICE-AT SITE | ICE FORMATION |  | -25 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 / 962 | 8.6 / 8.9 / 8.7 | 392 / 389 / 391 | Not done | ICE FORMATION ON COMPRESSOR | SUGGEST TO DO NOT CHANGE OVER DIRECTLY FIRST DO THE DEFROST AND THEN CHANGE THE SAME | YES |  |  | https://drive.google.com/open?id=1OAdNo6EC8UF0r6VBwO5-ElReD27X7bfv
JUL033 | 2024-07-25 16:56 | support@crystalgroup.in | Qwik Supply | NA | NA | NA | TCLU1903088 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:41 | pravin.shinde@crystalgroup.in | Qwik Supply | TCLU1903088 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL033 | Daikin | Daikin |  |  |  | Used | JSGA622180051 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:34 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:23 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:43 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:57 | 2024-07-16 | Lease | Phone | QWIK SUPPLY | LUCKNOW | TCLU1903088 | 20FT | SERVICE-AT SITE | PM SERVICES |  | 21*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 132 /1600 | 2009-09-09 | 421 / 421 /421 | Not done | Coil dirty | Coil dirty | NA |  |  | https://drive.google.com/open?id=1mQjWhs0bPjbgU-lWJ6MkSoApZLMUsnQX
JUL048 | 2024-07-25 16:58 | pravin.shinde@crystalgroup.in | Crystal JNPT | NA | NA | NA | HDMU2574289 | BODY REPAIR | KSHIROD |  |  | Running with issues |  |  |  | 2024-07-29 00:20 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | HDMU2574289 | 20-DRY GP | NA | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL048 | [7 empty] | KSHIROD |  | BODY REPAIR | 2024-08-27 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:27 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:18 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-20 23:39 | 2024-07-23 |  |  |  |  | HDMU2574289 | [36 empty] | BODY REPAIR | WORK DONE | NA |  |  |  | NA | No | No | Can be done on next PM | NA
JUL049 | 2024-07-25 16:59 | pravin.shinde@crystalgroup.in | Crystal JNPT | NA | NA | NA | SITE CABIN | KSHIROD | BODY REPAIR |  |  | Running with issues |  |  |  | 2024-07-29 00:21 | pravin.shinde@crystalgroup.in | Crystal Yard-JNPT | SITE CABIN | 20-DRY GP | NA-dry | REPAIR | STOCK | FOC | BODY REPAIR | WORK DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL049 | [7 empty] | KSHIROD |  | KSHIROD | 2024-08-27 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:28 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:18 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-20 23:45 | 2024-07-05 |  |  |  |  | SITE CABIN | [36 empty] | BODY REPAIR | WORK DONE | NA |  |  |  | NA | No | No | Can be done on next PM | NA
JUL050 | 2024-07-25 17:00 | pravin.shinde@crystalgroup.in | Crystal JNPT | NA | NA | NA | GESU9469328 | COMPRESSOR DEFECTIVE | PRAVIN |  |  | Running with issues |  |  |  | 2024-11-20 23:52 | operation@crystalgroup.in | Crystal Yard-JNPT | GESU9469328 | 40-REEFER | CARRIER-ELITLINE | REPAIR | NA | FOC | COMPRESSOR DEFECTIVE | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL050 | Carrier - Thinline | Elite line |  |  |  | Used |  | NA |  | COMPRESSOR DEFECTIVE | 2024-08-27 00:01 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:28 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:19 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-20 23:54 | 2024-07-23 |  |  |  |  | GESU9469328 | [36 empty] | COMPRESSOR DEFECTIVE | na | NO |  |  |  | NA | No | No | Can be done on next PM | NA
JUL051 | 2024-07-25 17:02 | pravin.shinde@crystalgroup.in | Reliance Industries | NA | NA | NA | TITU7263521 | COMPRESSOR DEFECTIVE | VINIT |  |  | Running with issues |  |  |  | 2024-11-20 23:57 | operation@crystalgroup.in | Qwik Supply | TITU7263521 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR DEFECTIVE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL051 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH |  | COMPRESSOR DEFECTIVE | 2024-08-27 00:01 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:28 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:19 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:45 | 2024-07-22 | Lease | Phone | QWIK SUPPLY | Hapur | TITU7263521 | 40FT | SERVICE-AT SITE | MACHINE SHUT DOWN |  | -30* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 30 / 1700 | 2010-10-10 | 400 / 400 / 400 | Short | COMPRESSOR DEFECTIVE | NA | YES |  |  | https://drive.google.com/open?id=1LUyp0NL-CQFXxHddF-v1PNC6TQQQMx_A
JUL052 | 2024-07-25 17:02 | pravin.shinde@crystalgroup.in | Crystal Yard-Vizag | NA | NA | NA | TRIU6680994 | NA | PRAVIN |  |  | Running with issues |  |  |  | 2024-11-21 00:06 | operation@crystalgroup.in | Crystal Yard-Vizag | TRIU6680994 | 20-REEFER | CARRIER-THINLINE | REPAIR | STOCK | FOC | PAINTING REQ | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL052 | Carrier - Thinline | Thinline |  | NSG60383780 |  | Used | JSGA623040285 | THIRD PARTY LOCAL |  | NA | 2024-08-27 00:01 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:54 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:20 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-21 00:10 | 2024-07-25 |  |  |  |  | TRIU6680994 | [36 empty] | PAINTING REQ | NA | NO |  |  |  | TRIP035 | No | No | Can be done on next PM | NA
JUL026 | 2024-07-25 17:05 | pravin.shinde@crystalgroup.in | DHL Supply Chain pvt Ltd | NA | NA | NA | DFOU6120281 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:33 | pravin.shinde@crystalgroup.in | DHL Supply | DFOU6120281 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | COIL DIRTY, LOW GAS | GAS REFILED AND CHECKED ALL PARAMETER WORKING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL026 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:38 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:20 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 01:20 | 2024-07-16 | Lease | Phone | DHL Supply | Hyderabad | DFOU6120281 | 40FT | SERVICE-AT SITE | PM SERVICES | Daikin | +3.5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 100 KPA / 1182 KPA | 8.5 A / 8.3 A/ 8.1 A | 398 A / 397 V / 395 V | Not done | COIL DIRTY, LOW GAS | GAS REFILED AND CHECKED ALL PARAMETER WORKING WELL | NA |  |  | https://drive.google.com/open?id=1k2Yop892GmsXbcCYug6bTwPST1vIae_0
JUL027 | 2024-07-25 17:08 | pravin.shinde@crystalgroup.in | Shivamrut | SHINDE | 9834586595 | NA | CXRU1032498 | NOT WORKING | RAMIZ |  |  | Running with issues |  |  |  | 2024-07-28 10:34 | pravin.shinde@crystalgroup.in | Shivamrut | CXRU1032498 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | SHEETKEY NEED TO REPLACED - DEFROST BUTTON NOT WORKING | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL027 | DAikin | LXE10E147F2 | M000892 | K31410139812 | DECOS 3F 2606 / 1 | used | JSGA622340362 | RAMIZ |  | NOT WORKING | 2024-08-02 23:39 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:20 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:01 | 2024-07-16 | Lease | Phone | Shivamrut | Solapur | CXRU1032498 | 40FT | SERVICE-ON CALL | FLUCTUATIONS IN TEMEPRATURE | Daikin | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1 B / 10.1 B | 9.5 A/ 9.5 A/ 9.7 A | 404 V/ 403 V/ 403 V | Not done | SHEETKEY NEED TO REPLACED - DEFROST BUTTON NOT WORKING | NEED PARTS | SHEET KEY |  |  | https://drive.google.com/open?id=1s2XtPV2O4tngQbrqACgaMEOSlJFpNVRP
JUL028 | 2024-07-25 17:08 | pravin.shinde@crystalgroup.in | Oriental Yeast | FAWAD | 8484936735 | NA | CICU1938117 | NOT PROPER | RAMIZ |  |  | Running with issues |  |  |  | 2024-07-28 10:35 | pravin.shinde@crystalgroup.in | Oriental Yeast | CICU1938117 | 20-SUPERFREEZER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | SET TEMP IS M20 & CONTAINER GOES TO M28 | NEED TO CHECK SENSOR | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL028 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | RAMIZ |  | NOT PROPER | 2024-08-26 23:54 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:21 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:38 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:10 | 2024-07-16 | Lease | Phone | Oriental Yeast | Pune | CICU1938117 | 20FT | SERVICE-ON CALL | FLUCTUATIONS IN TEMEPRATURE | Thermo king | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9 B / 10.5 B | 12.1 / 12.1/ 12.0 | 405/406/405 | Not done | SET TEMP IS M20 & CONTAINER GOES TO M28 | NEED TO CHECK SENSOR | NA |  |  | https://drive.google.com/open?id=1eQquhzraQGGcgGBp0t8z8ePjm73PyMlW
JUL029 | 2024-07-25 17:09 | pravin.shinde@crystalgroup.in | Mochan Food Processors Pvt Ltd | NA | NA | NA | MYRU4515260 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:36 | pravin.shinde@crystalgroup.in | Mochan Foods | MYRU4515260 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | INSTALLATION | done | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL029 | Daikin | Daikin | M0001112 | LXECOE136A2 | 24C2 | Used |  | RAMIZ |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:40 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:21 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:39 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:19 | 2024-07-12 | Lease | Phone | Mochan Foods | Kolkata | MYRU4515260 | 40FT | SERVICE-ON CALL | INSTALLATION | Daikin | -18*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B/ 11.8 B | 11.1 A/ 11.1 A/ 11.3 A | 401 V/ 400 V / 401 V | Not done | INSTALLATION | DONE | NA |  |  | https://drive.google.com/open?id=1thTnt93pSvhNXrDmZiX2rO5l5PzVKEaO
JUL030 | 2024-07-25 17:10 | pravin.shinde@crystalgroup.in | Mochan Food Processors Pvt Ltd | NA | NA | NA | MYRU4515260 | NOT WORKING WELL | VINIT |  |  | Running with issues |  |  |  | 2024-07-28 10:37 | pravin.shinde@crystalgroup.in | Mochan Foods | MYRU4515260 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | SHEETKEY & DISPLAY NOT PROPER, INLET SENSOR FAULTY, door damage | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL030 | Daikin | Daikin | M0001112 | LXECOE136A2 | 24C2 | Used |  | RAMIZ |  | NOT WORKING WELL | 2024-08-26 23:56 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:22 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:40 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:26 | 2024-07-16 | Lease | Phone | Mochan Foods | Kolkata | MYRU4515260 | 40FT | SERVICE-AT SITE | FLUCTUATIONS IN TEMEPRATURE | Daikin | -18*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3 B /11.9 B | 11.2 A / 11.2 A/ 11.3 A | 401 V/ 402 V/ 401 V | Not done | SHEETKEY & DISPLAY NOT PROPER, INLET SENSOR FAULTY, door damage | NEED TO REPLACED | NEED SPARE |  |  | https://drive.google.com/open?id=1j6OFljdc6_fWj2dRjdLM0Q8SeetDxb-T
JUL031 | 2024-07-25 17:11 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | NA | NA | NA | TITU9230980 | Not maintaining temp | PRAVIN |  |  | Running with issues |  |  |  | 2024-07-28 10:38 | pravin.shinde@crystalgroup.in | Cipla Unit 1 | TITU9230980 | 40-SUPERSTORE | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Condenser coil leak and keypad, display required | REPLACED CONDENSER COIL AND NITROGEN TEST DONE AND GAS CHARGED | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL031 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | SHAHBUDDIN |  | Not maintaining temp | 2024-08-02 23:42 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:22 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:40 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:40 | 2024-07-16 | Lease | Phone | Cipla Unit 1 | Goa | TITU9230980 | 40FT | SERVICE-AT SITE | FLUCTUATIONS IN TEMEPRATURE | Daikin | 3.5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 B / 18.0 B | 9.8 A / 9.8 A / 9.9 A | 410 V / 410 V/ 410 V | Short | Condenser coil leak and keypad, display required | REPLACED CONDENSER COIL AND NITROGEN TEST DONE AND GAS CHARGED | NA |  |  | https://drive.google.com/open?id=1zp4vCQJSGomPNMZZI5opwhYvXDv01FFw
JUL032 | 2024-07-25 17:12 | pravin.shinde@crystalgroup.in | GMR Hydrabad Air cargo | NA | NA | NA | CGMU2990461 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:40 | pravin.shinde@crystalgroup.in | GMR Hydrabad Air cargo | CGMU2990461 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | NEED AMBIENT & SUPPLY SENSOR | REQUIRED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL032 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-08-26 23:57 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:22 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:41 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 02:48 | 2024-07-17 | Lease | Phone | GMR Hyderabad Air cargo | Hyderabad | CGMU2990461 | 20FT | SERVICE-AT SITE | PM SERVICES | Carrier | NEED AMBIENT & SUPPLY SENSOR | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | DISCHARGE - 16.8 B | 11.0 A / 10.7 A / 10.9 A | 408 V/ 403 V / 405 V | Not done | NEED AMBIENT & SUPPLY SENSOR | REQUIRED PARTS | NA |  |  | https://drive.google.com/open?id=19BMJTPFI5vebzJLeEsQC5mXEC-Pyx-SO
JUL034 | 2024-07-25 17:13 | pravin.shinde@crystalgroup.in | Reliance Industries | NA | NA | NA | TITU7263521 | Breakdown | VINIT |  |  | Complete Breakdown |  |  |  | 2024-07-28 10:41 | pravin.shinde@crystalgroup.in | Reliance Industries | TITU7263521 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Leak in ESV and ISV valve | required parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL034 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH |  | Breakdown | 2024-08-26 23:57 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:23 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:44 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 03:18 | 2024-07-18 | Lease | Phone | QWIK SUPPLY | Hapur | TITU7263521 | 40FT | SERVICE-AT SITE | MACHINE SHUT DOWN |  | 30*C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 180 /1690 | 10.1 / 10.1 / 10.1 | 401 /401 / 401 | Short | Leak in ESV and ISV valve | required parts | YES |  |  | https://drive.google.com/open?id=1Z_GOcyTtw-s0NfUqD-EywSzE6bcLEjA4
JUL035 | 2024-07-25 17:14 | pravin.shinde@crystalgroup.in | Reliance Industries | NA | NA | NA | GESU9440432 | Breakdown | PRAVIN |  |  | Complete Breakdown |  |  |  | 2024-07-28 10:42 | pravin.shinde@crystalgroup.in | Reliance Industries | GESU9440432 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | VALVE LEAK | required parts | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL035 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | UMESH |  | Breakdown | 2024-08-26 23:57 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:24 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:44 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 03:24 | 2024-07-17 | Lease | Phone | QWIK SUPPLY | Lucknow | GESU9440432 | 40FT | SERVICE-AT SITE | MACHINE SHUT DOWN |  | NA | Clean | Clean |  |  | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | NA | NA | NA | Not done | VALVE LEAK | required parts | NA |  |  | https://drive.google.com/open?id=1rJgM5j19JF-WoCEEGGAnMN5MuX4oT5Af
JUL036 | 2024-07-25 17:14 | pravin.shinde@crystalgroup.in | Reliance Industries | NA | NA | NA | TDRU7151675 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:44 | pravin.shinde@crystalgroup.in | Reliance Industries | TDRU7151675 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL036 | Daikin | Daikin |  |  |  |  | JSGA622180053 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:45 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:24 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:45 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 03:35 | 2024-07-16 | Lease | Phone | QWIK SUPPLY | Lucknow | TDRU7151675 | 40FT | SERVICE-AT SITE | PM |  | -21*C | Clean | Clean |  |  | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 132 / 1600 | 2009-09-09 | 421 / 421/ 421 | Not done | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | NA |  |  | https://drive.google.com/open?id=11w02bHx9nbt2V-aULERGHdPnCRoIMoOP
JUL037 | 2024-07-25 17:15 | pravin.shinde@crystalgroup.in | North West logistic | NA | NA | NA | TITU9928040 | Breakdown | VINIT |  |  | Complete Breakdown |  |  |  | 2024-07-28 10:45 | pravin.shinde@crystalgroup.in | North West logistic | TITU9928040 | 40-REEFER | TK-MP4000 | SERVICE-ON CALL | LEASE | FOC | NOT ABLE TO FIND ON CALL | NEED TO VISIT | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL037 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | PRAVIN |  | Breakdown | 2024-08-02 23:46 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:24 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:45 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-11-21 00:14 | 2024-07-19 |  |  |  |  | TITU9928040 |  |  |  | Thermo king | [32 empty] | NOT ABLE TO FIND ON CALL | NEED TO VISIT | no |  |  |  | NA | No | No | Can be done on next PM | NA
JUL038 | 2024-07-25 17:16 | pravin.shinde@crystalgroup.in | Siemens | NA | NA | NA | TRIU6617646 | AMC | VINIT |  |  | Running with issues |  |  |  | 2024-07-28 10:46 | pravin.shinde@crystalgroup.in | Siemens | TRIU6617646 | 20-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | SALE | FOC | SPARES SENT | REQ TECHNICIAN FOR FITTING | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL038 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | VINIT |  | AMC | 2024-08-02 23:47 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:25 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:46 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 03:35
JUL039 | 2024-07-25 17:17 | pravin.shinde@crystalgroup.in | Reliance Industries | NA | NA | NA | CXRU1043912 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:47 | pravin.shinde@crystalgroup.in | Reliance Industries | CXRU1043912 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL039 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:50 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:25 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:46 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 03:49 | 2024-07-18 | Lease | Phone | QWIK SUPPLY | Hapur | CXRU1043912 | 40FT | SERVICE-AT SITE | PM |  | -25*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 95 / 1500 | 2008-08-08 | 398 / 398 / 398 | Not done | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | NA |  |  | https://drive.google.com/open?id=1emS1qjfRqY6gHNcXwlghClYu9YIHGl1Z
JUL040 | 2024-07-25 17:17 | pravin.shinde@crystalgroup.in | Jubliant Consumer Pvt Ltd | NA | NA | NA | GRMU3607418 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 10:48 | pravin.shinde@crystalgroup.in | Jubilant Consumer | GRMU3607418 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | VERIFICATION | SATISFIED CONTAINER RUNNING WELL | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL040 | Daikin |  |  |  |  | Used |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:51 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:25 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:46 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:02 | 2024-07-19 | Lease | Phone | Jubilant Consumer | Noida | GRMU3607418 | 40FT |  | PM |  | -25*C | Clean | Clean |  |  | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 200 / 1800 | 9.8 / 9.8 / 9.8 | 412 / 412 / 412 | Not done | VERIFICATION | SATISFIED CONTAINER RUNNING WELL | NA |  |  | https://drive.google.com/open?id=1HaaexO1WWqYLwUVL4IKtm7egEoXCPuJ3
JUL041 | 2024-07-25 17:18 | pravin.shinde@crystalgroup.in | Kiranakart | NA | NA | NA | KKFU6711832 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 23:51 | pravin.shinde@crystalgroup.in | Kiranakart | KKFU6711832 | 40-REEFER | CARRIER-THINLINE | INSTALLATION | LEASE | FOC | installation | INSTALLATION & TRANING DONE | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL041 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA623040288 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-02 23:52 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:26 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:47 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:08 | 2024-07-19 | Lease | Phone | Kiranakart | Delhi | KKFU6711832 | 40FT | SERVICE-AT SITE | PM |  | -2.9 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2 / 176 | 13 / 13/ 13 | 358 / 358 / 358 | Not done | NA | INSTALLATION & TRANING DONE | NA |  |  | https://drive.google.com/open?id=1N5q097G38gaaTGXhdJVxqjkbz6ZWgIRk
JUL042 | 2024-07-25 17:19 | pravin.shinde@crystalgroup.in | Kiranakart | NA | NA | NA | GESU9460634 | PREVENTIVE MAINTENANCE | VINIT |  |  | Preventive Maintenance |  |  |  | 2024-07-28 23:53 | pravin.shinde@crystalgroup.in | Kiranakart | GESU9460634 | 40-REEFER | CARRIER-ELITLINE | INSTALLATION | LEASE | FOC | INSTALLATION | INSTALLATION DONE BUT NEED SOME PARTS TO RECTIFY | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL042 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-26 23:59 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:26 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 01:48 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:15 | 2024-07-20 | Lease | Phone | Kiranakart | Haryana | GESU9460634 | 40FT | SERVICE-AT SITE | PM |  | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | DISCHARGE - 16 | 2011-11-11 | 373 /373 / 373 | Not done | AL-66 &AL-24 OBSERVED | INSTALLATION DONE BUT NEED SOME PARTS TO RECTIFY | NA |  |  | https://drive.google.com/open?id=1Cbro5AMbBSgJygrOB0fGXh0zQ8Fhn5yn
JUL053 | 2024-07-28 22:52 | pravin.shinde@crystalgroup.in | Oriental Yeast | NA | NA | NA | PCIU6008014 | Breakdown | RAMIZ |  |  | Complete Breakdown |  |  |  | 2025-01-18 16:49 | crm@crystalgroup.in | Oriental Yeast | PCIU6008014 | 40FT | Daikin | REPAIR | SALE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL053 | Daikin | Daikin | AOO4920 |  |  | Used |  | RAMIZ |  | Breakdown | 2024-08-27 00:02 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:54 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:20 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 04:52 | 2024-07-26 | Lease | Phone | Oriental Yeast | Satara | PCIU6008014 | 40FT | SERVICE-AT SITE | MACHINE SHUT DOWN |  | -2*C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | -1 B / 8.3B | 6 / 6 / 6.1 | 420/ 419 / 420 | Not done | SUCTION GAS SENSOR, FILTER SENSOR, R134A GAS | NA | YES |  |  | https://drive.google.com/open?id=1Lvgmn7RzEZ1x4qVpdzjnRKM_9Zm4MUH_
JUL054 | 2024-07-26 18:46 | mohammednehal64@gmail.com | Mohammed Nehal | Mohammed Nehal | 8697104745 | Founder | GESU9454891 | Installation Help Required |  |  |  | Installation |  |  |  | 2024-08-20 04:00 | [23 empty] | Installation Help Required | 2024-08-27 00:02 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:54 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:21 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:02
JUL056 | 2024-07-29 10:01 | vinit.mewada@crystalgroup.in | Lupin - Bhiwandi | Akash Gorle | 9370588166 | - | CXRU1030427 | abnormal sound | sushma |  |  | Running with issues |  |  |  | 2025-01-18 17:22 | crm@crystalgroup.in | Lupin - Bhiwandi | CXRU1030427 | 40FT | Hetero Unit 3 | SERVICE-AT SITE | LEASE | CHARGEABLE | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL056 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | VIRENDRA |  | abnormal sound | 2024-08-27 00:03 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:55 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:22 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:09 | 2024-07-19 | Paid | Phone | Hetero - 3 | Hyderabad | CXRU1030427 | 40FT |  |  |  | +5.0*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 112 KPA / 1603 KPA | 11.0 / 11.3 / 11.1 | 409 / 408 / 407 | Not done | INDICATOR SHEET PANLE & SHEETKEY DEFECTIVE REQ CHANGE SET POINT FROM +20 TO +5 | COIL CLEAN AND CHANGE SET TEMP WORKING WELL | YES |  |  | https://drive.google.com/open?id=1r7-NzVYK5zRVaCyfl7h3041gljU7l-2z
JUL057 | 2024-08-09 15:22 | support@crystalgroup.in | Qwik Supply | NA | NA | Na | MYRU4518356 | Coil dirty | VINIT |  |  | Running with issues |  |  |  | 2024-08-20 04:00 | support@crystalgroup.in | Qwik Supply | MYRU4518356 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL057 | Daikin | LXE10E136 A2 | M005086 | DCOZ3E |  | Used | JSGA622180065 | UMESH |  | Coil dirty | 2024-08-27 00:03 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:56 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:22 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:14 | 2024-07-26 | Free of Cost | Phone | QWIK SUPPLY | Lucknow | MYRU4518356 | 40FT | SERVICE-AT SITE | PM |  | -21.9 | Clean | Clean |  | Need to replace | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 135 / 1800 | 2012-12-12 | 422 / 422 / 422 | Not done | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | NO |  |  | https://drive.google.com/open?id=1fHslyTsXQU3kSV7jKGVpiUqXPTKoNShz
JUL058 | 2024-08-20 19:01 | vinit.mewada@crystalgroup.in | Qwik Supply | N/A | N/A | N/A | TCLU1903088 | PREVENTIVE MAINTENANCE | Umesh |  |  | Preventive Maintenance |  |  |  | 2024-08-20 06:37 | vinit.mewada@crystalgroup.in | Qwik Supply | TCLU1903088 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL058 | Daikin | Daikin |  |  |  | Used | JSGA622180051 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-08-20 06:38 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-20 06:42 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-22 01:01 | vinit.mewada@crystalgroup.in | NO | [7 empty] | 2024-09-13 05:22 | 2024-07-26 | Free of Cost | Phone | QWIK SUPPLY | Lucknow | TCLU1903088 | 20FT |  |  |  | -21* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 100 / 1700 | 2010-10-10 | 420 / 420 / 420 | Short | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | NO |  |  | https://drive.google.com/open?id=1xPWzlwMBdn-ok0KF81RM9YizgCxIZOB7
JUL059 | 2024-08-21 10:32 | chaurasiagarima97@gmail.com | Lupin Limited | NA | NA | NA | TCLU1908599 | INSTALLATION | UMESH |  |  | Installation |  |  |  | 2024-08-21 23:02 | vinit.mewada@crystalgroup.in | LUPIN LIMITED | TCLU1908599 | 20 FT | NA | SERVICE-AT SITE | NA | NA | REGULAR SURVEY | NA | UMESH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL059 | DAIKIN LXE |  |  |  |  | USed |  | UMESH |  | INSTALLATION | 2024-08-22 02:20 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:56 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:23 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:27 | 2024-07-30 | Lease | Phone | Lupin Limited | Bhopal | TCLU1908599 | 40FT | SERVICE-AT SITE |  | Daikin | -15* | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | NA | Not done | Coil dirty | coil cleaned with water, checked settings all found okay, checked all parameters | NO |  |  | https://drive.google.com/open?id=1Png2QWCb7CqshoRmFYUCpvadh2fWTFQf
JUL060 | 2024-08-21 10:32 | chaurasiagarima97@gmail.com | Lupin Limited | NA | NA | NA | TCLU1908599 | INSTALLATION | UMESH |  |  | Installation |  |  |  | 2024-08-21 23:10 | vinit.mewada@crystalgroup.in | BHARAT PETROLEUM | TCLU1908599 | 20 FT | 2010 | SERVICE-AT SITE | LEASE | NA | PREMAINTANCE | PREMAINTANCE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL060 | DAIKIN LXE |  |  |  |  | USed |  | UMESH |  | INSTALLATION | 2024-08-22 02:20 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:57 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:24 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 16:50 | 2024-07-27 |  |  |  |  | TRIU6618581 |  |  |  | Carrier | -3"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.6 | 2011-11-11 | 410/410/410 | Not done | NA | Container running in good condition | No | https://drive.google.com/open?id=1_b-uCGuzfNAhYU4bmZToaIsthzTBNuZN |  |  | TRIP031 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
JUL061 | 2024-08-21 10:37 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | TRIU6618391 | PRE MAINTANCE | UMESH |  |  | Preventive Maintenance |  |  |  | 2024-08-21 23:20 | vinit.mewada@crystalgroup.in | QWIK SUPPLY LUCKNOW | TRIU6618391 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | DATA SUPPLY, RETURN, DEFROST X 2 NOS REQUIRED | coil cleaned with water, checked settings all found okay, checked all parameters, required spares | DATA SUPPLY SENSOR, RETURN SENSOR, DEFROST SENSOR ( MAIN UNIT ) AND DEFROST SENSOR ( STANDBY UNIT ) |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL061 | Carrier - Thinline | Thinline |  |  |  | Used |  | UMESH |  | PRE MAINTANCE | 2024-08-22 02:25 | support@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:57 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:25 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 17:05 | 2024-07-28 |  |  |  |  | TRIU6618581 |  |  |  | Carrier | -30"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 15 -Discharge | 2011-11-11 | 399/399/399 | Not done | NA | Working in good condition | Yes | https://drive.google.com/open?id=1qVnjlBpGL0AnPnWJlI-Li9RDV2wkF1yH |  |  | TRIP031 | Yes | Yes | Urgent | Installation of Data Supply Sensor | Data Supply Sensor Return Sensor Defrost Sensor Standby Unit | crm@crystalgroup.in
JUL063 | 2024-08-21 10:40 | chaurasiagarima97@gmail.com | ITC Ltd | NA | NA | NA | PCIU6003244 | PREMAINTANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-08-21 23:33 | vinit.mewada@crystalgroup.in | ITC LTD | PCIU6003244 | 40 FT | 2007 | SERVICE-AT SITE | LEASE | NA | Panle foaming weak, Filter rusty, Evp motor noisy | required spares | FILLTER , RISEUP MOTOR , REFORMING R/S- 2,3,67 AND L/S- 5TH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL063 | Daikin |  |  |  |  | used |  | VIRENDRA |  | PREMAINTANCE | 2024-08-27 00:04 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:58 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:26 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 17:18 | 2024-07-28 |  |  |  |  | PCIU6003244 |  |  |  | Daikin | -20"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 63KPA/1580KPA | 8.9A/8.7A/8.5A | 413V/409V/411V | Not done | NA | Internal LIS 5th panel loose to refoaming , RIS Evp Motor noisy to be replaced | Yes | https://drive.google.com/open?id=1bRqonY37NlO0jlmQcbNKMQ3Sx9yJzOun |  |  | TRIP028 | Yes | Yes | Urgent | Internal LIS 5th panel loose to refoaming , RIS Evp Motor noisy to be replaced | Filter Drier RIS Evp motor REfoaming internal | crm@crystalgroup.in
JUL062 | 2024-08-21 10:38 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | CICU2779914 | PRE MAINTANCE | UMESH |  |  | Preventive Maintenance |  |  |  | 2024-08-21 23:24 | vinit.mewada@crystalgroup.in | Qwik Supply | CICU2779914 | 20 FT | 2022 | SERVICE-AT SITE | LEASE | NA | PRE MAINTAINANCE | PRE MAINTAINANCE | EVP SENSOR, SUPPLY SENSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL062 | Thermoking | Magnum Plus | E0GM030254 | ABC782800322010282 |  | BrandNew |  | UMESH |  | PRE MAINTANCE | 2024-08-27 00:04 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:58 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:25 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 17:28 | 2024-07-28 |  |  |  |  | CICU2779914 |  |  |  | Thermo king | -40'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Discharge - 24 | 2010-10-10 | 400/400/400 | Not done | NA | Container running in good condition | Yes | https://drive.google.com/open?id=1HztrSwN_mPWlADE1InaGP1ivfBB4SNa8 |  |  | TRIP031 | Yes | Yes | Urgent | YES | Evp sensor Supply sensor | crm@crystalgroup.in
JUL064 | 2024-08-21 10:41 | chaurasiagarima97@gmail.com | ITC Ltd | NA | NA | NA | MYRU4519748 | PREMAINTANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-08-21 23:39 | vinit.mewada@crystalgroup.in | ITC LIMITED | MYRU4519748 | 40 FT | 2010 | SERVICE-AT SITE | LEASE | NA | body work and evaporaor motor heavy noisy | REQUIRED SPARES | ALUMINIUM DAMPER SHEET, EVP MOTOR HEAVY SOUNDS |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL064 | Daikin | Daikin | M003143 | LXE10E136A |  | Used | JSGA623040176 | VIRENDRA |  | PREMAINTANCE | 2024-08-27 00:05 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:58 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:26 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 17:37 | 2024-07-28 |  |  |  |  | MYRU4519748 |  |  |  | Thermo king | -18'C | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 150KPA/1680KPA | 10.6/10.5/10.3 | 411/407/409 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1nurPEN0MpKMj8_eJizeCpLPg_K58M2a2 |  |  | TRIP028 | Yes | Yes | Urgent | Installation Aluminium Dambar Sheet ,Evp motor | Aluminium Dambar Sheet Evp motor | crm@crystalgroup.in
JUL065 | 2024-08-21 10:43 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | TITU9927240 | PREMAINTANCE | UMESH |  |  | Preventive Maintenance |  |  |  | 2024-08-21 23:47 | vinit.mewada@crystalgroup.in | Qwik Supply | TITU9927240 | 40 FT | 2013 | SERVICE-AT SITE | LEASE | NA | keypad, mantrap & patch work required | required spares | KEYPAB (MP400), MANTRAP , R/S PANEL NO.5 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL065 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | UMESH |  | PREMAINTANCE | 2024-08-27 00:05 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:59 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 17:57 | 2024-07-28 |  |  |  |  | TITU9927240 |  |  |  | Thermo king | +3.5'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Discharge - 22 | 2008-08-08 | 390/390/390 | Not done | NA | Running in good condition | Yes | https://drive.google.com/open?id=1kyvfL2JCXIKxLogI3UD5rCFVdRBpkc8G |  |  | TRIP031 | Yes | Yes | Urgent | Installation Keypad Mp4000,Mantrap,R/s Pannel | Keypad Mp4000 Mantrap R/s Pannel | crm@crystalgroup.in
JUL066 | 2024-08-21 10:46 | chaurasiagarima97@gmail.com | APL Health Care | NA | NA | NA | APRU5093234 | MOTOR MAKING NOISE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-21 23:51 | vinit.mewada@crystalgroup.in | APL Health | APRU5093234 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | MOTOR NOISY | WORKING WELL | R 134A |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL066 | Carrier - Thinline | Thinline | [5 empty] | VIRENDRA |  | MOTOR MAKING NOISE | 2024-08-27 00:05 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:59 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-10 18:15 | 2024-07-25 |  |  |  |  | APRU5093234 |  |  |  | Carrier | +20"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 13 | 9.6/9.8/10 | 404/401/403 | Short | NA | NA | No | https://drive.google.com/open?id=1EZxKcsa5nI37Slbqd2T4azsXAQcdlGqY |  |  | TRIP028 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
JUL069 | 2024-08-21 10:50 | chaurasiagarima97@gmail.com | Kiranakart | NA | NA | NA | GESU9460634 | TEMEPRATURE PROBLEM | UMESH |  |  | Running with issues |  |  |  | 2024-08-22 00:09 | vinit.mewada@crystalgroup.in | KIRANAKART ( ZEPTO ) | GESU9460634 | 40 FT | 2008 | SERVICE-AT SITE | LEASE | NA | SPT WITH JACK REQUIRED AND CONTROLLER SUSPECTED | REQUIRED SPARES | SPT WITH JACK , CONTROLLER |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL069 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH |  | TEMEPRATURE PROBLEM | 2024-08-27 00:06 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:02 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:28 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 09:54 | 2024-06-29 |  |  |  |  | GESU9460634 |  |  |  | Carrier | +3"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Discharge 18 | 2012-12-12 | 370/370/370 | Not done | Container running in good condition | Container running in good condition | No | https://drive.google.com/open?id=1C5FfjRfoikyK2vZP9eWdKBDvTNu3T7Te |  |  | TRIP031 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
JUL071 | 2024-08-21 10:52 | chaurasiagarima97@gmail.com | Jubliant Consumer Pvt Ltd | NA | NA | NA | TRIU6687350 | NOT COOLING | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-22 00:20 | vinit.mewada@crystalgroup.in | JUBILANT CONSUMER | TRIU6687350 | 20 FT | 2011 | SERVICE-AT SITE | LEASE | NA | LOW GAS IN THE SYSTEM | LOW GAS IN THE SYSTEM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL071 | Carrier |  |  |  |  | USed |  | SHAHBUDDIN |  | NOT COOLING | 2024-08-22 03:32 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:03 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 10:13 | 2024-07-31 |  |  |  |  | TRIU6687350 |  |  |  | Carrier | -25"C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/210 | 8.9/8.9/9.0 | 401/398/398 | Short | Temp. Issue Low Gas in System | Container working in satisfactory condition | No | https://drive.google.com/open?id=1gorpyktIDZafY_H3cAXXpdTmMHegfDlF |  |  | TRIP036 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
JUL072 | 2024-08-21 10:53 | chaurasiagarima97@gmail.com | Symbiotech | NA | NA | NA | TRIU6617292 | NOT COOLING | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-22 00:25 | vinit.mewada@crystalgroup.in | Symbiotech | TRIU6617292 | 20 FT | NA | SERVICE-AT SITE | LEASE | NA | LEFT SIDE EVAPORATOR MOTOR IS NOT WOLRING PROPERLY | REQUIRED SPARE | EVAPORATOR MOTOR SINGLE PHASE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL072 | Carrier - Thinline | Thinline |  |  |  | Used |  | RAMIZ |  | NOT COOLING | 2024-08-27 00:07 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:04 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 10:23 | 2024-07-31 |  |  |  |  | TRIU6687350 |  |  |  | Carrier | +15*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Not done | Clean |  | 0.8/9.8 | 12/12/12.1 | 390/391/390 | Not done | Found left side evp motor low speed ,coil burn out | Reefer unit running in normal condition | Yes | https://drive.google.com/open?id=1pUAkUHO8KWK-QxLhyse1ztQpHaYkvRPP |  |  | NA | Yes | Yes | Urgent | Installation Evp motor single phase | Evp motor single phase | crm@crystalgroup.in
JUL073 | 2024-08-21 10:56 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | CXRU1042578 | NOT COOLING | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-22 00:29 | vinit.mewada@crystalgroup.in | QWIK SUPPLY SILIGURI | CXRU1042578 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | ABNORMAL POWER SUPPLY AND SUPPLY SENSOR DEFECTIVE | REQUIRED SPARE | SUPPLY SENSORS - 2 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL073 | Daikin | LXE10E147F2 | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032 | RAMIZ |  | NOT COOLING | 2024-08-27 00:07 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:04 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 10:37 | 2024-07-29 |  |  |  |  | CXRU1042578 |  |  |  | Daikin | 0*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Not done | Clean |  | Suction 0.5 | 10.5/10.5/10.6 | 401/400/401 | Not done | Found abnormal power supply & supply sensor out of range | Need to replace supply sensor | Yes | https://drive.google.com/open?id=11L52l9IJMgWpR-P56M-1-O6TMTV6gmMu |  |  | NA | Yes | Yes | Urgent | Installation Supply sensor | Supply sensor | crm@crystalgroup.in
JUL074 | 2024-08-21 10:57 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | CXRU1045453 | NOT COOLING | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-22 00:33 | vinit.mewada@crystalgroup.in | Qwik Supply | CXRU1045453 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | EXPANSION VALVE DEFECTIVE | REQUIRED SPARES | EXPENSION VALVE BODY , EXPENSION VALVE COIL |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL074 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ |  | NOT COOLING | 2024-08-27 00:08 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:04 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:30 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 10:44 | 2024-07-27 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -6*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Not done | Clean |  | 0.1/9.5 | 9.1/9.1/9.3 | 419/420/419 | Not done | Expansion valve not working | Unit under observation | Yes | https://drive.google.com/open?id=1piByhMm9f7PNlEGmmr_TO-g8-AjBWR9j |  |  | NA | Yes | Yes | Can be done on next PM | Expansion valve suspected | Expansion valve suspected | crm@crystalgroup.in
JUL055 | 2024-08-21 11:15 | chaurasiagarima97@gmail.com | Mochan Food Processors Pvt Ltd | SUSANTA | 9674919458 | SITE IN CHARGE | MYRU4500552 | INSTALLATION | RAMIZ |  |  | Installation |  |  |  | 2024-12-13 14:58 | service@crystalgroup.in | MOCHAN FOODS | MYRU4500552 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | compressor tripped due to low voltage | need to replaced MP 3000 relay board | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL055 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | RAMIZ |  | INSTALLATION | 2024-08-27 00:03 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 00:55 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:21 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:02 | 2024-07-29 | Lease | Phone | Mochan Foods | Kolkata | MYRU4500552 | 40FT | SERVICE-AT SITE | COMPRESSOR TRIPPED |  | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3 B/ 16.3 B | 9.1 / 9.1/9.0 | 344 / 345 / 344 | Not done | UNIT TRIP EVERY AFTER 45MIN | NEED TO CHANGE RELAY BOARD | YES |  |  | https://drive.google.com/open?id=1VmPPsp0KRoh6D0I9RHSsO-DvxI_BKWBK
AUG003 | 2024-08-21 11:56 | chaurasiagarima97@gmail.com | LAURUS LAB UNIT 2 | MURTHY | 9908127999/ 8916762247 | NA | CICU1442220 | DISMENTAL AND REFIX 2 BAY REFEER CONTAINER | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-21 05:22 | vinit.mewada@crystalgroup.in | LAURUS LAB UNIT 2 | CICU1442220 | 40 FT | NA | SERVICE-AT SITE | SALE | CHARGEABLE | DISMENTAL AND REFIX THE ISSUE | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG003 | [7 empty] | VIRENDRA |  | DISMENTAL AND REFIX 2 BAY REFEER CONTAINER | 2024-08-22 00:46 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:18 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 11:35 | 2024-08-03 |  |  |  |  | CICU1442220 |  |  |  | Carrier | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | NA | NA | No | https://drive.google.com/open?id=11xX1X1qhEQO0Ptlee6fG6cit1eSBvCyo |  |  | TRIP037 | No | No | Can be done on next PM | Na | NA | crm@crystalgroup.in
AUG006 | 2024-08-21 12:17 | chaurasiagarima97@gmail.com | METRO FOODS | MR. PRAMOD | 8865021446 | DUTY INCHARGE TECH SECTION | TITU7263521 | COMPRESSOR MAKING NOISE, FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 02:09 | chaurasiagarima97@gmail.com | Qwik Supply | TITU7263521 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR MAKING NOISE | REPLACED COMPRASSURE AND FILTER AND REFILL THE GAS, EXPENSION VALVE, VACUMME SYSTEM, | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG006 | Daikin |  |  |  |  | brand New | JSGA622180055 | SHAHBUDDIN |  | COMPRESSOR MAKING NOISE, FLUCTUATIONS IN TEMEPRATURE | 2024-08-22 03:36 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:32 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:17 | chaurasiagarima97@gmail.com | YES | AUG001 | TECHNICIAN | [5 empty] | 2025-01-16 14:29 | 2024-08-02 |  |  |  |  | TITU7263521 |  |  |  | Daikin | -30*C | Clean | [22 empty] | Okay | [6 empty] | Short | NA | NA | No | https://drive.google.com/open?id=1jk24TKMOyTwm-2fvoTbRWHlXUrJP2rzx |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG004 | 2024-08-21 11:59 | chaurasiagarima97@gmail.com | LAURUS LAB UNIT 2 | MURTHY | 8916762247 | EXECUTIVE | CICU1442180 | DISMENTAL AND REFIX 2 BAY REFEER CONTAINER | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-21 05:16 | vinit.mewada@crystalgroup.in | LAURUS LAB UNIT 2 | CICU1442180 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PM SERVICES | SHEET KEY LOGO, SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG004 | [7 empty] | VIRENDRA |  | DISMENTAL AND REFIX 2 BAY REFEER CONTAINER | 2024-09-06 05:03 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-08 23:49 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:13 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 11:54 | 2024-08-03 |  |  |  |  | CICU1442180 |  |  |  | Thermo king | 24*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | 10.9/10.8/11 | 418/419/418 | Short | Container in proper working condition | Clean the condenser coil and set temp. as per cleint req. | Yes | https://drive.google.com/open?id=1OOjF97d_BXHgDJUm8uXyfE2ZswMnEOJj |  |  | TRIP037 | Yes | Yes | Can be done on next PM | Installation Sheetkey, Logo Software | Sheetkey Logo Software | crm@crystalgroup.in
AUG007 | 2024-08-21 12:21 | chaurasiagarima97@gmail.com | BIOCON | PURUMA YADAV | 9121483858 | NA | TDPU5800414 | ALEI07 & COMPRESSOR STOP | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-21 05:11 | vinit.mewada@crystalgroup.in | BIOCON | TDPU5800414 | 40FT | 2011 | SERVICE-AT SITE | LEASE | NA | ALE107, COMPRESSOR STOP | NA | R13YA DISCHARGE CENTER , INLET SENSOR ELDER DRIVER COMPRESSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG007 | [7 empty] | RAMIZ |  | ALEI07 & COMPRESSOR STOP | 2024-09-09 01:15 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2025-01-15 18:32 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:16 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 14:54 | 2024-08-05 |  |  |  |  | TDRU5800414 |  |  |  | Daikin | +4.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1C0OtWyn069q7GJqvaTcWnO54WT1w76yc |  |  | TRIP038 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG008 | 2024-08-21 12:26 | chaurasiagarima97@gmail.com | QWIK SUPPLY RAJPURA | DEEPAK S | 8814085199 | ASST. CPC MANAGER | CXRU1045453 | NOT WORKING WITH AL F803/F804 | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-21 05:06 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | CXRU1045453 | 40 FT | 2011 | SERVICE-AT SITE | NA | NA | UNIT NOT WORKING WITH AC F803 / F 809 | NA | GAS R13HA, FLITER DRIVER , TEMP SENSOR , INLET SENSOR, VACCUM PUMP |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG008 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | SHAHBUDDIN |  | NOT WORKING WITH AL F803/F804 | 2024-12-31 18:06 | mum.depot@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:33 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:18 | chaurasiagarima97@gmail.com | YES | AUG090 | COURIER | [5 empty] | 2025-01-16 15:08 | 2024-08-05 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -6*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1AQW3KMAZBxLqUmidyDMXb5_KpzbTBA96 |  |  | TRIP038 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG009 | 2024-08-21 12:34 | chaurasiagarima97@gmail.com | QWIK SUPPLY RAJPURA | DEEPAK SHARMA | 8814085799 | ASST CPC MANAGER | TCLU1130265 | PRE MATINATNCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-08-21 05:01 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | TCLU1130265 | 40 FT | 2010 | SERVICE-AT SITE | NA | NA | PM SERVICES | PRE MAINTAINACE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG009 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN |  | PRE MATINATNCE | 2024-08-22 03:38 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:19 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:28 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:07 | 2024-08-05 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/200 | 11.2/11.2/11.1 | 400/400/400 | Short | PM service | PM service done | No | https://drive.google.com/open?id=18Yq2-UuRaKJDONEg1K1cvX-9l3JJItxP |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG010 | 2024-08-21 12:36 | chaurasiagarima97@gmail.com | QWIK SUPPLY RAJPURA | DEEPAK S | 8814085199 | ASST CPC MANAGER | CICU1799140 | PRE MAINTANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-08-21 04:59 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURU | CICU1799140 | 10 FT | 2020 | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PRE MAINTAINACE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG010 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | SHAHBUDDIN |  | PRE MAINTANCE | 2024-08-22 03:39 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:19 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:28 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:17 | 2024-08-05 |  |  |  |  | TITU7263521 |  |  |  | Thermo king | -40*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6/19 | 9.8/9.8/9.8 | 403/403/403 | Short | PM service | PM service done | No | https://drive.google.com/open?id=1QI_MTXGe90xeGKi1eCUaMTzzacgkK71G |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG011 | 2024-08-21 13:14 | chaurasiagarima97@gmail.com | Qwik Supply | SAHIL MEHRA | 7340855526 | ROUTINE INCHARGE | MURU4501435 | PRE MAINTAINCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-08-21 04:55 | vinit.mewada@crystalgroup.in | Qwik Supply | MYRU4501435 | 40 FT | 2010 | SERVICE-AT SITE | LEASE | NA | PM SERVICES | PM SERVICES | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG011 | Daikin | Daikin |  | LXE10E136A |  | Refurbished |  | SHAHBUDDIN |  | PRE MAINTAINCE | 2024-08-22 03:39 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:19 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:22 | 2024-08-06 |  |  |  |  | MYRU4501435 |  |  |  | Daikin | -5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2018-08-01 | 12.3/12.3/12.4 | 401/401/402 | Short | PM Service | PM Service done | No | https://drive.google.com/open?id=1VZiT-8teDLvL_1X_3jzjz67881iYo2i3 |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG012 | 2024-08-21 13:19 | chaurasiagarima97@gmail.com | QWIK SUPPLY SHRIHID | SAHIL MEHRA | 7340855526 | ROUTIN INCHARGE | NYKU7931452 | PRE MAINTAINACE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-08-21 04:49 | vinit.mewada@crystalgroup.in | QWIK SUPPLY SHRIHID | NYKU7931452 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | PRE MAINTANANCE | NEED PRE MAINTAINANCE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG012 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | SHAHBUDDIN |  | PRE MAINTAINACE | 2024-08-22 03:40 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:20 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:29 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:29 | 2024-08-06 |  |  |  |  | NYKU7931452 |  |  |  | Carrier | -19*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7/18 | 12.5/12.6/12.6 | 402/402/402/ | Short | PM service | PM service Done | No | https://drive.google.com/open?id=1kfULuPkD9Xfab2cErbtXIC-8w8831dJO |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG013 | 2024-08-21 13:24 | chaurasiagarima97@gmail.com | FDC LIMITED | AMAR THAKUR | 9816366211 | SR MANAGER | TRIU6616911 | DISPLAY NOT VISIBLE, INSPECTION AND PTI | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-21 04:44 | vinit.mewada@crystalgroup.in | FDC PHARMA | TRIU6616911 | 20 FT | 2010 | SERVICE-AT SITE | LEASE | NA | CARRIER UNIT OFF LODGE INSPECTION AND PTI, FIND DISPLAY IS FADED AND NEED TO COMPRESSOR OIL FOR REFILING. | NEED TO CKECK ALL PARTS WITH CONTAINER STATUS | DISPLAY - 1, COMPRESSOR - 1, BATTERY PACE CARRIER (AC53) --1 , RISLU C- 1KG |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG013 | Carrier - Thinline | Thinline |  | M3X60329564 |  | Used |  | SHAHBUDDIN |  | DISPLAY NOT VISIBLE, INSPECTION AND PTI | 2024-09-09 01:15 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2025-01-15 18:33 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:19 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 15:21 | 2024-08-07 |  |  |  |  | TRIU6616911 |  |  |  | Carrier | -18*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1SrYE3n8v9JYTHpMLo1BS6-a2cqJdrORE |  |  | TRIP038 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG015 | 2024-08-21 13:30 | chaurasiagarima97@gmail.com | Shivamrut | RAJKUMAR SHINDE | 9834586595 | NA | CXRU1032498 | ALF803, SHEET KEY NOT WORKING UNIT OFF | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-21 04:24 | vinit.mewada@crystalgroup.in | SHIVAMRUT - AKLUJ | CXRU1032498 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | ALF803, SHEET KEY NOT WORKING , UNIT OFF | NEED TO REPLACE HUS SENSOR AND SHEET KEY, CONTROLLER AND EXPANCTION VALVE AND COIL | HUMADITY SENSOR , SHEET KEY, CONTROLLER AND EXPANCTION VALVE AND COIL |  |  |  | DAikin | LXE10E147F2 | M000892 | K31410139812 | DECOS 3F 2606 / 1 | used | JSGA622340362 | RAMIZ |  | ALF803, SHEET KEY NOT WORKING UNIT OFF | 2024-08-21 21:12 | vinit.mewada@crystalgroup.in | YES | JUL037 | 13.6.24 |  | SHIVAMRUT | AKLUJ | CXRU1032498 | SITE | FOC |  | 2025-01-15 18:34 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:20 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 15:33 | 2024-08-07 |  |  |  |  | CXRU1032498 |  |  |  | Daikin | -21*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1oIF-XiGaoD68MlR4iuql3zpgGjk6BybP |  |  | NA | No | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG014 | 2024-08-21 13:27 | chaurasiagarima97@gmail.com | QWIK SUPPLY RAJPURA | NA | NA | NA | CICU3876631 | UNIT NOT WORKING | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-21 04:35 | vinit.mewada@crystalgroup.in | QWIK SUPPLY RAJPURA | CICU3876631 | 10 FT | Thermoking 2023 | SERVICE-AT SITE | LEASE | AMC | UNIT NOT WORKING | DISCONNECTED THE BATTERY MODULE ( NEED TO REPLACE BATTERY ) | BATTERY PACK -MP4000 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG014 | Thermoking | Magnum + | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New |  | RAMIZ |  | UNIT NOT WORKING | 2024-09-09 01:15 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:06 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:20 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 15:45 | 2024-08-07 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40*C | Clean | [22 empty] | Need to replace | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1tI9AsyDm_TH71lMyywtQMhOH0SVi0JO5 |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG016 | 2024-08-21 13:34 | chaurasiagarima97@gmail.com | Mochan Food Processors Pvt Ltd | NA | NA | NA | CXRU1026582 | SHEET KEY DEFECTIVE , SUCATION GAS SENSOR | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-21 04:01 | vinit.mewada@crystalgroup.in | MOCHAN FOOD | CXRU1026582 | 40FT | 2011 | SERVICE-AT SITE | LEASE | NA | SHEET KEY DEFECTIVE, SUCATION GAS SENSOR | NEED TO REPLACE SHEET KEY AND SUCATION GAS SENSOR | SHEET KEY AND SUCATION GAS SENSOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG016 | DAikin | LXE10E147F2 | M001597 | K31408135807 | DECOS 3F 2551 / 1 | Used | JSGA621320212 | RAMIZ |  | SHEET KEY DEFECTIVE , SUCATION GAS SENSOR | 2024-08-21 04:50 | vinit.mewada@crystalgroup.in | YES | AUG004 | 13.6.24 |  | SHIVAMRUT | AKLUJ | CXRU1032498 | SITE | FOC |  | 2025-01-15 18:34 | crm@crystalgroup.in | YES | AUG004 | NA |  |  | 2024-09-08 22:22 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:02 | 2024-08-08 |  |  |  |  | CXRU1026582 |  |  |  | Daikin | -21*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1lCfmJrFx9k7PSNvyzNo-YYUir9BSECm4 |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG017 | 2024-08-21 13:39 | chaurasiagarima97@gmail.com | VERKA AMRITSAR - PUNJAB | SANJEEV MAHAJAN | 9814615332 | INCHARGE REFRIGERATIONN | CXRU1186385 | PREMAINTANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-08-21 04:16 | vinit.mewada@crystalgroup.in | VERKA AMRITSAR | CXRU1186385 | 40FT | 2012 | SERVICE-AT SITE | LEASE | NA | PRE MAINTANCE REQUIRED | PRE MAINTAINCE | NA |  |  |  | Daikin | LXE10E136F2 | M002086 | K31505147912 | DECOS 3F 2557 / 1 | Used | JSGA622180073 | SHAHBUDDIN |  | PREMAINTANCE | 2024-08-22 03:41 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:20 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:30 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:41 | 2024-08-08 |  |  |  |  | CXRU1186385 |  |  |  | Daikin | +4*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6/180 | 9.9/9.9/9.9 | 402/401/401 | Short | PM Service | PM Service Done | No | https://drive.google.com/open?id=1puoTUtXTCUldQO_rbwaJBhPFQuse2Gll |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG001 | 2024-08-22 11:13 | vinit.mewada@crystalgroup.in | ORIENTAL YEAST SATARA | MUKUND FAWADE | 8484936735 | NA | CICU1938117 | FLUCTUATIONS IN TEMEPRATURE | UMESH |  |  | Running with issues |  |  |  | 2024-08-21 22:32 | vinit.mewada@crystalgroup.in | ORIENTAL YEAST SATARA | CICU1938117 | NA | 2021 | SERVICE-AT SITE | NA | NA | TEMPERATURE ISSUE | CHECKED AND FOUND CONTAINER RAISEDTHE TEMP -10* TO 12* . THE SET POINT IS -20* AND COMPRESSOR AT OFF -28 TO -32 *. TO SOLVE THIS ISSUE NEED TO MAINTAIN 3 TO 5 TON MIN. VOLUME. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG001 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | UMESH |  | FLUCTUATIONS IN TEMEPRATURE | 2024-08-22 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:17 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:26 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:52 | 2024-08-02 |  |  |  |  | CICU1938117 |  |  |  | Thermo king | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | 2011-11-11 | 395/395/395 | Not done | Temperature issue | Conatiner running in good condition | No | https://drive.google.com/open?id=1wfM_wKEK2zMKQ-38hUT5qjjqaDJG5PFJ |  |  | TRIP036 | No | No | Can be done on next PM | Na | NA | crm@crystalgroup.in
AUG002 | 2024-08-22 11:19 | vinit.mewada@crystalgroup.in | Mochan Food Processors Pvt Ltd | NA | NA | NA | MYRU4500552 | FLUCTUATIONS IN TEMEPRATURE | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-21 05:39 | vinit.mewada@crystalgroup.in | MOCHAN FOOD | MYRU4500552 | 40 FT | NA | SERVICE-AT SITE | LEASE | NA | TEMP NOT PULL DOWN AS DESIRE | CLEAN CONDENSER COIL WITH FREAH WATER, MANUAL DEFROST DONE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG002 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | RAMIZ |  | FLUCTUATIONS IN TEMEPRATURE | 2024-08-22 00:33 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-29 23:17 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 12:58 | 2024-08-01 |  |  |  |  | MYRU4500552 |  |  |  | Thermo king | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Done | Clean |  | 2.5/16.7 | 9.9/10.1/10.1 | 399/399/399 | Not done | Condenser coil dirty | Reefer working in good condition | No | https://drive.google.com/open?id=1Cz259VJH60hlIvZupfcR4qq47sN4aDyH |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
JUL067 | 2024-08-21 10:47 | chaurasiagarima97@gmail.com | APL Health Care | NA | NA | NA | CXRU1032327 | SENSOR DEFECTIVE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-22 00:01 | vinit.mewada@crystalgroup.in | APL HEALTHCARE | CXRU1032320 | 40 FT | 2011 | SERVICE-AT SITE | LEASE | NA | REPLACED THE SUCTION GAS SENSOR | WORKING WELL | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL067 | [7 empty] | VIRENDRA |  | SENSOR DEFECTIVE | 2024-08-22 03:29 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:00 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-08 18:09 | 2024-07-25 |  |  |  |  | CXRU1032327 |  |  |  | Daikin | +20.C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 165 KPA - 167 KPA | 10.6 A /10.5 A/10.3 | 395/393/396 | Short | We have replaced suction gas sensor, container show PTI pass and maintain temp at 20."C without any alarm | We have replaced suction gas sensor, container show PTI pass and maintain temp at 20."C without any alarm | No | https://drive.google.com/open?id=13jJx7niiUqIbVZyP3rnZ_u2RnDyhZ0et |  |  | TRIP028 | No | No | Can be done on next PM | No | NA | crm@crystalgroup.in
AUG018 | 2024-08-12 21:53 | ramiz.raja@crystalgroup.in | Reliance DC -Surat | Deepak Varma | 918962570559 | Manager | BMOU9782197 | MCB tripping during Compressor operation | Ramiz |  |  | Running with issues |  |  |  | 2024-08-29 22:09 | chaurasiagarima97@gmail.com | Qwik Supply | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR MAKING NOISE | need to switch off the unit | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG018 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | RAMIZ |  | MCB tripping during Compressor operation | 2024-08-29 23:12 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:21 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:30 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 14:05 | 2024-08-10 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Done | Need to replace |  | -45960 | 11.1/11.2/11.1 | 402/403/402 | Not done | NA | NA | Yes | https://drive.google.com/open?id=11Kd0U1CkLPo6uwz0_MwIHPBdAEMUDXxh |  |  | TRIP036 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in
AUG031 | 2024-08-14 18:34 | ramiz.raja@crystalgroup.in | Dr Reddy'S - Hyderabad | Suresh Kasem | 919908125456 | Mantanac team | TITU9930074 | Temperature Issue | Ramiz Raja |  |  | Running with issues |  |  |  | 2024-09-06 03:08 | chaurasiagarima97@gmail.com | SHIVAMRUT | TITU9930074 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | SUPPLY SENSOR GOT STUCK AND POCKET SUPPY SENSOR DEFECTIVE | NEED SPARES | Daikin EVP inlet sensor, Daikin Suction Gas Sensor |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG031 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | RAMIZ |  | Temperature Issue | 2025-01-17 19:24 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:25 | operation@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:29 | chaurasiagarima97@gmail.com | YES | AUG091 | TECHNICIAN | [5 empty] | 2025-01-18 15:30 | 2024-08-14 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1MW3ZgwQLttCnqxw6aJQTscVM01BVaA4y |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
JUL076 | 2024-08-27 13:50 | vinit.mewada@crystalgroup.in | SYMBIOTECH | NA | NA | NA | NA | NA | UMESH |  |  | Running with issues |  |  |  | 2024-08-27 01:23 | vinit.mewada@crystalgroup.in | SYMBIOTECH | NA | NA | NA | SERVICE-AT SITE | LEASE | NA | NA | NA | UMESH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL076 | [7 empty] | UMESH |  | NA | 2024-08-27 00:08 | vinit.mewada@crystalgroup.in | NO | [9 empty] | 2024-08-27 01:05 | vinit.mewada@crystalgroup.in | NO |  |  |  |  | 2024-08-27 02:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2024-09-13 05:27
AUG005 | 2024-08-29 21:26 | chaurasiagarima97@gmail.com | TEJ CONTRY YARD | Arun | 7065402353 | NA | NA | MACHINE PART COLLECTION FROM YARD | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-29 22:06 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | NA | NA | NA | NA | NEED TO COLLECT COMPRESSOR FROM NEW DELHI CARRIER TRANSPORT | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG005 | [7 empty] | SHAHBUDDIN |  | MACHINE PART COLLECTION FROM YARD | 2024-08-29 23:11 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:18 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 14:13 | 2024-08-01 |  |  |  |  | NA |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | Compressor parts collected from New delhi | Compressor parts collected from New delhi | No | https://drive.google.com/open?id=1iVwFykKlPa7Sq-gz2KBOwJg1B3riARP5 |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG020 | 2024-08-29 21:30 | chaurasiagarima97@gmail.com | Samora Stud | Balkrishna Prjapati | 7747937090 | NA | TCIU1904607 | CONTAINER NOT WORKING | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-29 22:12 | chaurasiagarima97@gmail.com | Samora Stud | TCIU1904607 | 20 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | UNIT NOT WORKING AND EVAPORATOR COIL LEAKAGE | REPLACE AND FIXED THE REEFER MAIN UIT ALIMMENTS. ALSO CHCKED GAS LEVEL. UNIT IS IN WORKING CONDIACTION | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG020 | [7 empty] | SHAHBUDDIN |  | CONTAINER NOT WORKING | 2024-08-29 23:12 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:21 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:30 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 14:33 | 2024-08-09 |  |  |  |  | TCIU1904607 |  |  |  | Daikin | NA | Dirty | Clean |  | Okay | Leakage | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/190 | 9.8/9.8/9.8 | 403/403/402 | Short | Container not working | Unit under observation | No | https://drive.google.com/open?id=1FPZZQaJbbg8aklRbk1ZJhi0DB6PJQQND |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG021 | 2024-08-29 21:32 | chaurasiagarima97@gmail.com | Qwik Supply | Shivaram | 9380924470 | NA | CICU3876626 | CONTAINER NOT WORKING | RAMIZ |  |  | Running with issues |  |  |  | 2024-08-29 22:14 | chaurasiagarima97@gmail.com | Qwik Supply | CICU3876626 | 10 FT | TK - MP4000 | SERVICE-AT SITE | LEASE | NA | Temperature Issue | CHECKED COMPRESSOR AND CONTROLLER , RESOLVED THE ISSUE AND UNIT WORKING PROPERLY | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG021 | Thermoking | Magnum + | 21K2124JT | ABC782800322110152 | ABC782900322110202 | Brand New |  | RAMIZ |  | CONTAINER NOT WORKING | 2024-08-29 23:12 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:21 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 15:49 | 2024-08-10 |  |  |  |  | CICU3876626 |  |  |  | Thermo king | -40*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Done | Clean |  | 2.5/18.3 | 11.1/11.1/11.2 | 401/400/401 | Not done | Unit stopped working | Reset the controller manually | No | https://drive.google.com/open?id=1LXqofrxmY6sffAEN52JVlehrtz5yzWbN |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG026 | 2024-08-29 21:34 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | BMOU9782197 | BREAKDOWN | UMESH |  |  | Complete Breakdown |  |  |  | 2024-08-29 22:16 | chaurasiagarima97@gmail.com | Qwik Supply | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | COMPRESSOR NOISY | NEED TO REPLACE COMPRESSOR AD GAS | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG026 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH |  | BREAKDOWN | 2024-08-29 23:13 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:22 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-15 16:29 | 2024-08-11 |  |  |  |  | BMOU9782197 |  |  |  | Daikin |  | Clean | [22 empty] | Okay | [6 empty] | Not done | NA | NA | No | https://drive.google.com/open?id=1naumHjFpvhRskblna5l9Wn3EL8NC2b5L |  |  | TRIP036 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG030 | 2024-08-29 21:44 | chaurasiagarima97@gmail.com | Andabar | NA | NA | NA | TRIU6616531 | Minor issue | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-29 22:41 | chaurasiagarima97@gmail.com | Andabar | TRIU6616531 | 10 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | MINOR ISSUE | The client reported a minor issue, which the Clima's technician addressed at the client's request. Unit operating efficiently | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG030 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Used |  | VIRENDRA |  | Minor issue | 2024-08-29 23:13 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:22 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 16:37 | 2024-08-12 |  |  |  |  | TRIU6616531 |  |  |  | Carrier | -18*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 18.09 | 11/11.5/11.3 | 415/411/413 | Not done | NA | NA | No | https://drive.google.com/open?id=1uinp47o49j1AGJFbdQR75q_QVDbgtdo- |  |  | TRIP037 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG032 | 2024-08-29 21:46 | chaurasiagarima97@gmail.com | Qwik Supply | Dipak Verma | NA | NA | BMOU9782197 | BREAKDOWN | Umesh |  |  | Complete Breakdown |  |  |  | 2024-08-29 22:48 | chaurasiagarima97@gmail.com | Qwik Supply | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Compressor leakage | SPARES REQUIRED | COMPRESSOR WITH OIL, GASLET , R134A, N2, VACUMM |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG032 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH |  | BREAKDOWN | 2024-09-09 01:19 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:59 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:31 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-15 16:32 | 2024-08-15 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | NA | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1SNx8jU32bI9P7k9cvbFGsgt3xvTxQfez |  |  | TRIP036 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG034 | 2024-08-29 21:52 | chaurasiagarima97@gmail.com | Qwik Supply | Ravi Kumar | Ravi Kumar | NA | BMOU9782197 | BREAKDOWN | UMESH |  |  | Complete Breakdown |  |  |  | 2024-08-29 22:52 | chaurasiagarima97@gmail.com | Qwik Supply | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Compressor Issue | SHPARES REQUIRED | DPRV, LSV, EXPENSION VALVE, BYPASS VALVE, COMPRESSOR OIL, GAS,VACCUM, BEAZZING SET WITH N2 |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG034 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | UMESH |  | BREAKDOWN | 2024-09-09 01:20 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:00 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-15 16:36 | 2024-08-17 |  |  |  |  | BMOU9782197 |  |  |  | Daikin |  | Clean | [22 empty] | Need to replace | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1CBRPu5GjHY90kmGC0uxaiV0rSAYhdTmd |  |  | TRIP036 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG036 | 2024-08-29 21:54 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | Suresh Kasem | 9908125456 | NA | TITU9930074 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-29 22:55 | chaurasiagarima97@gmail.com | DR REDDY FTO 07 | TITU9930074 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Temperature Issue | Clean and restored the sensor port and unit is working normal | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG036 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | SHAHBUDDIN |  | FLUCTUATIONS IN TEMEPRATURE | 2024-08-29 23:14 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:23 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 16:50 | 2024-08-19 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 / 18 | 9.9/9.8/9.8 | 406/405/405 | Short | TEMPERATURE ISSUE | NA | No | https://drive.google.com/open?id=11tTgjTq02-i4I_QEKYsXkUGRTyFrCmUZ |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG038 | 2024-08-29 21:56 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | NA | NA | NA | PCIU6025808 | BREAKDOWN | VIRENDRA |  |  | Complete Breakdown |  |  |  | 2024-08-29 23:02 | chaurasiagarima97@gmail.com | DR REDDY FTO 07 | PCIU6025808 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Condensor coil dirty | Condenser coil clean with fresh water. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG038 | Daikin | Daikin | A950890 | LXE10EA36B | NA | Used | JSGA622340507 | VIRENDRA |  | BREAKDOWN | 2024-08-29 23:14 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:23 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 16:56 | 2024-08-21 |  |  |  |  | PCIU6025808 |  |  |  | Daikin | +20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 82KPA/1039KPA | 9/8.9/8.7 | 404/401/403 | Not done | CONDESER COIL DIRTY | CONDENSER RUNNING IN GOOD CONDITION | No | https://drive.google.com/open?id=1K3sR7eBNimTPkVrBo8_3o1KBH31EVFvp |  |  | TRIP037 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG039 | 2024-08-29 21:58 | chaurasiagarima97@gmail.com | DIVIS LAB | NA | NA | NA | CON 1 | container shown alarm | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-08-29 23:04 | chaurasiagarima97@gmail.com | DIVIS LAB | CON 1 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | container shown alarm DEL 70 | Need PM service and compressor defective | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG039 | [7 empty] | SHAHBUDDIN |  | container shown alarm | 2024-08-29 23:14 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:23 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 17:00 | 2024-08-21 |  |  |  |  | CONT-1 |  |  |  | Carrier | +19.9*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6/185 | 12.9/12.9/13 | 408/408/408 | Short | NA | NA | No | https://drive.google.com/open?id=1HRtgaby5TE0go3PKfkdMS45UvefbMWgl |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG040 | 2024-08-29 22:01 | chaurasiagarima97@gmail.com | Qwik Supply | G MISHRA | 9875242261 | NA | BMOU9782197 | BREAKDOWN | MUKESH |  |  | Complete Breakdown |  |  |  | 2024-08-29 23:08 | chaurasiagarima97@gmail.com | Qwik Supply | BMOU9782197 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Temperature Issue | NEED TO SET VOLTAGE ISSUE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG040 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | MUKESH |  | BREAKDOWN | 2024-08-29 23:15 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-08-29 23:24 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-08-29 23:33 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-15 16:39 | 2024-08-25 |  |  |  |  | BMOU9782197 |  |  |  | Daikin |  | Clean | [22 empty] | Need to replace | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1dCeRmPbf_Zc7iWJ3PThoTbmozNrqKVK9 |  |  | TRIP039 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG050 | 2024-08-31 02:10 | chaurasiagarima97@gmail.com | Kirloskar Corrocoat | SIWAM TIWARI | 7000978917 | NA | NYKU7931452 | CONTAINER NOT WORKING | VIRENDRA |  |  | Running with issues |  |  |  | 2024-08-31 02:13 | chaurasiagarima97@gmail.com | KRIOSKAR | NYKU7931452 | NA | NA | SERVICE-ON CALL | LEASE | NA | CONTAINER NOT WORKING | ERROR - AA22 SHOWING DUE TO R/S EVP MOTOR DEFECTIVE, NEED TO REPLACE | EVP MOTOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG050 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | VIRENDRA |  | CONTAINER NOT WORKING | 2025-01-17 19:24 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:25 | operation@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:43 | chaurasiagarima97@gmail.com | YES | AUG094 | TECHNICIAN | [5 empty] | 2025-01-16 16:24
AUG019 | 2024-09-01 23:38 | chaurasiagarima97@gmail.com | Earl Corvus Habitat | NA | NA | NA | APRU5091606 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 02:17 | chaurasiagarima97@gmail.com | Earl Corvus Habitat | APRU5091606 | 40 FT | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | NA | FLUCTUATIONS IN TEMEPRATURE | NEED TO REPLACE SYSTEM EVAPRATOR COIL, REFILL THE GAS R 134 A, N2, VACCUM PUMPS. | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG019 | Carrier - Thinline | Thinline | NA | NA |  | Used |  | VIRENDRA | No | FLUCTUATIONS IN TEMEPRATURE | 2024-09-09 01:16 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2025-01-15 18:35 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:22 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11 | 2024-08-10 |  |  |  |  | APRU5091606 |  |  |  | Carrier | 0*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=18jhTtkQGmaUFGY6LDauq70vuDr0oZyyz |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG022 | 2024-09-01 23:41 | chaurasiagarima97@gmail.com | ITC Ltd | NA | NA | NA | PCIU6010243 | ALARM CODE VISIBLE, AL F803 | UMESH |  |  | Running with issues |  |  |  | 2025-01-18 17:35 | crm@crystalgroup.in | ITC Ltd | PCIU6010243 | 40FT | Thermo King | SERVICE-ON CALL | LEASE | FOC | Showing Alarm F803 | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG022 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | UMESH |  | ALARM CODE VISIBLE, AL F803 | 2024-09-06 04:57 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2025-01-18 17:47 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 22:23 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-18 18:17 | 2024-08-09 |  |  |  |  | PCIU6010243 |  |  |  | Daikin | -18*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=139axKxp9UAGS1mvsGAHj7l5t0dhYQElp |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG023 | 2024-09-01 23:46 | chaurasiagarima97@gmail.com | Crystal | NA | NA | NA | GESU9469328 | SERVICES | VIRENDRA |  |  | Running with issues |  |  |  | 2024-09-06 02:31 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9469328 | 40 FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | DISPLAY ISSUE | NEED TO REPLACE THE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG023 | Carrier - Thinline | Elite line |  |  |  | Used |  | VIRENDRA |  | SERVICES | 2024-09-09 01:16 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:07 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:24 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 17:42 | 2024-08-09 |  |  |  |  | GESU9469328 |  |  |  | Carrier | -18*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2/19.7 | 9.9/9.7/9.5 | 420/419/417 | Full | NA | NA | Yes | https://drive.google.com/open?id=1mXf4cjgrZHgE4HaDuBko4QphCJ-RTAUz |  |  | NA | Yes | Yes | Urgent | Installation Display | Display | crm@crystalgroup.in
AUG024 | 2024-09-01 23:48 | chaurasiagarima97@gmail.com | Crystal | NA | NA | NA | GESU9379498 | SERVICES | UMESH |  |  | Running with issues |  |  |  | 2024-09-06 02:36 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9379498 | 40 FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | container controller defective, No gas in system, Solonerd Coil defected, Power Cable short | NEED SPARES | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG024 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH |  | SERVICES | 2024-09-09 01:17 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:09 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:25 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 17:49 | 2024-08-09 |  |  |  |  | GESU9379498 |  |  |  | Carrier | -18*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | Need to install controller first | Need to install controller first | Yes | https://drive.google.com/open?id=14Wp6keCiXS9cJzgW-tSTgLwO2dHMxruj |  |  | NA | Yes | Yes | Urgent | Installation controller | Controller | crm@crystalgroup.in
AUG025 | 2024-09-01 23:51 | chaurasiagarima97@gmail.com | Cipla | NA | NA | NA | CXRU1033787 | SERVICES | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 02:41 | chaurasiagarima97@gmail.com | Cipla Unit 1 | CXRU1033787 | 40FT | CARRIER-ELITLINE | SERVICE-AT SITE | LEASE | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG025 | DAikin | LXE10E147F2 | M001107 | K31412141829 | DECOS 3F 2557 / 1 | used | JSGA622340249 | MUKESH |  | SERVICES | 2024-09-09 01:17 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:10 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:25 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG027 | 2024-09-02 00:02 | chaurasiagarima97@gmail.com | Qwik Supply | RANVIK SINGH | 9872609126 | NA | TCLU1130265 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 02:44 | chaurasiagarima97@gmail.com | Qwik Supply | TCLU1130265 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | FOUND ICE ON EVAPROTOTER COIL ,EXSP. COIL SENSOR ANDREALY BOARD SUSPECTED. | WHILE PHYSICAL INSPECTION HE SUGGESTED NEED TO REPLACE THE SENSOR. UNIT WORKING WELL | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG027 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN |  | FLUCTUATIONS IN TEMEPRATURE | 2024-09-09 01:18 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:56 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:26 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-11 18:18 | 2024-08-16 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | -20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Not done | Clean |  | 2/16.5 | 10.1/10/10.1 | 401/401/401 | Not done | Found ice on evp coil , return sensor defective | Reefer unit running in good condition | Yes | https://drive.google.com/open?id=1OMzIv1cKCblSn5UobP3pQsSj30PGIL47 |  |  | TRIP038 | Yes | Yes | Urgent | Installation of Evp coil sensor , Return sensor | Evp coil sensor Return sensor | crm@crystalgroup.in
AUG028 | 2024-09-06 00:18 | chaurasiagarima97@gmail.com | Dr Reddy Biotechnology | V SADUPVALAM | 9550002448 | NA | TITU9930114 | PREVENTIVE MAINTENANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-09-06 02:58 | chaurasiagarima97@gmail.com | Dr Reddy Biotechnology | TITU9930114 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | PM SERVICES AD INTERNAL INSPECTION | INSPECTION DONE AND RESOLVE THE ISSUE OF BLUESTAR UNIT 2 AFTER CLEANING CONDENSOR COIL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG028 | Thermoking | MP-4000 | 14E219055 | EOG1000667 |  |  | JSGA622180063 ¦ JSGA622180011 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-09-09 01:18 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:56 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-13 10:20 | 2024-08-29 |  |  |  |  | TITU9930114 |  |  |  | Thermo king | -28*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.8/0.4 and Discharge 200/190 | 9.9/9.8/9.9 9.8/9.6/9.7 | 397/396/397 | Short | PM service and internal inspection | NA | No | https://drive.google.com/open?id=1-tKVZWI4Bcjw9a9NQ8HhlXU_7cIlXrX5 |  |  | TRIP038 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG029 | 2024-09-06 00:32 | chaurasiagarima97@gmail.com | Crystal JNPT | NA | NA | NA | GESU9379498 | CONTAINER NOT WORKING | UMESH |  |  | Running with issues |  |  |  | 2024-09-06 03:03 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | GESU9379498 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | CONTAINER NOT WORKING | NEED SPARES | Daikin Keypad, Daikin Display, Liquid Filter, Refrigerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG029 | Carrier-Primeline | Elite line | S3617R013P1 | 69NT40551506 |  | Used |  | UMESH |  | CONTAINER NOT WORKING | 2024-09-09 01:19 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 00:57 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 22:27 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-13 10:29 | 2024-08-10 |  |  |  |  | GESU9379498 |  |  |  | Carrier | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | NA | NA | Yes | https://drive.google.com/open?id=1GBBKsHEP9FqKIjp6j_RRWE2K5JB-dOe_ |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG033 | 2024-09-06 00:35 | chaurasiagarima97@gmail.com | Chemplast Sanmar Limited | Mohan | 7904271114 | NA | TITU9930222 | COMPRESSOR TRIPPED | RAMIZ |  |  | Running with issues |  |  |  | 2024-09-06 03:11 | chaurasiagarima97@gmail.com | Chemplast Sanmar Limited | TITU9930222 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | Compressor Defective | SPARES REQUIRED | Daikin Inlet Sensor, Liquid Filter, Daikin Return Temperature Sensor, Refrigerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG033 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | RAMIZ |  | COMPRESSOR TRIPPED | 2025-01-17 19:26 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:32 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-18 15:51 | 2024-08-16 |  |  |  |  | TITU9930222 |  |  |  | Thermo king |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1B7uLkVhlWyNVbI9WCC5aHd_hPaSWX6Kg |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG035 | 2024-09-06 00:37 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | PCIU6015055 | COMPRESSOR MAKING NOISE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 03:15 | chaurasiagarima97@gmail.com | Qwik Supply | PCIU6015055 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | NEED COMPRESSURE , FILTER, GAS KET , GAS - N32 , R134A AND VACCUM PUMP | SPARES REQUIRED | Daikin Inlet Sensor, Refirgerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG035 | Daikin | Daikin | NA | NA | NA | used |  | SHAHBUDDIN |  | COMPRESSOR MAKING NOISE | 2025-01-15 13:08 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:23 | crm@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:33 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:16 | 2024-08-17 |  |  |  |  | PCIU6015055 |  |  |  | Daikin | -30* C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=10ZTXg2fh46ungwZLW0sabj5p5Vfd97ll |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
AUG037 | 2024-09-06 00:39 | chaurasiagarima97@gmail.com | DR REDDY CTO 06 | NA | NA | NA | KKFU6712802 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 03:18 | chaurasiagarima97@gmail.com | Dr Reddy CTO 6 | KKFU6712802 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | FLUCTUATIONS IN TEMEPRATURE | NEED FUSE | Carrier Keypad, USB RS232 ADAPTOR WITH CASE & SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG037 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | SHAHBUDDIN |  | FLUCTUATIONS IN TEMEPRATURE | 2025-01-17 19:26 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:34 | chaurasiagarima97@gmail.com | YES | AUG086 | COURIER | [5 empty] | 2025-01-16 16:11
AUG041 | 2024-09-06 00:41 | chaurasiagarima97@gmail.com | Laurus Unit 3 | NA | NA | NA | APRU5091340 | COMPRESSOR TRIPPED | VIRENDRA |  |  | Running with issues |  |  |  | 2024-09-06 03:44 | chaurasiagarima97@gmail.com | Laurus Unit 3 | APRU5091340 | 40 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | COMPRESSOR DEFECTIVE | NEED TO REPLACED COMPRESSOR | USB RS232 ADAPTOR WITH CASE & SOFTWARE |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG041 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA |  | COMPRESSOR TRIPPED | 2024-09-09 01:21 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:01 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:36 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-13 12:10 | 2024-08-25 |  |  |  |  | APRU5091340 |  |  |  | Carrier |  | Dirty | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Need to replace |  |  |  | Okay | Not done | Need to replace |  |  | 9.8/9.7/9.5 | 403/401/404 | Not done | NA | Compressor need to replace , Supply sensor need to replace | Yes | https://drive.google.com/open?id=1Jlk1b2uRpOiy491-P7bRGFwVYIotFVr2 |  |  | TRIP037 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in
AUG042 | 2024-09-06 00:43 | chaurasiagarima97@gmail.com | CIPLA UNIT 1 | Kiran Nair | 9146012093 | NA | TITU9230980 | KEYPAD NOT WORKING | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 03:48 | chaurasiagarima97@gmail.com | Cipla Unit 1 | TITU9230980 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | KEYPAD NOT WORKING | NEED SPARES | Refirgerant Gas - R134a, Brazing Set, Liquid Filter, GAUGE MANIFOLD & ADAPTOR, Daikin Inlet Sensor, Daikin Compressor Contactor 30A (PCC1-PCC2) |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG042 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | MUKESH |  | KEYPAD NOT WORKING | 2024-09-09 01:21 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:08 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG043 | 2024-09-06 00:45 | chaurasiagarima97@gmail.com | North West logistic | Eknath Khandelvilkar | 9763487755 | NA | MYRU4505847 | FLUCTUATIONS IN TEMEPRATURE | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 03:51 | chaurasiagarima97@gmail.com | North West logistic | MYRU4505847 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | ERROR FOUND AL E401, IN SUPPY SENSOR , HPT SESOR , SHEET KEY AND GAS REPLACEMENT | RETURN BACK TO US AFTER WARD WE WORK ON IT. | TK-4000 COMPRESSOR CONTACTOR |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG043 | Daikin | Daikin |  |  |  | Used |  | MUKESH |  | FLUCTUATIONS IN TEMEPRATURE | 2024-09-09 01:21 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:09 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG044 | 2024-09-06 00:46 | chaurasiagarima97@gmail.com | North West logistic | Eknath Khandelvilkar | 9763487755 | NA | TITU9928040 | KEYPAD NOT WORKING | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 03:56 | chaurasiagarima97@gmail.com | North West logistic | TITU9928040 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | KEYPAD DEFECTIVE | RETURN BACK TO US AFTER WARD WE WORK ON IT. | Daikin Reefer Unit, Packing, Transport |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG044 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | MUKESH |  | KEYPAD NOT WORKING | 2024-09-09 01:22 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:09 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:37 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG045 | 2024-09-06 00:47 | chaurasiagarima97@gmail.com | North West logistic | Eknath Khandelvilkar | 9763487755 | NA | MYRU4513729 | FLUCTUATIONS IN TEMEPRATURE | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 03:58 | chaurasiagarima97@gmail.com | North West logistic | MYRU4513729 | 10 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | ERROR FOUND AL E401, IN SUPPY SENSOR , HPT SESOR , SHEET KEY AND GAS REPLACEMENT | NEED TO REFILL Refirgerant Gas - R134a | Refirgerant Gas - R134a |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG045 | Daikin | Daikin |  |  |  | Refurbished |  | MUKESH |  | FLUCTUATIONS IN TEMEPRATURE | 2024-09-09 01:22 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:10 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:38 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG046 | 2024-09-06 00:50 | chaurasiagarima97@gmail.com | North West logistic | Eknath Khandelvilkar | NA | NA | MYRU4515188 | PREVENTIVE MAINTENANCE | MUKESH |  |  | Preventive Maintenance |  |  |  | 2024-09-06 04:00 | chaurasiagarima97@gmail.com | North West logistic | MYRU4515188 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | PM SERVICES | NEED SPARES | Refirgerant Gas - R134a, MAK Process Oil - RL32H - Emkarte |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG046 | Daikin | Daikin |  |  |  | Used |  | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-09-09 01:23 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:10 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:38 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG047 | 2024-09-06 00:52 | chaurasiagarima97@gmail.com | CIPLA UNIT 1 | NA | NA | NA | TITU9231009 | DISPLAY NOT VISIBLE | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 04:04 | chaurasiagarima97@gmail.com | Cipla Unit 1 | TITU9231009 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | DISPLAY ISSUE | Spare Required | Display, Keypad, Carrier Thinline Ambient Sensor, Carrier Supply Sensor, Carrier Compressor Contactor 30A, Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG047 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | MUKESH |  | DISPLAY NOT VISIBLE | 2024-12-31 17:53 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:53 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:40 | chaurasiagarima97@gmail.com | YES | AUG092 | COURIER | [5 empty] | 2025-01-14 15:40 | 2024-08-28 |  |  |  |  | TITU9231009 |  |  |  | Daikin | 4.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=14y3NkDg_1T0kxQq24_o0UcCD4iE7y4Y_ |  |  | NA | Yes | Yes | Urgent | Display installation | Sheet key Daikin Display 1.5kg gas R134a | crm@crystalgroup.in
AUG048 | 2024-09-06 00:53 | chaurasiagarima97@gmail.com | CIPLA UNIT 1 | NA | NA | NA | CXRU1033344 | FLUCTUATIONS IN TEMEPRATURE | MUKESH |  |  | Running with issues |  |  |  | 2024-09-06 04:07 | chaurasiagarima97@gmail.com | Cipla Unit 1 | CXRU1033344 | NA | DAIKIN | SERVICE-AT SITE | LEASE | NA | SUPPLY TEMP SENSOR DEFECTED | NEED TO REPLACE TEMP SUPPLY SENSOR | Daikin Display, Liquid Filter, LED Light 20W, Curtain set for 40ft [Model - Frigus], L&T MCB 16 AMP X 2P, Polycab Flexible Cable 1.5 sq mm X 2 Core, Insulation Tape, RIVIT, CABLE TIE, 12INCH BLACK, RIVIT GUN, Drill Machine, CASING PATTI 1 INCH |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG048 | DAikin | LXE10E147F2 | M001118 | K31411114078 | DECOS 3F 2609 / 1 | Used | JSGA622340264 | MUKESH |  | FLUCTUATIONS IN TEMEPRATURE | 2024-12-31 17:53 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:54 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:41 | chaurasiagarima97@gmail.com | YES | AUG093 | COURIER | [5 empty] | 2025-01-14 15:02 | 2024-08-28 |  |  |  |  | CXRU1033344 |  |  |  | Daikin | NA | Clean | [22 empty] | Okay | [6 empty] | Short | Need to replace supply sensor | NA | Yes | https://drive.google.com/open?id=1U0qZluf47VTgCYgBI8JDWhl-D3x0fU5I |  |  | NA | Yes | Yes | Can be done on next PM | Installation Supply Sensor 1 | Supply Sensor 1 | crm@crystalgroup.in
AUG049 | 2024-09-06 00:55 | chaurasiagarima97@gmail.com | DIVIS LAB | NA | NA | NA | CONT 2 | COMPRESSOR TRIPPED | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 04:10 | chaurasiagarima97@gmail.com | Divis Lab | CONT-3 | NA | NA | SERVICE-AT SITE | LEASE | NA | COMPRESSOR TRIPPED | NEED TO REPLACE COMPRESSOR AND FILTER, NET BOLT | Carrier Supply Sensor |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG049 | [7 empty] | SHAHBUDDIN |  | COMPRESSOR TRIPPED | 2024-09-09 01:24 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:12 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:42 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:24 | 2024-08-30 |  |  |  |  | CONT 2 | [5 empty] | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1i9JBVqPOKfCosE83ovvRkDklgOwVL-5d |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
AUG051 | 2024-09-06 00:58 | chaurasiagarima97@gmail.com | Crystal JNPT | NA | NA | NA | CRLU6220410 | PREVENTIVE MAINTENANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-09-06 04:16 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | CRLU6220410 | 40FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | NEED TO REPLACE BOTH DOOR GASLET | NEED TO REPLACE BOTH DOOR GASLET | Carrier Supply Sensor, Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG051 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA622170434 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-12-31 17:54 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:54 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-09-08 23:44 | chaurasiagarima97@gmail.com | YES | AUG096 | COURIER | [5 empty] | 2025-01-14 14:50 | 2024-08-31 |  |  |  |  | CRLU6220410 |  |  |  | Carrier | -18*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1j3prgT1jxXacEjAHKvTabI91FR9PreV4 |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
AUG052 | 2024-09-06 00:59 | chaurasiagarima97@gmail.com | Crystal JNPT | NA | NA | NA | MYRU4500552 | PREVENTIVE MAINTENANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-09-06 04:19 | chaurasiagarima97@gmail.com | Crystal Yard-JNPT | MYRU4500552 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | NEED TO REPLACE SUPPLY SENSOR , ABINENT SESOR, CONDENSOR SENSOR,EVP SENSOR | Spare Required | Liquid Filter |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG052 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-09-09 01:25 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:12 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:45 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG053 | 2024-09-06 01:01 | chaurasiagarima97@gmail.com | DSV LOGISTIC | ARUN | 9014414441 | NA | TITU9930006 | INSTALLATION | SHAHABUDDIN |  |  | Installation |  |  |  | 2024-09-06 04:22 | chaurasiagarima97@gmail.com | DSV | TITU9930006 | 40 FT | TK-MP3000 | SERVICE-AT SITE | LEASE | NA | DIX40 TK MP4000 FOR INSTATTION , INTERNAL LIGHT NOT WORKING AND NEED TO INSTALL EXTERNAL LIGHTS | SPARES REQUIRED | Daikin HSV-DSV-BSV Solenoid Valve, MAK Process Oil - RL32H - Emkarte, Compressor Gasket - Suction & Discharge, Liquid Filter, Daikin Compressor Contactor 30A (PCC1-PCC2) Refirgerant Gas - R134a, Nitrogen, Oxygen, Brazing Set, Brazing Rod, Daikin Inlet Sensor, Daikin Return Temperature Sensor, Vaccume Pump |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG053 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | SHAHBUDDIN |  | INSTALLATION | 2024-09-09 01:26 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:13 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:45 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-16 16:11
AUG054 | 2024-09-06 01:03 | chaurasiagarima97@gmail.com | DSV LOGISTIC | Ramesh | 7799437098 | NA | SJKU4000104 | INSTALLATION | SHAHABUDDIN |  |  | Installation |  |  |  | 2024-09-06 04:26 | chaurasiagarima97@gmail.com | DSV | SJKU4000104 | 40 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | DIX40 TK MP4000 FOR INSTATTION, | AC INSTATTALLATION DONE WORKING WELL | Daikin LSV Coil, Daikin HSV-DSV-BSV Solenoid Valve, Daikin Expansion Valve, Daikin Compressor, Compressor Gasket - Suction & Discharge, Refirgerant Gas - R134a, Nitrogen Oxygen, Brazing Set, Brazing Rod, Vacuum Pump |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG054 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN |  | INSTALLATION | 2024-09-09 01:27 | chaurasiagarima97@gmail.com | NO | [9 empty] | 2024-09-09 01:13 | chaurasiagarima97@gmail.com | NO |  |  |  |  | 2024-09-08 23:46 | chaurasiagarima97@gmail.com | NO | [7 empty] | 2025-01-14 12:50 | 2024-08-31 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | =2*C | Clean | [22 empty] | Okay | [6 empty] | Short | NA | NA | No | https://drive.google.com/open?id=1u_wwahHdwvFrigU4kM4zmBR5zSc8z3Za |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
SEP001 | 2024-09-06 01:05 | chaurasiagarima97@gmail.com | Qwik Supply | SATISH | 9182561382 | NA | CGHU2988654 | CONTAINER INSPECTION | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 04:29 | chaurasiagarima97@gmail.com | Qwik Supply | CGHU2988654 | 20 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | WATER ENTERED IN ELECTRICAL PANEL, ENTERNAL LIGHT DAAMAGED , EVAPROTER MOTOR NOISY, MAIN POWER CABLE DAAMAGED WITH POWER PLUGIN , | DUE TO HEAVY RAIN NOT ABLE TO DO TEST. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP001 | [7 empty] | NA | No | CONTAINER INSPECTION | 2024-10-03 03:30 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:55 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:51 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-14 12:08 | 2024-09-01 |  |  |  |  | CGHU2988654 |  |  |  | Carrier |  | Dirty | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | [6 empty] | Not done | NA | NA | Yes | https://drive.google.com/open?id=1XUrQMzH8-iY4xwNLBWaiKREib48ooi4G |  |  | NA | Yes | Yes | Can be done on next PM | NA | NA | crm@crystalgroup.in
SEP002 | 2024-09-06 01:06 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | CGHU2989060 | CONTAINER INSPECTION | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 04:31 | chaurasiagarima97@gmail.com | Qwik Supply | CGHU2989060 | 20 FT | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | NA | UNIT UNABLE TO RUN DUE TO HEAVY RAINFALL.INTERNAL LIGHT DAMAGED,MAIN POWER PLUGIN AND CABLE IS DAMAGED AND RUSTY, | DUE TO HEAVY RAIN NOT ABLEE TO DO TEST. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP002 | [7 empty] | NA | No | CONTAINER INSPECTION | 2024-10-03 03:30 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:56 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:52 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-14 12:24 | 2024-09-01 |  |  |  |  | CGHU2989060 |  |  |  | Carrier | NA | Dirty | Clean |  | Okay |  | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Damaged |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1Bn0Bmu8iyqpC2PHs6vIGnlyhOyyrxPhk |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in
SEP003 | 2024-09-06 01:07 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | Manoj kumar | 8008097255 | NA | MYRU4517508 | SITE INSPECTION | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 04:32 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | MYRU4517508 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | NA | Need replace Daikin keypad, display & display cover, CPU guard cover, internal cleaning,, lights , need togaslet fixed kick plate / baffle plates is damaged, door , PTI failed | SPARES REQUIRED | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP003 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | SHAHBUDDIN | No | SITE INSPECTION | 2024-10-03 03:57 | operation@crystalgroup.in | YES | SEP001 | 7.9.24 | Spares, FOC | TIANISH | VIZAG | MYRU4517508 | SITE | FOC | DAIKIN | 2024-12-31 17:57 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:53 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-14 15:25 | 2024-09-02 |  |  |  |  | MYRU4517508 |  |  |  | Daikin | +19*C | Clean | [22 empty] | Okay | [6 empty] | Short | NA | NA | No | https://drive.google.com/open?id=1diPRVTkZijKxZFBo6tAHyynbkspPLRQk |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
SEP004 | 2024-09-06 01:09 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | NA | NA | NA | CGMU2990461 | SITE INSPECTION | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-09-06 04:34 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | CGMU2990461 | 20 FT | TK-MP4000 | SERVICE-AT SITE | LEASE | NA | PM services / Inspection / PTI | PM service done, convertor coil clean, Air pressure, sensor reading, gas level , Oil test, leakage test done. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP004 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | SHAHBUDDIN | No | SITE INSPECTION | 2024-10-03 04:20 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:57 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:54 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-14 12:32 | 2024-09-02 |  |  |  |  | CGMU2990461 |  |  |  | Carrier | -20*C | Clean | [22 empty] | Okay | [6 empty] | Not done | NA | NA | Yes | https://drive.google.com/open?id=1iZeMoargGAxGf9WDz5GAmFKPIc6hqZZT |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in
SEP015 | 2024-09-11 02:55 | sushma.poojari@crystalgroup.in | Tan90 Pune | Shamboo | 89258 46277 | Site incharge | CICU3876523 | PCM pads blasting issue | Sushma |  |  | Running with issues |  |  |  | 2024-10-02 23:57 | operation@crystalgroup.in | Tan90 | CICU3876523 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | NOT ACHEIVING TEMP | REARRANGE THE CARGO AND DEFROST SETTING CHANGE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No | PCM pads blasting issue | 2024-10-03 04:52 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:12 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:31 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 16:38 | 2024-09-11 |  |  |  |  | CICU3876523 |  |  |  | Thermo king | -40*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1UK7HJ05FyBsvUYN-NUeY-xtf94YZW0o3 |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP005 | 2024-09-11 21:17 | chaurasiagarima97@gmail.com | Shivamrut | NA | NA | NA | CXRU1030854 | BREAKDOWN | SHAHABUDDIN |  |  | Complete Breakdown |  |  |  | 2024-10-02 23:25 | operation@crystalgroup.in | Shivamrut | CXRU1030854 | NA | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | LEAK IN CONTAINER | CUSTOMER WILL ARRANGE CONSUMABLES | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP005 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | Mukesh |  | BREAKDOWN | 2024-10-03 04:24 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-13 11:57 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-13 11:57 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-14 12:39 | 2024-09-01 |  |  |  |  | CXRU1030854 |  |  |  | Daikin | -15*C | Clean | [22 empty] | Okay | [6 empty] | Not done | NA | NA | Yes | https://drive.google.com/open?id=1QCRS_vmXB8aV9PAFTdsF3lwbl8mTWruy |  |  | NA | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in
SEP006 | 2024-09-11 21:19 | chaurasiagarima97@gmail.com | Dr Reddy CTO5 | NA | NA | NA | GSOU6384153 | CONTAINER NOT WORKING | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-02 23:28 | operation@crystalgroup.in | Dr Reddy CTO5 | GSOU6384153 | NA | NA | SERVICE-AT SITE | LEASE | FOC | EVP MOTOR NOISY | NEED TO REPLACED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP006 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN | Yes | CONTAINER NOT WORKING | 2024-10-03 04:25 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:21 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:32 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 17:14 | 2024-09-03 |  |  |  |  | GSOU6384153 | [5 empty] | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1bwc6qfQGnjseu1gPIll3r3WXQaq-1anV |  |  | TRIP041 | Yes | Yes | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP007 | 2024-09-11 21:21 | chaurasiagarima97@gmail.com | Dr Reddy CTO5 | NA | NA | NA | CXRU1045896 | PREVENTIVE MAINTENANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-10-02 23:30 | operation@crystalgroup.in | Dr Reddy CTO5 | CXRU1045896 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP007 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:26 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:21 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:32 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 17:23 | 2024-09-03 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | +4*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1kCLZCn19ywxDI3uffU9PyLJMhCQT3Mwl |  |  | TRIP041 | No | No | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP008 | 2024-09-11 21:22 | chaurasiagarima97@gmail.com | Dr Reddy CTO5 | NA | NA | NA | GSOU6384240 | PREVENTIVE MAINTENANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-10-02 23:33 | operation@crystalgroup.in | Dr Reddy CTO5 | Dr Reddy CTO5 | GSOU6384240 | NA | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP008 | [7 empty] | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:26 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:20 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 18:17 | 2024-09-03 |  |  |  |  | GSOU6384240 |  |  |  |  | +20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1tyxIdjIrGUj7H6qCICjZCd5vuI5WPzcv |  |  | SEP008 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP009 | 2024-09-11 21:23 | chaurasiagarima97@gmail.com | Dr Reddy CTO5 | NA | NA | NA | CXRU1032564 | PREVENTIVE MAINTENANCE | SHAHABUDDIN |  |  | Preventive Maintenance |  |  |  | 2024-10-02 23:35 | operation@crystalgroup.in | Dr Reddy CTO5 | CXRU1032564 | CXRU1032564 | NA | SERVICE-AT SITE | LEASE | FOC | condensor coil dirty | condensor coil clean with fresh water. | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP009 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:26 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:19 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 18:22 | 2024-02-03 |  |  |  |  | CXRU1032564 |  |  |  | Daikin | +20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1JxGMjB5CEDztqR9xEAHiFDHfML2UHNbp |  |  | TRIP041 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP010 | 2024-09-11 21:24 | chaurasiagarima97@gmail.com | GMR Hydrabad Air cargo | NA | NA | NA | SJKU4000104 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-02 23:38 | operation@crystalgroup.in | DSV | SJKU4000104 | NA | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | POWER MODULE DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP010 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN | Yes | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 04:39 | operation@crystalgroup.in | YES | SEP002 | 9.9.24 | Spares, FOC | DSV Air & Sea Pvt. Ltd. | HYDERABAD | SJKU4000104 | SITE | FOC | TK-MP4000 | 2025-01-15 18:19 | crm@crystalgroup.in | YES | SEP002 | NA |  |  | 2025-01-18 11:04 | crm@crystalgroup.in | YES | SEP002 | NA | [5 empty] | 2025-01-18 11:14 | 2024-09-04 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | +2*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1mzm4GWhD0IXbj0UGzcZ7xe0eV9OrKbcC |  |  | TRIP041 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP011 | 2024-09-11 21:26 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | NA | NA | NA | CXRU1033616 | COMPRESSOR MAKING NOISE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-02 23:49 | operation@crystalgroup.in | Dr Reddy FTO-7 | CXRU1033616 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | INLET SENSOR DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP011 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | VIRENDRA | Yes | COMPRESSOR MAKING NOISE | 2024-10-03 04:43 | operation@crystalgroup.in | YES | SEP081 | 20.9.24 | Spares, FOC | DR REDDY | VIZAG | CXRU1033616 | SITE | FOC | DAIKIN | 2025-01-15 18:18 | crm@crystalgroup.in | YES | SEP081 | NA |  |  | 2025-01-18 11:05 | crm@crystalgroup.in | YES | SEP081 | NA | [5 empty] | 2025-01-18 12:13 | 2024-09-06 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | +3*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1rpYPQe8lm-6p9URVzC9sQFFLzBM-XyFu |  |  | TRIP044 | Yes | Yes | Can be done on next PM | Installation Inlet sensor | Inlet sensor | crm@crystalgroup.in | REEFER
SEP012 | 2024-09-11 21:29 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | NA | NA | NA | KKFU6712802 | PREVENTIVE MAINTENANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-10-02 23:50 | operation@crystalgroup.in | Dr Reddy FTO-7 | KKFU6712802 | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | MOTOR NOISY | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP012 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:45 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:17 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:59 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 18:27 | 2024-09-06 |  |  |  |  | KKFU6712802 |  |  |  | Carrier | +4.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1umTh0XGNckZO8SdIGSuLkzOKNlYNgHQ7 |  |  | TRIP044 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP013 | 2024-09-11 21:30 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | NA | NA | NA | TRIU6632949 | SERVICES | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-02 23:52 | operation@crystalgroup.in | Dr Reddy FTO-7 | TRIU6632949 | NA | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | KING VALVE, KEYPAD & LEAK FOUND | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP013 | Carrier - Thinline | Thinline | 1808L295 | MS60317785 |  | Used |  | VIRENDRA | Yes | SERVICES | 2024-10-03 04:49 | operation@crystalgroup.in | YES | SEP082 | 20.9.24 | Consumables, Spares, FOC | DR REDDY | VIZAG | TRIU6632949 | SITE | FOC | CARRIER-THINLINE | 2025-01-15 18:15 | crm@crystalgroup.in | YES | SEP082 | NA |  |  | 2025-01-18 11:06 | crm@crystalgroup.in | YES | SEP082 | NA | [5 empty] | 2025-01-18 12:47 | 2024-09-06 |  |  |  |  | TRIU6632949 |  |  |  | Carrier | +3*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1909cU63jX-l1BhlmvR3QtdaG57vNz9v2 |  |  | TRIP044 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP014 | 2024-09-11 21:32 | chaurasiagarima97@gmail.com | DR REDDY FTO 7 | NA | NA | NA | TITU9930074 | FLUCTUATIONS IN TEMEPRATURE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-02 23:54 | operation@crystalgroup.in | Dr Reddy FTO-7 | TITU9930074 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | COMP CONTACTOR REQ | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP014 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 04:51 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:12 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:59 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 18:32 | 2024-09-08 |  |  |  |  | TITU9930074 |  |  |  | Thermo king |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1iynOZrh4l31G17fkibwkk4GPnG78zbkO |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP015 | 2024-09-11 22:09 | chaurasiagarima97@gmail.com | T 90 | NA | NA | NA | CICU3876523 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-02 23:57 | operation@crystalgroup.in | Tan90 | CICU3876523 | 10-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | NOT ACHEIVING TEMP | REARRANGE THE CARGO AND DEFROST SETTING CHANGE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No | PCM pads blasting issue | 2024-10-03 04:52 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:12 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 10:31 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 16:38 | 2024-09-11 |  |  |  |  | CICU3876523 |  |  |  | Thermo king | -40*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1UK7HJ05FyBsvUYN-NUeY-xtf94YZW0o3 |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP016 | 2024-09-11 22:10 | chaurasiagarima97@gmail.com | Gennova Biopharmaceuticals Ltd | NA | NA | NA | CICU1938565 | CONTAINER NOT WORKING | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:01 | operation@crystalgroup.in | Gennova Biopharma | CICU1938565 | 20-REEFER | TK-MP4000 | SERVICE-ON CALL | SALE | FOC | WORKING WELL | ITS A SUPERFREEZER MACHINE HAVING 2 COMPRESSORES AND ITS QUIT LOUD IN NATURE COMPAIR TO OTHER SINGLE COMPRESSOR UNITS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP016 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | NA | No | CONTAINER NOT WORKING | 2024-10-03 04:52 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:10 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:00 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-16 18:46 | 2024-09-11 |  |  |  |  | CICU1938565 |  |  |  | Thermo king | +3.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1Hnzuxf2u_p8nb57aX5PdIbkQey4EdgoH |  |  | ONC | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP017 | 2024-09-11 22:12 | chaurasiagarima97@gmail.com | Crystal JNPT | NA | NA | NA | CGMU2989060 | CONTAINER NOT WORKING | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:02 | operation@crystalgroup.in | Crystal Yard-JNPT | CGMU2989060 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | STOCK | FOC | CABLE, PLUG, DISPLAY, KEYPAD, CONTACTOR REQUIRED | NEED PARTS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP017 | Carrier - Thinline | Thinline | LSM 60197754 | LSM60197754 |  |  | JSGA622180043 | NA | No | CONTAINER NOT WORKING | 2024-10-03 04:53 | operation@crystalgroup.in | YES | SEP083 | 20.9.24 | Spares | PI INDUSTRY | PANOLI | CXRU1035856 | SITE | FOC | DAIKIN | 2025-01-15 18:07 | crm@crystalgroup.in | YES | SEP017 | NA |  |  | 2025-01-18 11:06 | crm@crystalgroup.in | YES | SEP083 | NA | [5 empty] | 2025-01-18 13:03 | 2024-09-11 |  |  |  |  | CGMU2989060 |  |  |  | Carrier |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1-Q62Gc03S9utslEJuwWqy_MKJahd-clD |  |  | TRIP041 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP018 | 2024-09-11 22:12 | chaurasiagarima97@gmail.com | Siemens | NA | NA | NA | SHAHABUDDIN | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:04 | operation@crystalgroup.in | Siemens | PRGU4958724 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | SALE | FOC | VOLTAGE ERROR | VOLTAGE GET CORRECTED FROM CLIENT AND WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP018 | Carrier - Thinline |  |  |  |  | Used |  | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 04:53 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:00 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 10:39 | 2024-09-11 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | +20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1kOND6Mz4B0LtDi5toxnDFW5ewHLGzPbh |  |  | ONC | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP030 | 2024-09-16 04:52 | pravin.shinde@crystalgroup.in | PI Industries Limited | Mahendra S Dhatarwal | NA | NA | CXRU1035856 | Contactor & Sensor Problem | Pravin over email |  |  | Running with issues |  |  |  | 2024-10-03 00:43 | operation@crystalgroup.in | PI Industry | CXRU1035856 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | CONTACTOR & SENSOR DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP030 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used |  | NA | No | Contactor & Sensor Problem | 2024-10-03 05:07 | operation@crystalgroup.in | YES | SEP084 | 20.9.24 | Spares, FOC | PI INDUSTRY | PANOLI | CXRU1035856 | SITE | FOC | DAIKIN | 2025-01-15 18:00 | crm@crystalgroup.in | YES | SEP084 | YES |  |  | 2025-01-18 11:07 | crm@crystalgroup.in | YES | SEP084 | NA | [5 empty] | 2025-01-18 13:07 | 2024-09-14 |  |  |  |  | CXRU1035856 |  |  |  | Daikin | +7.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1g9IedX0CgF9HkDFB9_OjMJVFB-L2Pjca |  |  | ONC | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP057 | 2024-09-16 04:54 | viru0068@gmail.com | Reliance sirhind | Shahil mehra | +91 73408 55526 | Electrician | NYKU7931452 | Container gasleakge | Virender Kumar |  |  | Running with issues |  |  |  | 2024-10-03 02:08 | operation@crystalgroup.in | Qwik Supply | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | LEAK IN DISCHARGE LINE | RESOLVED AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP057 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | RAMIZ | No | Container gasleakge | 2024-10-03 06:00 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:05 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:01 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 10:47 | 2024-09-22 |  |  |  |  | NYKU7931452 |  |  |  | Carrier | -19*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=16KZtUdL7gnklDgdoGjc9PllbJSuGtzMN |  |  | TRIP043 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP019 | 2024-09-20 23:50 | chaurasiagarima97@gmail.com | Qwik Supply | Satish | 9182561382 | NA | CGMU2988654 | Inspection for pull out | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:06 | operation@crystalgroup.in | Qwik Supply | CGMU2988654 | 20-REEFER | CARRIER-THINLINE | SERVICE-AT SITE | LEASE | FOC | CONTAINER INSPECTION FOR OFF LEASING THE SAME | INSPECTION DONE | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP019 | Carrier - Thinline | Thinline | 2907L50458 | LSM60197481 |  | Used |  | NA | Yes | Inspection for pull out | 2024-10-03 04:54 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:01 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 10:52 | 2024-09-01 |  |  |  |  | CGMU2988654 |  |  |  | Carrier |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1PdwQqapz5Ly78yM7mQurpT_-pLhLTBsh |  |  | TRIP041 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP020 | 2024-09-20 23:52 | chaurasiagarima97@gmail.com | DIVIS LAB | NA | NA | NA | CONT-3 | PREVENTIVE MAINTENANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-10-03 00:08 | operation@crystalgroup.in | Divis Lab | CONT-3 | NA | CARRIER-THINLINE | SERVICE-AT SITE | SALE | FOC | LEAK IN TERMINAL BOX BECAUSE TERMINALS ARE TRIPPED WHILE TIGHTNING | NEED TO REPLACED TERMINAL | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP020 | [7 empty] | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:54 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:02 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 10:58 | 2024-09-09 |  |  |  |  | CONT-3 |  |  |  | Carrier |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1Crbj_3TF2NAVAqbpk-Z3mTXzL5Blfq_B |  |  | TRIP044 | Yes | Yes | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP021 | 2024-09-20 23:58 | chaurasiagarima97@gmail.com | DSV LOGISTIC | NA | NA | NA | TITU9930006 | PREVENTIVE MAINTENANCE | VIRENDRA |  |  | Preventive Maintenance |  |  |  | 2024-10-03 00:19 | operation@crystalgroup.in | DSV | TITU9930006 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | LED LIGHT NOT WORKING | CHANGED IN WIRING | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP021 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-10-03 04:55 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:03 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 11:02 | 2024-09-09 |  |  |  |  | TITU9930006 |  |  |  | Thermo king | -20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1BmLgq7SHLplxaFkBkzgTmAVZKLb8Vuj0 |  |  | TRIP044 | Yes | Yes | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP022 | 2024-09-21 00:06 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | BMOU9782197 | FLUCTUATIONS IN TEMEPRATURE | UMESH |  |  | Running with issues |  |  |  | 2024-10-03 00:21 | operation@crystalgroup.in | Qwik Supply | BMOU9782197 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EXPANSION VALVE AND COIL, LIQUID VALVE, BY PASS VALVE AND GAS REQ | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP022 | DAikin |  |  | DECOSIIIF/2553/1 |  | Used |  | NA | No | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 04:56 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:04 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 11:10 | 2024-09-09 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | -22*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=13Oxv7vB4KizQq4JBpTgziehXn0qNS2dx |  |  | TRIP043 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP023 | 2024-09-21 00:08 | chaurasiagarima97@gmail.com | Dr Reddy Biotechnology | OMMI | 8464937171 | NA | TITU9930114 | SERVICES | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-03 00:32 | operation@crystalgroup.in | Dr Reddy Biotechnology | TITU9930114 | NA | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | WORKING WELL | WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP023 | Thermoking | MP-4000 | 14E219055 | EOG1000667 |  |  | JSGA622180063 ¦ JSGA622180011 | VIRENDRA | Yes | SERVICES | 2024-10-03 04:57 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:04 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 11:34 | 2024-09-11 |  |  |  |  | TITU9930114 |  |  |  | Thermo king | -28*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1VtwUV0I9M0Q3UIQ0xpayXW-eGWOaRWnI |  |  | TRIP044 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP024 | 2024-09-21 00:10 | chaurasiagarima97@gmail.com | Dr Reddy Biotechnology | NA | NA | NA | TITU9930074 | SERVICES | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-03 00:33 | operation@crystalgroup.in | Dr Reddy Biotechnology | TITU9930074 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | SENSOR CONNECTION LOOSE | FIX PROPERLY AND WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP024 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes | SERVICES | 2024-10-03 04:57 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:04 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 11:39 | 2024-09-11 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1DIsOuT4pc3Dg-OvL41AIggXczZ5NMcui |  |  | TRIP044 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP025 | 2024-09-21 00:12 | chaurasiagarima97@gmail.com | Chemplast Sanmar Limited | NA | NA | NA | TITU9930222 | COMPRESSOR MAKING NOISE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-03 00:35 | operation@crystalgroup.in | Chemplast Sanmar Limited | TITU9930222 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | NEED TO REPLACED COMPRESSOR | COMPRESSOR REPLACED BUT KEYPAD REQUIRED | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP025 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | VIRENDRA | Yes | COMPRESSOR MAKING NOISE | 2024-10-03 04:58 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:05 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 11:55 | 2024-09-12 |  |  |  |  | TITU9930222 |  |  |  | Thermo king | 0*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1Mh70Q_nyaNaBWkE5xc4olSdxH_c6kzNG |  |  | TRIP044 | Yes | Yes | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP026 | 2024-09-21 00:18 | chaurasiagarima97@gmail.com | ITC Ltd | NA | NA | NA | PCIU6010243 | SERVICES | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-03 00:36 | operation@crystalgroup.in | ITC Ltd | PCIU6010243 | 40-REEFER | TK-MP3000 | SERVICE-AT SITE | LEASE | FOC | SETTINGS NOT PROPER | WORKING WELL CHANGED IN SETTING, BODY VALVE SUSPECTED MAY BE NEED TO CHANGE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP026 | Daikin | Daikin | NA | NA | NA | used | JSGA623040191 | VIRENDRA | Yes | SERVICES | 2024-10-03 04:58 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:05 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 12:16 | 2024-09-13 |  |  |  |  | PCIU6010243 |  |  |  | Daikin | -18*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1gDFBelJnDI0Nlwb8NRm0RrkhbambNS0S |  |  | TRIP044 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP027 | 2024-09-21 00:20 | chaurasiagarima97@gmail.com | Qwik Supply | NA | NA | NA | NYKU7931452 | SERVICES | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:38 | operation@crystalgroup.in | Qwik Supply | NYKU7931452 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | FOUND VOLTAGE FLUCTUATION | GET CORRECTED FROM CLINET AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP027 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040289 | SHAHBUDDIN | No | SERVICES | 2024-10-03 04:59 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:05 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 12:26 | 2024-09-13 |  |  |  |  | NYKU7931452 |  |  |  | Carrier | -18*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1y1Nm-PJtO6oFrHolyweRi-FiAhY61q1L |  |  | ONC | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP028 | 2024-09-21 00:22 | chaurasiagarima97@gmail.com | Jubliant Consumer Pvt Ltd | MD BRAHMIALA | 7095177094 | NA | CXRU1030387 | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:39 | operation@crystalgroup.in | Hetero Biopharma | CXRU1030387 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | MOTOR NOISY | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP028 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | SHAHBUDDIN | No | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | 2024-10-03 04:59 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:06 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 12:47 | 2024-09-14 |  |  |  |  | CXRU1030387 |  |  |  | Daikin |  | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1yX7tbNmQPaGyzstxrpWk1FMXL_TR-jX1 |  |  | ONC | Yes | Yes | Urgent | Installation EVP motor | EVP motor | crm@crystalgroup.in | REEFER
SEP029 | 2024-09-21 00:23 | chaurasiagarima97@gmail.com | Laurus Unit 3 | MR. CHENAPA | 6303569967 | NA | ARCU4530675 | FLUCTUATIONS IN TEMEPRATURE | SHAHABUDDIN |  |  | Running with issues |  |  |  | 2024-10-03 00:41 | operation@crystalgroup.in | Laurus Unit 3 | ARCU4530675 | 40-REEFER | CARRIER-THINLINE | SERVICE-ON CALL | LEASE | FOC | FUSE & HARNESS CABLE NOT CONNECTED WELL | FIX IT PRPERLY AND NOW WORKING WELL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP029 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used |  | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 05:00 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 18:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:06 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 12:52 | 2024-09-14 |  |  |  |  | ARCU4530675 |  |  |  | Carrier | +25*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1enH2FgYoIOIG50E_RDPP9SzeEpSCy0Ov |  |  | ONC | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP030 | 2024-09-21 00:24 | chaurasiagarima97@gmail.com | PI Industries Limited | SNEHAL SAHAR | 6357971026 | NA | CXRU1035856 | FLUCTUATIONS IN TEMEPRATURE | VIRENDRA |  |  | Running with issues |  |  |  | 2024-10-03 00:43 | operation@crystalgroup.in | PI Industry | CXRU1035856 | 40-REEFER | TK-MP3000 | SERVICE-ON CALL | LEASE | FOC | CONTACTOR & SENSOR DEFECTIVE | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP030 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used |  | NA | No | Contactor & Sensor Problem | 2024-10-03 05:07 | operation@crystalgroup.in | YES | SEP084 | 20.9.24 | Spares, FOC | PI INDUSTRY | PANOLI | CXRU1035856 | SITE | FOC | DAIKIN | 2025-01-15 18:00 | crm@crystalgroup.in | YES | SEP084 | YES |  |  | 2025-01-18 11:07 | crm@crystalgroup.in | YES | SEP084 | NA | [5 empty] | 2025-01-18 13:07 | 2024-09-14 |  |  |  |  | CXRU1035856 |  |  |  | Daikin | +7.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=1g9IedX0CgF9HkDFB9_OjMJVFB-L2Pjca |  |  | ONC | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP031 | 2024-09-21 00:29 | chaurasiagarima97@gmail.com | Cipla Unit 3 | NA | NA | NA | TITU9231009 | REPAIR | UMESH |  |  | Running with issues |  |  |  | 2024-10-03 00:44 | operation@crystalgroup.in | Cipla Unit 3 | TITU9231009 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | COIL DIRTY, KEYPAD DEFECTIVE | KEYPAD CHANGED, CLEAN COIL & CHECKED PARAMAETERS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP031 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622170399 | NA | Yes | REPAIR | 2025-01-17 19:29 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:31 | operation@crystalgroup.in | NO |  |  |  |  | 2025-01-18 13:18 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-18 13:24 | 2024-09-14 |  |  |  |  | TITU9231009 |  |  |  | Daikin | 4.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1pGVfkmQkfgfjUJL0n_wM_pwIAIKouV4E |  |  | TRIP043 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
SEP032 | 2024-09-21 00:31 | chaurasiagarima97@gmail.com | Cipla Unit 3 | NA | NA | NA | TITU9230980 | FLUCTUATIONS IN TEMEPRATURE | UMESH |  |  | Running with issues |  |  |  | 2024-10-03 00:46 | operation@crystalgroup.in | Cipla Unit 3 | TITU9230980 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DISPLAY DEFECTIVE, AND GAS FOUND SHORT | NEED PARTS | Yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP032 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | NA | Yes | FLUCTUATIONS IN TEMEPRATURE | 2024-10-03 05:18 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-17 19:31 | operation@crystalgroup.in | NO |  |  |  |  | 2025-01-18 13:18 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-18 13:28 | 2024-09-17 |  |  |  |  | TITU9230980 |  |  |  | Daikin | 3.5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | Yes | https://drive.google.com/open?id=11VD6iw-YpIh3x6icSjnPcxSa5yKIiuFc |  |  | TRIP043 | Yes | Yes | Urgent | NA | NA | crm@crystalgroup.in | REEFER
SEP033 | 2024-09-21 00:32 | chaurasiagarima97@gmail.com | UPS | NA | NA | NA | SJKU4000110 | INSTALLATION | SHAHABUDDIN |  |  | Installation |  |  |  | 2024-10-03 00:47 | operation@crystalgroup.in | UPS | SJKU4000110 | 40-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | INSTALLATION | DONE AND GIVEN TRAINIG | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP033 | Thermoking | MP-4000 |  |  |  | Brand New |  | SHAHBUDDIN | Yes | INSTALLATION | 2024-10-03 05:18 | operation@crystalgroup.in | YES | SEP114 | 28.9.24 | Consumables, FOC | UPS | HYDRABAD | SJKU4000110 | SITE | FOC | TK-MP4000 | 2025-01-15 14:48 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:07 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 12:58 | 2024-09-16 |  |  |  |  | SJKU4000110 |  |  |  | Thermo king | +20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1fUlaYPjJhnVKZlILg8L9Pnb_YKRZLNIO |  |  | TRIP041 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
OCT012 | 2024-10-03 23:57 | pravin.shinde@crystalgroup.in | Jubliant Consumer Pvt Ltd | Arjun Das | 6378922807 | Manager - Operations | TRIU6687350 | MACHINE SHUT DOWN | SANDEEP |  |  | Running with issues |  |  |  | 2024-10-06 22:13 | operation@crystalgroup.in | JUBILANT | TRIU6687350 | 20-REFEER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONDENSOR COIL VERY DIRTY SO CLEANEDD IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENT ALL WORKING GOOD TEMPERATURE COOLING -25 IN RANGE | container running good need to clean condenser coil every 10 days | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT012 | Carrier |  |  |  |  | USed |  | UMESH |  | MACHINE SHUT DOWN | 2024-10-06 22:38 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-06 22:43 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-06 22:44 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-06 03:41 | 2024-10-06 |  |  | Jubliant | Noida | TRIU6687350 | 20FT |  | TEMPRATURE ISSUE | Carrier | -25 | Clean | Clean | https://drive.google.com/open?id=1G2swp9MlIh4TBuPglneTKCmri1n2NkHj | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 16bar | 10 | 405 | Short |  | Need to clean condenser coil every 10 days | No |  |  | https://drive.google.com/open?id=1YYPEaiwFkjKUnVvrnOzWdpW0GuxN41nC https://drive.google.com/open?id=1_BPoWYlzC9jIAwvnlLWibp8sGLaz_5Yq | TRIP049
OCT001 | 2024-10-04 00:42 | operation@crystalgroup.in | Crystal | NA | NA | NA | TITU9928040 | CONTAINER NOT WORKING, PTI FAIL | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-04 00:44 | operation@crystalgroup.in | CRYSTAL | TITU9928040 | 40-REEFER | THERMOKING MP4000 | REPAIR | STOCK | FOC | POWER MODULE FAIL | NEED TO CHANGE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT001 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | VIRENDRA |  | CONTAINER NOT WORKING, PTI FAIL | 2024-10-04 00:46 | operation@crystalgroup.in | YES | OCT003 | 2025-10-01 | Spares, FOC | CRYSTAL | JNPT | TITU9928040 | DEPOT | FOC | TK-MP4000 | 2024-10-04 00:48 | operation@crystalgroup.in | YES | OCT003 | YES |  |  | 2024-10-04 00:48 | operation@crystalgroup.in | YES | OCT003 | TECHNICIAN | [5 empty] | 2024-10-04 01:22 | 2024-10-01 |  |  | CRYSTAL | JNPT | TITU9928040 | 40FT |  | PTI FAIL | Thermo king | M18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Full | PTI PASS - CONTAINER OKAY | POWER MODULE - LP SWITCH - DISPLAY | YES |  |  | https://drive.google.com/open?id=1GOwDB79y-7uvv8cfmJ5OuuNt4h_-PW1K | NA
OCT002 | 2024-10-04 00:59 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | K. SHREEVIVET | 9184268772 | EXECUTIVE | APRU5091041 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 01:03 | operation@crystalgroup.in | HETERO | APRU5091041 | 40-REEFER | NA | PREVENTIVE MAINTENANCE | LEASE | FOC | AL60 DEFROST SENSOR | DEFROST SENSOR REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT002 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-10-04 01:04 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 01:04 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 01:04 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 02:45 | 2024-10-02 |  |  | HETERO | HYDERABAD | APRU5091041 | 40FT |  |  | Carrier | 5 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35 PSI & 280 PSI | 2010-10-10 | 430/430/430 | Short | CHECK AND FOUND THIS CONTAINER DEFROST SENSOR D/F | DEFROST SENSOR REPLACE | NO |  |  | https://drive.google.com/open?id=1lzB6zNwrHWhA_2ZEFjJvRncaEJqYIe12 | TRIP045
OCT003 | 2024-10-04 01:57 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | K. SHREEVIVET | 9154268772 | EXECUTIVE | PCIU6016370 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 02:01 | operation@crystalgroup.in | HETERO | PCIU6016370 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CONTROLLER D/F | CONTROLLER REPLACE AND CONTAINER RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT003 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-10-04 02:01 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 02:01 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 02:01 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 02:50 | 2024-10-02 |  |  | HETERO | HYDERABAD | PCIU6016370 | 40FT |  | CONTROLLER D/F | Daikin | 8 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35PSI & 250PSI | 2010-10-10 | 400/420/410 | Short | CHECK AND FOUND CONTROLLER D/F | CONTROLLER REPLACE AND CONTAINER RUNNING GOOD | NO |  |  | https://drive.google.com/open?id=1tIq6W8iw9lg9fcb_5wCi-pwH6BMIE7xE | TRIP045
OCT004 | 2024-10-04 02:09 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | K. SHREEVIVET | 9154268772 | EXECUTIVE | CXRU1030427 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 02:11 | operation@crystalgroup.in | HETERO | CXRU1030427 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | ALE607 KEYPAD/SHEET KET D/F | SHEET KEY AND DISPLAY COVER REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT004 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-10-04 02:11 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 02:12 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 02:12 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 02:56 | 2024-10-02 |  |  | HETERO | HYDERABAD | CXRU1030427 | 40FT |  | ALE607 KEYPAD/SHEET KEY D/F | Daikin | 5 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 34psi& 260 psi | 2010-10-10 | 410/430/420 | Short | checked and found sheet key and display cover d/f | sheet key and display cover replace and container running good | NA |  |  | https://drive.google.com/open?id=1p0fC_bAbXK_6KycKvU7CCKPsr-SlcoHx | TRIP045
OCT005 | 2024-10-04 02:14 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | CRV SHANI | 9154268772 | EXECUTIVE | CXRU1026520 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 02:20 | operation@crystalgroup.in | HETERO | CXRU1026520 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED AND FOUNF CONTAINER | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT005 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-10-04 02:20 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 02:21 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 02:21 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 03:01 | 2024-10-03 |  |  | HETERO | HYDERABAD | CXRU1026520 | 40FT |  | NA | Daikin | 5 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35PSI & 270PSI | 9.9/9.8/10 | 400/410/400 | Short | CHECK AND FOUND CONTAINER RUNNING GOOD CONDITION | NA | NA |  |  | https://drive.google.com/open?id=1eahiLnWmtAzKvb041w5cor5mSGkMQpl3 | TRIP045
OCT006 | 2024-10-04 02:24 | operation@crystalgroup.in | CIPLA | DEEPAK.D | 8322889145 | SR. EXECUTIVE | TITU9230980 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 02:27 | operation@crystalgroup.in | CIPLA | TITU9230980 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | REFILL R-134a 1800g | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT006 | Daikin | Daikin | NA | LXE10E136F2R | NA | Brand new | JSGA622180039 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-04 02:27 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 02:28 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 02:28 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 03:04 | 2024-10-03 |  |  | CIPLA | GOA | TITU9230980 | 40FT |  | NA | Daikin | 4.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 120KPA & 1600KPA | 7.2/7.0/7.1 | 396/392/394 | Not done | NA | REFILL R-134a 1800g | NO |  |  | https://drive.google.com/open?id=1YDGlL3Gn2jNAal7zCzwHmYnj_hCBqUWH | TRIP046
OCT007 | 2024-10-04 04:44 | operation@crystalgroup.in | TIPTOP PLAZA | PRASHANT DUTTA | 9920230772 | MANAGER | SITE INSPECTION | SITE INSPECTION | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-04 04:49 | operation@crystalgroup.in | TIPTOP PLAZA | SITE INSPECTION | NA | NA | NA | NA | NA | THERE IS NO SUFFICIENT SPACE FOR TRAILER AND HYDRA SO DISCUSSED WITH PRASHANT SIR SAME | THE CONTAINER IN BASEMENT IS FULLY SECURE AND CLEANED AREA NO ISSUE FOR CONDENSATION , NEED TOMAKE SURE WHILE UNLOADING OF CONTAINER SINCE THE SPACE OF TOP IS LESS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT007 | [7 empty] | UMESH |  | SITE INSPECTION | 2024-10-04 04:51 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 04:52 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 04:52 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 05:02 | 2024-10-04 |  |  | TIPTOP PLAZA | THANE | SITE INSPECTION |  |  | SITE INSPECTION | [34 empty] | THERE IS NO SUFFICIENT SPACE FOR TRAILER AND HYDRA SO DISCUSSED WITH PRASHANT SIR SAME | THE CONTAINER IN BASEMENT IS FULLY SECURE AND CLEANED AREA NO ISSUE FOR CONDENSATION , NEED TOMAKE SURE WHILE UNLOADING OF CONTAINER SINCE THE SPACE OF TOP IS LESS |  |  | https://drive.google.com/open?id=14ACfjWGRAtjmFQMwsIHQEXEFWDPI3nll | TRIP047
OCT008 | 2024-10-04 05:15 | operation@crystalgroup.in | Shri. SWAMI NARAYAN TEMPLE | SADHU UTTAMSEVADAS | 7045995068 | NA | TCLU1911479 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-04 05:13 | operation@crystalgroup.in | Shri. SWAMI NARAYAN TEMPLE | TCTU1911479 | 20-REFEER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION | NEED WASH ONLY RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT008 | [7 empty] | UMESH |  | PREVENTIVE MAINTENANCE | 2024-10-04 05:10 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-04 05:10 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-04 05:10 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-04 05:09 | 2024-10-04 |  |  | Shri. SWAMI NARAYAN TEMPLE | DADAR | TCLU1911479 | 20FT |  | REGULAR SERVICE | Daikin | -15 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 223 KPA & 1728 KPA | 2011-11-11 | 405/405/405 | Short | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION | NEED WASH ONLY RUNNING GOOD | NA |  |  | https://drive.google.com/open?id=1-KOWTk0Sem4-F114Ggn84rgmGRCvRSAW | TRIP047
OCT009 | 2024-10-04 21:27 | operation@crystalgroup.in | Symbiotech | Balkishan | 7747937030 | NA | CRIU6617292 | FLUCTUATIONS IN TEMEPRATURE, TEMP ISSUE | PUSHPA |  |  | Running with issues |  |  |  | 2024-10-07 05:02 | operation@crystalgroup.in | SYMBIOTEC | CRIU6617292 | 20-REFEER | CARRIER | SERVICE-ON CALL | SALE | FOC | ALARM 22 EVAPORATOR MOTOR 1PH , ALARM 72 LESS GASS | NEED TO LEAK TEST, AND REPLACE MOTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT009 | [7 empty] | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE, TEMP ISSUE | 2024-12-31 18:03 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:03 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 13:20 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-16 16:11
OCT010 | 2024-10-05 | operation@crystalgroup.in | SOFTBOX | KONDAPALLI SATISH | 8977711235 | SITE MANAGER | GRMU3707470 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-05 00:02 | operation@crystalgroup.in | SOFTBOX PVT LTD | GRMU3703470 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | PM DONE AND SHORT PTI PASS CONTAINER IS RUNNING GOOD IOT INSTALLED | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT010 | [7 empty] | MUKESH |  | PREVENTIVE MAINTENANCE | 2024-10-05 00:05 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-05 00:05 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-05 00:05 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-05 00:11 | 2024-10-04 |  |  | SOFTBOX PVT LTD | TELANGANA | GRMU3707470 | 40FT |  | IOT INSTALLATION & PM | Daikin | -21 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35PSI & 270 PSI | 2010-10-10 | 420/420/420 | Short | NA | PM DONE AND SHORT PTI PASS CONTAINER RUNNING GOOD CONDITION IOT INSTALLED | NA |  |  | https://drive.google.com/open?id=1A4nhRnAhRE9JxCex9JPsCVyZmkjKZfm1 | TRIP045
OCT011 | 2024-10-05 01:45 | pravin.shinde@crystalgroup.in | Parle Biz | Bhupendra Negi | 919808239694 | Na | CXRU1186404 | COMPRESSOR MAKING NOISE | Pushpa ma'am |  |  | Running with issues |  |  |  | 2024-10-07 05:43 | operation@crystalgroup.in | PARLE | CXRU1186404 | 40-REFEER | DAIKIN | SERVICE-ON CALL | SALE | FOC | COMPRESSOR NOISY | NEED TO REPLACE COMPRESSOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT011 | DAikin | LXE10E136F2 | M002106 | K11910045666 | DECOS 3F 2551 / 1 | used |  | UMESH |  | COMPRESSOR MAKING NOISE | 2024-10-14 10:20 | operation@crystalgroup.in | YES | NA | NA | Spares, FOC | PARLE BISCUIT | RUDRAPUR | CXRU1186404 | SITE | FOC | DAIKIN | 2024-10-14 10:21 | operation@crystalgroup.in | YES | NA | NA |  |  | 2024-10-14 10:22 | operation@crystalgroup.in | YES | NA | ARRENGING AT SITE | [5 empty] | 2024-10-14 10:35 | 2024-10-12 |  |  | PARLE BISCUIT | RUDRAPUR | CXRU1186404 | 40FT |  | CONTAINER BREAKDOWN | Daikin | -10 | [31 empty] | CHECK AND FOUND CONTAINER BREAKDOWN THEN START CONTAINER & FOUND COMPRESSOR ROTARY DAMAGE COMPRESSOR IS IN DEAD CONDITION NEED TO REPLACE THE COMPRESSOR | CONTAINER BREAKDOWN | YES |  |  | https://drive.google.com/open?id=1gEpOYVAejGDyAp8rKvqjeoVq8xpIB5df | TRIP048
OCT013 | 2024-10-06 03:00 | pravin.shinde@crystalgroup.in | Jubliant Consumer Pvt Ltd | Na | Na | Na | GRMU3607418 | PREVENTIVE MAINTENANCE | Pravin |  |  | Preventive Maintenance |  |  |  | 2024-10-06 22:22 | operation@crystalgroup.in | JUBILANT | GRMU3607418 | 20-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED & FOUND CONTAINER BREAKDOWN DUE TO HEAVVY SOUND IN COMPRESSOR SO CHECKED & FOUND EV COIL NOT OPEN PROPERLY | SO FIX THE EV COIL AND CONTAINER RUNNING OK | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT013 | Daikin |  |  |  |  | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-31 18:03 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:04 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 13:21 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-10-06 03:41 | 2024-10-06 |  |  | Jubliant | Noida | GRMU3607418 | 20FT |  | TEMPRATURE ISSUE | Carrier | -25 | Clean | Clean | https://drive.google.com/open?id=1G2swp9MlIh4TBuPglneTKCmri1n2NkHj | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 16bar | 10 | 405 | Short |  | Need to clean condenser coil every 10 days | No |  |  | https://drive.google.com/open?id=1zSvvc7OClIwG-HCCPjXKj6vTtwqHKE5f https://drive.google.com/open?id=1-bmFIZ9zD8KvlHJgaymKaFlyV5aLJu0S | TRIP049
OCT014 | 2024-10-06 08:18 | pravin.shinde@crystalgroup.in | GMR - HYD | Na | Na | Na | MYRU4517508 | Off lease inspection | Pravin |  |  | Running with issues |  |  |  | 2024-10-06 22:25 | operation@crystalgroup.in | GMR AIR CARGO | MYRU4517508 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING GOOD , DISPLAY FADED | PM , SHORT PTI PASS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT014 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | MUKESH |  | Off lease inspection | 2024-10-06 22:40 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-06 22:43 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-06 22:45 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-06 03:14 | 2024-10-05 |  |  | GMR Hyderabad Air cargo | Hyderabad | MYRU4517508 | 40FT |  |  | Daikin |  | Clean | Clean | https://drive.google.com/open?id=1CL7eWrxinLCga-fhkHbnbIWj1II0cDAb | Okay | Clean | Okay | Okay |  | Okay | https://drive.google.com/open?id=1n_-3iYBYaJVcJoxk9da9TpMp2h3v9XDK | Okay | https://drive.google.com/open?id=1BOlcvjnYF_rKaCm0JHfNkg4MXECahNh6 | Okay | https://drive.google.com/open?id=1OhErdbqPgziDyXBFbhgXVvbl20MjNTQ- | Okay |  | Okay | Okay | https://drive.google.com/open?id=1MT7EUd-Zv4aXMpxy1LrM0apoeRNQuQ1F | Okay | https://drive.google.com/open?id=1MPmkcByOszgclDU1KsaFqf4tekFN3-Au | Okay | Okay |  | Done | Clean | https://drive.google.com/open?id=1DxfaTHM28RfVnQe61D88dDtKaOemnhSg | 35 psi suction 270 discharge | 10,10,10 | 400410400 | Short | Na | Pm done ,and short pti paas container running good condition | Na |  |  | https://drive.google.com/open?id=1wzVpwFjXOnISIUvSZxF8LoEt54Rbp8OR https://drive.google.com/open?id=14HEWMN_BtDrRxFeZ_BNcPLcBg1FAm488 | TRIP045
OCT015 | 2024-10-06 21:01 | pravin.shinde@crystalgroup.in | BPCL | NA | NA | NA | CXRU1043337 | CONTAINER NOT WORKING | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-06 22:29 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND NO GAS IN SYSTEM HPT AND LPT GOES TO MINUS AND EXPENSION OPEN 100% | WE HAVE REFILL R-134a 5kg NOW CONTAINER RUNNING IN RANGE TEMP PRESENT TEMP +14.2 C AND SENSOR VALVE Ab 30.6C ,EI 12.1C ,EO 13.2C, dC 87.0C , SGS 22.9C, SMV 21%, EV 47% | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT015 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | VIRENDRA |  | CONTAINER NOT WORKING | 2024-10-06 22:40 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-06 22:44 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-06 22:45 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-06 22:56 | 2024-10-05 |  |  | BPCL | KOCHIN | CXRU1043337 | 40FT |  | NA | Daikin | 14 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 222KP & 833KP | 9.3A/9.0A/9.1A | 401V/397V/399V | Not done | WE HAVE ATTEND THIS UNIT AND FOUND NO GAS IN SYSTEM HPT AND LPT GOES TO MINUS AND EXPENSION OPEN 100% DAY 2 - "WE HAV FOUND CONTAINER WORKING SOUND CONDITION WITHOUT ANY ALARM EV 53% , SMV 14%, DC 85C PRESENT TEMP +15 C" | WE HAVE REFILL R-134a 5kg NOW CONTAINER RUNNING IN RANGE TEMP PRESENT TEMP +14.2 C AND SENSOR VALVE Ab 30.6C ,EI 12.1C ,EO 13.2C, dC 87.0C , SGS 22.9C, SMV 21%, EV 47% | SHEET KEY |  |  | https://drive.google.com/open?id=1hJgzl_7XJPtvMtCx7f-P2nq8n-Fj2poe | NA
OCT016 | 2024-10-06 22:14 | pravin.shinde@crystalgroup.in | GMR | NA | NA | NA | CGMU2990462 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-06 22:37 | operation@crystalgroup.in | GMR AIR CARGO | CGMU2990462 | 20-REFEER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKD AND FOUND DEFROST SENSOR DEFECTIVE NEED TO REPLACE | PM DONE AND SHORT PTI FAIL PS CONTAINER RUNNING GOOD CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT016 | [7 empty] | SHAHBUDDIN | No | PREVENTIVE MAINTENANCE | 2024-12-31 18:04 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:04 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 13:22 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-10-06 23:01 | 2024-10-05 |  |  | GMR AIR CARGO | HYDERABAD | CGMU2990461 | 20FT |  | PM | Carrier | 3 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35PSI & 270PSI | 2010-10-10 | 400/400/400 | Not done | CHECKD AND FOUND DEFROST SENSOR DEFECTIVE NEED TO REPLACE | PM DONE AND SHORT PTI FAIL PS CONTAINER RUNNING GOOD CONDITION | DEFROST SENSOR AL60 THERMOSTATE SENSOR AL59 |  |  | https://drive.google.com/open?id=115GWshg17_DXeeWPQ6cLM0xZrKViwQ-Z | NA
OCT017 | 2024-10-07 22:55 | operation@crystalgroup.in | DIVIS LAB | SURARCHIT | 9441911498 | NA | DCUNIT07 | COMPRESSOR SHUTDOWN AFTER 2-3 MIN OF WORKING EVAPORATOR COIL ALSO NOT WORKING | NINAD |  |  | Running with issues |  |  |  | 2024-11-20 17:41 | service@crystalgroup.in | DIVIS LAB | DC-UNIT-09 | 40 FT | CARRIER | SERVICE-ON CALL | LEASE | CHARGEABLE | COMPRESSOR CUT OUT & SUPPLY AIR FLOW BLOCK | T BAR FLOOR CLEAN WITH HOT WATER . | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT017 | [7 empty] | RAMIZ |  | COMPRESSOR SHUTDOWN AFTER 2-3 MIN OF WORKING EVAPORATOR COIL ALSO NOT WORKING | 2024-11-20 18:07 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-20 18:08 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-20 18:08 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-20 18:24 | 2024-10-07 |  |  |  |  | DC-UNIT-09 |  |  |  | Carrier | -20 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9- 13.1 | 12.1/12.2/12.1 | 410/411/410 | Not done | COMPRESSORCUT OF & AIR FLOW BLOCK IN T BAR FLOOR | CLEAN T BAR FLOOR WITH HOT WATER | NA |  |  | https://drive.google.com/open?id=1-LRG0iCfgovFw6mwKsj8-xWSzEUpSHnE | NA | No | No | Can be done on next PM | NA
OCT018 | 2024-10-08 03:45 | operation@crystalgroup.in | RELIANCE | NA | NA | NA | CICU2094089 | CONTACTOR NOT WORKING | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-09 03:14 | operation@crystalgroup.in | RELIANCE | CICU2094089 | 10-REFEER | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND COMPRESSOR CONTACTOR BURN AND TRANSFORMER NOISY. COMPRESSOR CREATE NOISE ALARM BUZER NOT CREATE SOUND | WE HAVE REPLACE CONTACTOR BUT NOT SUPPORTED NEED CONTACTOR 1NOS PRESENT CONTAINER RUN IN BURN CONTACTOR SO NEED CONTACTOR ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT018 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 |  | BrandNew |  | VIRENDRA |  | CONTACTOR NOT WORKING | 2024-10-09 03:17 | operation@crystalgroup.in | YES | OCT064 | 08.10.2024 | Spares, FOC | RELIANCE | KERELA | CICU2094089 | SITE | FOC | TK-MP4000 | 2024-10-09 03:28 | operation@crystalgroup.in | YES | OCT064 | YES |  |  | 2024-10-09 03:30 | operation@crystalgroup.in | YES | OCT064 | TECHNICIAN | [5 empty] | 2024-10-09 04:02 | 2024-10-08 |  |  | RELIANCE | KERELA | CICU2094089 | 10FT |  | NA | Thermo king | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -NA- & 22.3B | 11.6A/12.1A/12.3A | 405V/401V/403V | Not done | WE HAVE ATTEND THIS UNIT AND FOUND COMPRESSOR CONTACTOR BURN AND TRANSFORMER NOISY. COMPRESSOR CREATE NOISE ALARM BUZER NOT CREATE SOUND | WE HAVE REPLACE CONTACTOR BUT NOT SUPPORTED NEED CONTACTOR 1NOS PRESENT CONTAINER RUN IN BURN CONTACTOR SO NEED CONTACTOR ASAP | CONTACTOR 25A, TRANSFORMER, MANTRAP |  |  | https://drive.google.com/open?id=1XMxRfY_r82Tr9ZB-inev2EnGvaH-rLnF | TRIP46
OCT019 | 2024-10-09 00:11 | sushma.poojari@crystalgroup.in | Renew Power | Sunil Meghrajani | Mobile: 7043217657; WhatsApp: (+91) 9727373022 | SM - Commercial | CICU2782230 | FLUCTUATIONS IN TEMEPRATURE | Sushma |  |  | Running with issues |  |  |  | 2024-12-02 14:31 | service@crystalgroup.in | RENEW POWER | CICU2782230 | 40HQ | MP4000 | SERVICE-ON CALL | SALE | FOC | TEMPERATURE NOT POLL DOWN, CONDENSOR COIL HEAVY DIRTY | CONDENSOR COIL CLEANED WITH FRESH WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT019 | Thermoking | Magnum Plus | E0GM030246 | ABC782800322010263 |  | BrandNew |  | SHAHBUDDIN |  | FLUCTUATIONS IN TEMEPRATURE | 2024-12-03 10:12 | service@crystalgroup.in | NO | [9 empty] | 2024-12-03 10:12 | service@crystalgroup.in | NO |  |  |  |  | 2024-12-03 10:13 | service@crystalgroup.in | NO | [7 empty] | 2024-12-02 14:37 | 2024-10-09 |  |  |  |  | CICU2782230 |  |  |  | Thermo king | -30C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2,2B/17.6B | 9.8/9.8/9.9 | 411/410/411 | Not done | CONDENSOR COIL DIRTY | CLEANED CONDENSER COIL WITH FRESH WATER | NO | https://drive.google.com/open?id=14BTekcbRtCnWUOop1xqhptryuCpozIKn |  |  | NA | No | No | Can be done on next PM | NO
OCT052 | 2024-10-11 16:16 | pushpa.shetty@crystalgroup.in | Parle Sitarganj | Supreet Lamba | 9917480215 | Warehouse | MYRU4506735 | temp getting increased | Pushpa |  |  | Running with issues |  |  |  | 2024-11-20 16:13 | operation@crystalgroup.in | PARLE | MYRU4506735 | 40-REEFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | TEMPERATURE NOT PULL DOWN | HOT WATER WASHING EVP COIL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT052 | [7 empty] | RAMIZ |  | temp getting increased | 2024-11-20 16:13 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-20 16:14 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-20 16:15 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-20 16:26 | 2024-10-11 |  |  |  |  | MYRU4506735 |  |  |  | Daikin | -6 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  |  |  | Okay | Okay | Okay | Done | Clean |  | 0.1& 12.5 | 10/10.1/10 | 400/401/403 | Not done | ICE FOUNDATION ON EVAPORATOR COIL | EVAPORATOR COIL CLEAN WITH HOT WATER | NO |  |  | https://drive.google.com/open?id=1YcdlifjQxRNWZHgsT7AIlGLb9ro7GLCk | NA | No | No | Can be done on next PM | NO
OCT020 | 2024-10-14 10:39 | operation@crystalgroup.in | AAK LIMITED | NA | NA | NA | SJKU4000038 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 10:42 | operation@crystalgroup.in | AAK LIMITED | SJKU4000038 | 40-REFEER | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT020 | Carrier-Primeline | Primeline |  |  |  |  | JSGA623040167 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-14 10:42 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 10:42 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 10:43 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 10:48 | 2024-10-11 |  |  | AAK LIMITED | KHOPOLI | SJKU4000038 | 40FT |  | NA | Carrier | 20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4.4b & 18.0b | 9.8A/9.3A/9.5A | 398V/393V/395V | Not done | NA | WE HAVE REFULL COMPRESSOR OIL 1LTR AND R-134a GAS REFULL 7 KG CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM PRESENT TEMP +19.9C | NA |  |  | https://drive.google.com/open?id=10X4Kp9FhJw7G43MPRzw0aoGXmFZuaNss | TRIP051
OCT021 | 2024-10-14 10:50 | operation@crystalgroup.in | AAK LIMITED | NA | NA | NA | CICU8118070 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 10:52 | operation@crystalgroup.in | AAK LIMITED | CICU8118070 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT021 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-14 10:52 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 10:53 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 10:53 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 10:57 | 2024-10-11 |  |  | AAK LIMITED | KHOPOLI | CICU8118070 | 40FT |  | NA | Thermo king | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 18.1b | 8.0A/8.1A/8.3A | 410V/407V/409V | Not done | NA | WE HAVE UPDATED SOFTWARE IN THIS UNIT | NA |  |  | https://drive.google.com/open?id=1-mNpqZMWrcXtw-DsdpRZP5tVk3xUfR-L | TRIP051
OCT022 | 2024-10-14 10:59 | operation@crystalgroup.in | AAK LIMITED | NA | NA | NA | CICU8118130 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 11:01 | operation@crystalgroup.in | AAK LIMITED | CICU8118130 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT022 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-14 11:01 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 11:02 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 11:02 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 11:05 | 2024-10-11 |  |  | AAK LIMITED | KHOPOLI | CICU8118130 | 40FT |  | PM | Thermo king | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 18.7b | 8.0A/7.7A/7.9A | 405V/401V/403V | Not done | PM | WE HAVEUPDATED THE SOFTWARE IN THIS UNIT | NO |  |  | https://drive.google.com/open?id=1kZhANvfOYgtOuZC5Us3qrk4sL70ixDDj | TRIP051
OCT023 | 2024-10-14 11:06 | operation@crystalgroup.in | AAK LIMITED | NA | NA | NA | CICU8118167 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 11:07 | operation@crystalgroup.in | AAK LIMITED | CICU8118167 | 40-REFEER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT023 | Thermoking | MP4000 |  |  |  | Brand new |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-14 11:08 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 11:08 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 11:09 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 11:15 | 2024-10-11 |  |  | AAK LIMITED | KHOPOLI | CICU8118167 | 40FT |  | TK-MP4000 | Thermo king | 20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 16.8b | 8.8A/8.3A/8.5A | 407V/403V/405V | Not done | WE HAVE ATTENDED THIS UNIT AND FOUND SYSTEM SHOW GAS LEVEL DOWN AND OIL START TO SICHARGE PIPELINE | WE HAVE UPDATED THE SOFTWARE IN THIS UNIT | NA |  |  | https://drive.google.com/open?id=1mUYyB7b5ay_dL2M7Z55bpfXmyuEkhm2d | TRIP051
OCT024 | 2024-10-14 11:17 | operation@crystalgroup.in | RELIANCE | NA | NA | NA | CXRU1040322 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 11:18 | operation@crystalgroup.in | RELIANCE | CXRU1040322 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT024 | [7 empty] | UMESH |  | PREVENTIVE MAINTENANCE | 2024-10-14 11:19 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 11:19 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 11:21 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 11:34 | 2024-10-11 |  |  | RELIANCE | HAPUR | CXRU1040322 | 40FT |  | PM | Daikin | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 150 & 1600 | 2009-09-09 | 401/401/401 | Not done | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION ALL EQUIPMENTS WORKING GOOD | CONTAINER RUNNING IN GOOD CONDITION | NA |  |  | https://drive.google.com/open?id=1jJ0-NfQ0idldJoxyxSwwGropHl4dtU6Z | TRIP048
OCT025 | 2024-10-14 12:12 | operation@crystalgroup.in | RELIANCE | NA | NA | NA | CXRU1043912 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 12:12 | operation@crystalgroup.in | RELIANCE | CXRU1043912 | 40-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT025 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-10-14 12:13 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 12:13 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 12:13 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 12:18 | 2024-10-11 |  |  | RELIANCE | HAPUR | CXRU1043912 | 40FT |  | PM | Daikin | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 180 - 1700 | 2010-10-10 | 400/400/400 | Not done | checked and found container running in good condition all component working in good condition | container running in good condition | NO |  |  | https://drive.google.com/open?id=1q__i7US-Zs_G_Dmc7Ji4J1QqAz1_a5F5 | TRIP048
OCT026 | 2024-10-14 12:22 | operation@crystalgroup.in | RELIANCE | PRASHANT | 8318896867 | SR. EXECUTIVE | TITU7263521 | BREAKDOWN | PRAVIN |  |  | Complete Breakdown |  |  |  | 2024-10-14 12:24 | operation@crystalgroup.in | RELIANCE | TITU7263521 | 10-REFEER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | BREAKDOWN | NEED TO REPLACE ALL VALVE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT026 | Daikin |  |  |  |  | brand New | JSGA622180055 | UMESH |  | BREAKDOWN | 2024-10-14 12:29 | operation@crystalgroup.in | YES | NA | NA | Spares, FOC | RELIANCE | HAPUR | TITU7263521 | SITE | FOC | DAIKIN | 2024-10-14 12:30 | operation@crystalgroup.in | YES | NA | NA |  |  | 2024-10-14 12:31 | operation@crystalgroup.in | YES | NA | ARRENGING AT SITE | [5 empty] | 2024-10-14 12:36 | 2024-10-11 |  |  | RELIANCE | HAPUR | TITU7263521 | 10FT |  | BREAKDOWN | Daikin | -30 | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 180 & 1900 | 11.2/11.2/11.2 | 400/400/400 | Not done | CHECKED & FOUND SOME ISSUE IN CONTAINER COMPRESSOR BACK PRESSURE SOUND GREAT NEED TO REPLACE SOON IN FUTURE | CONTAINER RUNNING GOOD THIS TIME BUT NEED TO REPLACE ALL VALVE OR REPLACE THE UNIT ONLY | YES |  |  | https://drive.google.com/open?id=1G9BR9MJtJEi4i2hbkNJP8mA4OT0Dct-R | TRIP048
OCT027 | 2024-10-14 12:38 | operation@crystalgroup.in | RELIANCE | RAJVEER YADAV | 8826818750 | CPC MANAGER | TCLU1130265 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 12:39 | operation@crystalgroup.in | RELIANCE | TCLU1130265 | 40-REFEER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT027 | Thermoking | MP-4000 |  |  |  | Refurbished |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-10-14 12:39 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 12:40 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 12:40 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 12:44 | 2024-10-08 |  |  | RELIANCE | RAJPURA | TCLU1130265 | 40FT |  | PM | Thermo king | -20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 21 | 2010-10-10 | 400/400/400 | Not done | CHECKED AND FOUND CONDENSOR COIL DIRTY SO CLEANED IT PROPERLY WITH WATER THEN CHECKED OTHER PARTS MOTOR COMRPESSOR AND SENSORS ALL PARTS WORKING GOOD | CONTAINER RUNNING INM GOOD CONDITION | NA |  |  | https://drive.google.com/open?id=1V5mNR4XA4TVrHfHbqJrieiLJh5GAtnHQ | TRIP048
OCT028 | 2024-10-14 12:46 | operation@crystalgroup.in | RELIANCE | RAJEEV YADAV | 8826818750 | CPC MANAGER | CICU1799140 | FLUCTUATIONS IN TEMEPRATURE | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-14 12:48 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-REFEER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | EVP SENSOR NOT WORKING PROPERLY DUE TO ICE FORMATION INSIDE THE CONTAINER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT028 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH |  | FLUCTUATIONS IN TEMEPRATURE | 2024-10-14 12:48 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 12:49 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 12:49 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-14 12:53 | 2024-10-08 |  |  | RELIANCE |  | CICU1799140 | 10FT |  | TEMPERATURE ISSUE | Thermo king | -40 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 22b | 2010-10-10 | 399/399/399 | Short | CHECKED AND FOUND PROBE ERROR ALARM SHOWING IN DISPLAY , THEN CHECKED & FOUND EVP SENSOR NOT WORKING PROPERLY DUE TO ICE FORMATION INSIDE THE CONTAINER | CONTAINER IS RNNING IN GOOD CONDITION | NO |  |  | https://drive.google.com/open?id=179nDhm9NiCakosA6i_ZCcZ2MSO4UmOWy | TRIP048
OCT029 | 2024-10-14 12:55 | operation@crystalgroup.in | RELIANCE | RAJVEER YADAV | 8826818750 | CPC MANAGER | CXRU1045453 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-14 12:56 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | NA | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT029 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-10-14 13:00 | operation@crystalgroup.in | YES | na | na | Spares, FOC | RELIANCE | RAJPURA | CXRU1045453 | SITE | FOC | DAIKIN | 2024-10-14 13:00 | operation@crystalgroup.in | YES | NA | NA |  |  | 2024-10-14 13:00 | operation@crystalgroup.in | YES | NA | ARRENGING AT SITE | [5 empty] | 2024-10-14 13:05 | 2024-10-08 |  |  | RELIANCE | RAJPURA | CXRU1046463 |  |  | PM | Daikin | -20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 233& 1850 | 2009-09-09 | 398/398/398 | Not done | CHECKED & FOUND CONDENSOR COIL DIRTY SO CLEANED IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENT. ELECTRICAL AND MECHANICAL ALL PARTS WORKING GOOD | CONTAINER RUNNING IN GOOD CONDITION | YES |  |  | https://drive.google.com/open?id=1ezA5DCqgMALHMTGSDhwGBtk7plH3qu1D | TRIP048
OCT030 | 2024-10-14 16:25 | pravin.shinde@crystalgroup.in | Swadesh Milk | Mr Patil | NA | NA | GESU9290991 | INSTALLATION | Pushpa ma'am |  |  | Installation |  |  |  | 2024-10-14 16:51 | operation@crystalgroup.in | SWADESH MILK | GESU9290991 | 40-REFEER | NA | INSTALLATION | SALE | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT030 | Carrier | Thineline |  |  |  | Used |  | UMESH |  | INSTALLATION | 2024-10-14 16:51 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 16:52 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 16:52 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-15 11:08 | 2024-10-14 |  |  |  |  | GESU9290991 |  |  |  | Carrier | -24 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | [5 empty] | CHECKED AND FOUND INSTALLATION DONE ALL EQUIPMENT ELECTRICAL AND MECHANICAL ARE WORKING GOOD GAS PRESSURE & VOLTAGE & AMPS ARE ALSO GOOD | CONTAINER RUNNING GOOD | ISO MALE AND FEMALE PLUG REPLACED |  |  | https://drive.google.com/open?id=1ZZTH2QdT1vwbMzYzhfDciVU9H2zIEC5g | TRIP048 | No | No | Can be done on next PM | PLEASE CHANGE THE MAIN MCB 32A TO 63A
OCT031 | 2024-10-14 16:54 | operation@crystalgroup.in | Swadesh Milk | Mr. Patil | NA | NA | NYKU7932356 | INSTALLATION | PUSHPA MA'AM |  |  | Installation |  |  |  | 2024-10-14 16:55 | operation@crystalgroup.in | SWADESH MILK | NYKU7932356 | 40-REFEER | NA | INSTALLATION | SALE | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT031 | Carrier | Thineline |  |  |  | Used |  | UMESH |  | INSTALLATION | 2024-10-14 16:56 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-14 16:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-14 16:56 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-15 11:12 | 2024-10-14 |  |  |  |  | NYKU7932356 |  |  |  | Carrier | -24 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | [5 empty] | CHECKED AND FOUND INSTALLATION DONE ALL EQUIPMENT ELECTRICAL AND MECHANICAL WORKING GOD GAS PRESSURE & VOLTAGE AMP ARE ALSO GOOD` | CONTAINER RUNNING IN GOOD CONDITION | MALE AND FEMALE ISO PLUG INSTALLED |  |  | https://drive.google.com/open?id=1u8d6akgWPy73Cn2mz8bHEBjjQt9GJkpU | TRIP048 | No | No | Can be done on next PM | PLEASE CHANGE MCB 32A TO 63A ( CLIENT SIDE)
OCT032 | 2024-10-15 13:18 | operation@crystalgroup.in | Crystal | NA | NA | NA | MYRU4505847 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-15 13:24 | operation@crystalgroup.in | CRYSTAL YARD | MYRU4505847 | 40-REEFER | DAIKIN | REPAIR | STOCK | FOC | REQUIRED THESE PART FOR THIS CONTAINER | SPARE REQUEST | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT032 | Daikin | Daikin |  |  |  | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-16 11:20 | operation@crystalgroup.in | YES | OCT066 | 15.10.24 | Consumables, Spares, FOC | CRYSTAL YARD | JNPT | MYRU4505847 | DEPOT | FOC | DAIKIN | 2024-10-16 11:25 | operation@crystalgroup.in | YES | OCT066 | NA |  |  | 2024-10-16 11:26 | operation@crystalgroup.in | YES | OCT066 | ARRENGING AT SITE | [5 empty] | 2024-10-16 12:43 | 2024-10-15 |  |  |  |  | MYRU4505847 |  |  |  | Daikin | -18 | [31 empty] | REQUIRED THERE PART FOT THIS CONTAINER | NA | YES |  |  | https://drive.google.com/open?id=1CqrTZsjy4bu-TzWyiNYBg41E5IKpEGii | NA | Yes | Yes | Urgent | ARRANGE REQUESTED SPARE
OCT033 | 2024-10-15 13:20 | operation@crystalgroup.in | Crystal | NA | NA | NA | MYRU4513729 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-15 13:26 | operation@crystalgroup.in | CRYSTAL YARD | MYRU4513729 | 40-REEFER | DAIKIN | REPAIR | STOCK | FOC | REQUIED THESE PART FOR THIS CONTAINER | REQUEST FOR SPARE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT033 | Daikin | Daikin |  |  |  | Refurbished |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-16 11:22 | operation@crystalgroup.in | YES | OCT067 | 15.10.2024 | Consumables, Spares, FOC | CRYSTAL YARD | JNPT | MYRU4513729 | DEPOT | FOC | DAIKIN | 2024-10-16 11:26 | operation@crystalgroup.in | YES | OCT067 | NA |  |  | 2024-10-16 11:27 | operation@crystalgroup.in | YES | OCT067 | ARRENGING AT SITE | [5 empty] | 2024-10-16 12:45 | 2024-10-15 |  |  |  |  | MYRU4513729 |  |  |  | Daikin | -25 | [31 empty] | REQUEST THESE PART FOR THIS CONTAINER | NA | YES |  |  | https://drive.google.com/open?id=1-8DeIRfMA9OtKMQ7SJKicTh-F1VSRJ93 | NA | Yes | Yes | Urgent | ARRANGEMENT OF SPARE
OCT034 | 2024-10-16 11:01 | operation@crystalgroup.in | AMUL GOREGAON MUMBAI | SUJIT | 8291259886 | BCAL WEST MUMBAI | CXRU1056669 | BREAKDOWN (SHOCK ON CONTAINER BODY | PRAVIN |  |  | Complete Breakdown |  |  |  | 2024-10-16 11:06 | operation@crystalgroup.in | AMUL | CXRU1056669 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION | SHORT PTI PASS | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT034 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | MUKESH |  | BREAKDOWN (SHOCK ON CONTAINER BODY | 2024-10-16 11:23 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-16 11:26 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-16 11:27 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-16 12:49 | 2024-10-15 |  |  |  |  | CXRU1056669 |  |  |  | Daikin | 4 | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35PSI & 270 PSI | 2010-10-10 | 410/410/410 | Short | CHECKED AND FOUND CONTAINER RUNNING GOOD CONDITION | SHORT PTI PASS | NO |  |  | https://drive.google.com/open?id=1z0e-zo2EYwoCitdwS_4jbxVxRNTORnzh | NA | No | No | Can be done on next PM | NA
OCT035 | 2024-10-16 11:04 | operation@crystalgroup.in | AMUL GOREGAON MUMBAI | SUJIT SANGLE | 8291259886 | BCAL | GESU9440129 | BREAKDOWN ( SHOCK ON CONTAINER BODY) | PRAVIN |  |  | Complete Breakdown |  |  |  | 2024-10-16 11:08 | operation@crystalgroup.in | AMUL | GESU9440129 | 40-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTROLLER D/F NEED TO REPLACE REVERSE PHASE CONNECTION DUE TO THE REVERSE PHASE CONNECTION THE CONTAINER CONTROLLER IS DAMAGED AND NOT WORKING | NEED TO REPLACE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT035 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | MUKESH |  | BREAKDOWN ( SHOCK ON CONTAINER BODY) | 2024-10-16 11:59 | operation@crystalgroup.in | YES | OCT068 | 16.10.2024 | Spares | AMUL | GOREGAON | GESU9440129 | SITE | FOC | CARRIER-PRIMLINE | 2024-10-16 12:03 | operation@crystalgroup.in | YES | OCT068 | NA |  |  | 2024-10-16 12:03 | operation@crystalgroup.in | YES | OCT068 | ARRENGING AT SITE | [5 empty] | 2024-10-16 12:52 | 2024-10-15 |  |  |  |  | GESU9440129 |  |  |  | Carrier | --- | Dirty | Clean | [29 empty] | CHECKED AND FOUND CONTROLLER D/F NEED TO REPLACE REVERSE PHASE COLLECTION DUE TO THE REVERSE PHASE CONNECTION THE CONTAINER IS DAMAGED AND NOT WORKING | NA | YES |  |  | https://drive.google.com/open?id=1_yD_H2IN77ppkc3YwrWPWS-w_K1sNz5_ | NA | Yes | Yes | Urgent | ARRNGE SPARE AND REPLACE
OCT036 | 2024-10-16 15:11 | operation@crystalgroup.in | RELIANCE | VEER SINGH | 9813816264 | MST | TRIU6618391 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-16 15:17 | operation@crystalgroup.in | RELIANCE | TRIU6618391 | 20-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER BREAKDOWN AL26 GAS PRESSURE 16 THEN CHECKED AND FOUND FILTER CHOKE AND SENSOR FAULTY | NEED TO REPLACE/REPAIR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT036 | Carrier - Thinline | Thinline |  |  |  | Used |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-11-25 13:41 | operation@crystalgroup.in | YES | NOV045 | 16.10.24 | Spares, FOC | RELIANCE | KUMASHPUR | TRIU6618391 | SITE | FOC | CARRIER-THINLINE | 2024-11-25 13:45 | operation@crystalgroup.in | YES | NOV045 | YES |  |  | 2024-11-25 13:45 | operation@crystalgroup.in | YES | NOV045 | COURIER | [5 empty] | 2024-11-25 13:52 | 2024-11-16 |  |  |  |  | TRIU6618391 |  |  |  | Carrier | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | [5 empty] | CHECKED AND FOUND CONTAINER BREAKDOWN AL26 ALARM, CEHCKED AND FOUND SENSOR AND FILTER CHOKED/ FAULTY | CONTAINER RUNNING IN GOOD CONDITION | YES |  |  | https://drive.google.com/open?id=1Klqo9Ml_hgrvpLJcQtKROYMu33lH8Je9 | NA | Yes | No | Can be done on next PM | SENSORS
OCT037 | 2024-10-16 15:14 | operation@crystalgroup.in | RELIANCE | VEER SINGH | 9813816264 | MST | CICU2779914 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-16 15:32 | operation@crystalgroup.in | RELIANCE | CICU2779914 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED & FOUND CONDENSOR COIL VERY DIRTY SO CLEANED IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENTS ALL WORKING GOOD | CONTAINER IS RUNNING GOOD | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT037 | Thermoking | Magnum Plus | E0GM030254 | ABC782800322010282 |  | BrandNew |  | RAMIZ |  | PREVENTIVE MAINTENANCE | 2024-11-25 12:48 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-25 12:49 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-25 12:49 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-25 12:54 | 2024-10-16 |  |  |  |  | CICU2779914 |  |  |  | Carrier | [32 empty] | CHECKED & FOUND CONDENSOR COIL VERY DIRTY SO CLEANED IT PROPERLY WITH WATER AND CHECKED OTHER EQUIPMENTS ALL WORKING GOOD | CONTAINER IS RUNNING GOOD | NO |  |  |  | NA | No | No | Can be done on next PM | NA
OCT038 | 2024-10-18 16:55 | operation@crystalgroup.in | CSIR PILANI RAJASTHAN | NARTAKSINGH | 7891661366 | INCHARGE | MORU0322200 | MOTOR RUNNING IN REVERSE | PUSHPA MA'AM |  |  | Running with issues |  |  |  | 2024-11-21 11:42 | service@crystalgroup.in | CSIRPILANI | MORU0322200 | 20FT | CARRIER | SERVICE-ON CALL | SALE | FOC | EVP FAN MOTOR DEFECTIVE | REPLACED EVP FAM MOTOR | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT038 | Thermoking MP-3000 | MP 3000 |  |  |  | Used | JSGA623040313 | VIRENDRA | No | MOTOR RUNNING IN REVERSE | 2024-12-31 18:05 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:05 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-14 15:30 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
NOV031 | 2024-11-15 12:49 | operation@crystalgroup.in | Dr Reddy CTO5 | SRIRAM TEJA | 7036305829 | SR ENGINEER | CXRU1045896 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-15 12:58 | operation@crystalgroup.in | DR REDDY CTO 5 | CXRU1045896 | 40-REEFER | DAAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV031 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-15 14:35 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-15 14:43 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-15 14:44 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-14 16:43 | 2024-11-14 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | + 4 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/190 PSIG | 9.9/9.8/9.9 | 410/411/411 | Short | UNIT WORKIN AS SATISFACTORY | NA | NO |  |  | https://drive.google.com/open?id=1enqKZ3-GZAopuwb0duEOSdLrzlzavQQI , https://drive.google.com/open?id=10Si8PpzsFI8Z5K7CIVBNSt_djGRB5_od | TRIP054 | No | No | Can be done on next PM | NA
NOV032 | 2024-11-15 12:51 | operation@crystalgroup.in | Dr Reddy CTO5 | SRIRAM TEJA | 7036305829 | SR ENGINEER | CXRU1032564 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-15 13:22 | operation@crystalgroup.in | DR REDDY CTO 05 | CXRU1032564 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV032 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-15 14:43 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-15 14:43 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-15 14:44 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-14 20:56 | 2024-11-14 |  |  |  |  | CXRU1032564 |  |  |  | Daikin | + 20 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/180 | 9.8/9.9/9.8 | 410/410/410 | Short | UNIT WORKINGAS FINE AND MIANITING SET TEMP. | NO | NO |  |  | https://drive.google.com/open?id=1SHH0SYoAv_OgUDzCp1rC0mR5LuHI_WfB , https://drive.google.com/open?id=1WJDwplNB0YJXrnaraoXBqMfjiUa4aK8O | TRIP054 | No | No | Can be done on next PM | NO
NOV033 | 2024-11-15 12:53 | operation@crystalgroup.in | Dr Reddy CTO5 | SRIRAM TEJA | 7036305829 | SR ENGINEER | GSOU6384153 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-15 13:24 | operation@crystalgroup.in | DR REDDY CTO 05 | GSOU6384153 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV033 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-15 14:43 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-15 14:43 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-15 14:44 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-14 21:05 | 2024-11-13 |  |  |  |  | GSOU6384153 |  |  |  | Carrier | + 20 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190 | 12.8/12.9/12.8 | 410/410/410 | Short | UNIT MAINTAINING TEMP. AND WORKING WITH NO ALARM | SERVICE EVP MOTOR AND RE ARRANGE ELECTRICAL PANEL WIRING | NO |  |  | https://drive.google.com/open?id=11nnBVLLMpQsqzB7SXX8VHNJJ6uEqsO-3 , https://drive.google.com/open?id=1qXa_dblNi-zHcWO57Z6wClSOePoAGaCt | TRIP054 | No | No | Can be done on next PM | NA
OCT039 | 2024-10-18 17:12 | operation@crystalgroup.in | BPCL | SREEKANTH | 9446898214 | SR MANAGER | CXRU1043337 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-18 17:21 | operation@crystalgroup.in | BPCL | CXRU1043337 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DAY 1 TEMP ISSUE & EVP LEAK- UNIT REPLACE DAY 2 CONTAINER HOLE UNIT REPLACED | UNIT REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT039 | DAikin | LXE10E147F2 | M002030 | K31405126348 | DECOS 3F 2353 / 1 | used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-10-18 17:22 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-18 17:22 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-18 17:22 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-18 17:30 | 2024-10-17 |  |  |  |  | CXRU1043337 |  |  |  | Daikin | 15 | [31 empty] | DAY 1 TEMPERATURE ISSUE FOUND FOUND DAIKIN UNIT EVAPORATOR COIL INTERNAL LEAKING DAY 2 UNIT CANABALIZED FIXED CARRIER THINLINE ENIT | DAY 1 REMOVED HOLE UNIT FROM CONTAINER FIXING GOOD ONE CARRIER THIN LINE UNIT INSTALLATION DONE DAY 2 FIXED SILLICON SEALANT TO UNIT LEAK TOST FIXED & REPAIR KICK PLATE INSIDE DOORFAN UNIT OPERATION CHECKED ALL PARAMETER & FOUND SATISFACTORY & HANDED OVER TO OPERATIOM | NO |  |  | https://drive.google.com/open?id=17Ajoo_zfNIQyqzld0eEzys5_YTC5mVA3 | TRIP052 | No | No | Can be done on next PM | NA
OCT040 | 2024-10-21 11:07 | operation@crystalgroup.in | UCT | NA | NA | NA | TRIU6617353 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-21 11:13 | operation@crystalgroup.in | UCT | TRIU6617353 | 20-REEFER | CARRIER | SERVICE-AT SITE | STOCK | FOC | NA | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT040 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-21 11:14 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-21 11:14 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-21 11:14 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-21 11:27 | 2024-10-20 |  |  |  |  | TRIU6617353 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 17.1b | 9.3/9/9.1 | 420/417/419 | Full | na | we have replace evp motor 2 nos, 12A contactor 3 nos , 30 A contactor 1 nos , filter drier 1 nos , keypad 1 nos, display 1 nos | no |  |  | https://drive.google.com/open?id=17s2cG5sYeyjnjnx0mutHqwImbKgF9jQ1 | TRIP053 | No | No | Can be done on next PM | na
OCT041 | 2024-10-21 11:09 | operation@crystalgroup.in | UCT | NA | NA | NA | MWCU5709930 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-10-21 11:31 | operation@crystalgroup.in | UCT | MWCU5709930 | 20-REEFER | CARRIER | SERVICE-AT SITE | STOCK | FOC | CONTROLLER NEED CONFIGER THREW SOFTWARE CONDENSOR MOTOR NOT REPLACE DUE TO BLADE NOT OPENING | WE HAVE REPLACE LIS EVP MOTOR CONTROLLER , DISPLAY AND HUMIDITY SENSOR FIX DUE TO MISSING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT041 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-10-21 11:53 | operation@crystalgroup.in | YES | OCT073 | 2024-10-21 | Consumables, Spares, FOC | UCT | CHENNAI | MWCU5709930 | DEPOT | FOC | CARRIER-THINLINE | 2024-10-21 11:54 | operation@crystalgroup.in | YES | OCT073 | NA |  |  | 2024-10-21 11:54 | operation@crystalgroup.in | YES | OCT073 | ARRENGING AT SITE | [5 empty] | 2024-10-21 11:58 | 2024-10-20 |  |  |  |  | MWCU5709930 |  |  |  | Carrier | [32 empty] | CONTAINER NEED CONFIGURATION THREW SOFTWARE CONDENSOR MOTOR NOT REPLACE DUE TO BLADE NOT OPENONG | WE HAVE REPLACE L/S EVAPORATOR MOTOR CONTROLLER DISPLAY AND HUMIDITY SENSOR FIX DUE TO MISSING | YES |  |  | https://drive.google.com/open?id=16p2KrAqRGzYRuPkvs3mBkgl6Ym4N3XWe | TRIP053 | Yes | Yes | Can be done on next PM | REPAIR WORK
OCT042 | 2024-10-22 09:50 | operation@crystalgroup.in | APL Health Care | S. RAJESH | AST. MANAGER | 9553485038 | TITU9230954 | SERVICE CALL ( COMPRESSOR INSTALLATION) | PRAVIN |  |  | Installation |  |  |  | 2024-10-22 09:54 | operation@crystalgroup.in | APL HEALTH CARE | TITU9230954 | 40-REEFER | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | COMPRESSOR REPLACE REQUEST | COMPRESSOR REPLACED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT042 | [7 empty] | VIRENDRA |  | SERVICE CALL ( COMPRESSOR INSTALLATION) | 2024-10-22 09:54 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-22 09:55 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-22 09:55 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-22 10:01 | 2024-10-21 |  |  |  |  | TITU9230954 |  |  |  | Daikin | 5,0 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 170KPA & 1800KPA | 8.9A/9.0A/9.1A | 415V/411V/413V | Not done | NA | WE HAVE REPLACE COMPRESSOR N2 TEST, VACCUME AND GASS REFULL 4 KG CONTAINER RUN IN SOUNF CONDITION WITHOUT ANY ALARM PRESENT TEMP MAINTAIN +5.0 C | NO |  |  | https://drive.google.com/open?id=13CNUM_EyDUKjiMLdjbvDS96ilFCuLAF_ | TRIP053 | No | No | Can be done on next PM | NO
OCT043 | 2024-10-23 16:00 | operation@crystalgroup.in | ITC Ltd | NA | NA | NA | MYRU4519748 | SERVICE CALL | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-23 16:07 | operation@crystalgroup.in | ITC | MYRU4519748 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | WE HAVE REPLACE R/S EVP MOTOR, FILTER DRIER, R134a REFULL 900gm AND DAMPER SHEET APPLY 3MTR IN TOP ROOF CONTAINER RUNNING IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT043 | Daikin | Daikin | M003143 | LXE10E136A |  | Used | JSGA623040176 | VIRENDRA |  | SERVICE CALL | 2024-10-23 16:14 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-23 16:15 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-23 16:16 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-23 16:22 | 2024-10-22 |  |  |  |  | MYRU4519748 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 140KPA & 1600KPA | 8.7A/8.9A/9.0A | 413V/410V/411V | Not done | NA | WE HAVE REPLACED RIGHT SIDE EVP MOTOR FILTER DRIER REPLACE, R134a REFULL 900gm AND DAMPER SHEET APPLY 3MTR IN TOP CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NA |  |  | https://drive.google.com/open?id=15HxRFjGy-D3UYOl01WTi3bnHDlq8-qSn | TRIP053 | No | No | Can be done on next PM | NEED ROOF PROPER WORK OLD PATCH
OCT044 | 2024-10-23 16:02 | operation@crystalgroup.in | ITC Ltd | NA | NA | NA | PCIU6003244 | SERVICE CALL | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-23 16:09 | operation@crystalgroup.in | ITC | PCIU6003244 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | NA | WE HAVE REPLACE R/S EVP MOTOR AND FILTER DRIER REPLACE CONTAINER RUNNING IN SOUND CONDITION WITHOUT ANY ALARM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT044 | Daikin |  |  |  |  | used |  | VIRENDRA |  | SERVICE CALL | 2024-10-23 16:15 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-23 16:16 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-23 16:16 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-23 16:28 | 2024-10-23 |  |  |  |  | PCIU6003244 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | 9.8A/9.3A/9.5A | 415V/411V/413V | Not done | NA | WE HAVE REPLACE RIGHT SIDE EVAPORATOR MOTOR AND FILTER DRIER REPLACE CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://drive.google.com/open?id=1Km9QZZlxAlEgQVE3UL3JXmV3Hc-y56GJ | TRIP053 | No | No | Can be done on next PM | NA
OCT045 | 2024-10-23 17:42 | operation@crystalgroup.in | TIPTOP ENTERPRISES | NIRAV | 8082455555 | OPERATION MANAGER | CICU3876570 | INSTALLATION | PRAVIN |  |  | Installation |  |  |  | 2024-10-23 17:50 | operation@crystalgroup.in | TIPTOP PLAZA | CICU3876570 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER PLACED IN LOCATION SO DONE THE INSTALLATION AND CHECKED AFTER EQUIPMENTS ALL WORKING GOOD THEN CHECKED GAS MOTOR & COMPRESSOR ALLL WORKING GOOD | CONTAINER WORKING IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT045 | Thermoking | Magnum + | 22A8578JT | ABC782800322010281 | ABC782900321510326 | Brand New |  | UMESH |  | INSTALLATION | 2024-10-23 17:54 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-23 17:54 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-23 17:57 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-23 18:04 | 2024-10-23 |  |  |  |  | CICU3876570 |  |  |  | Thermo king | -15 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done |  |  | - & 23.4 | 10A/10A/10A | 399V/399V/399V | Not done | CHECKED AND FOUND CONTAINER PLACED IN LOCATION SO DONE THE INSTALLATION AND CHECKED AFTER EQUIPMENTS ALL WORKING GOOD THEN CHECKED GAS MOTOR & COMPRESSOR ALLL WORKING GOOD | CONTAINER WORKING IN GOOD CONDITION | NO |  |  | https://drive.google.com/open?id=15rFgp2Az82AFefxRDvCj2bpaHvC2eNfh | NA | No | No | Can be done on next PM | NA
OCT046 | 2024-10-23 17:46 | operation@crystalgroup.in | TIPTOP PLAZA | NIRAV | 8082455555 | OPERATION MANAGER | CICU3876565 | INSTALLATION | PRAVIN |  |  | Installation |  |  |  | 2024-10-23 17:53 | operation@crystalgroup.in | TIPTOP PLAZA | CICU3876565 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | CHECKED AND FOUND CONTAINER PLACED IN LOCATION AND INSTALLATION & CHECKED ALL EQUIPMENTS THEN CHECKED MOTOR AND COMPRESSOR ALL WORKING GOOD | CONTAINER RUNNING IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT046 | Thermoking | Magnum + | 22A4218AT | ABC782800322010051 | ABC782900321510023 | Brand New |  | UMESH |  | INSTALLATION | 2024-10-23 17:54 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-23 17:55 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-23 17:56 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-23 18:07 | 2024-10-23 |  |  |  |  | CICU3876565 |  |  |  | Thermo king | -15 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 24 | 11A/11A/11A | 400V/400V/400V | Not done | CHECKED AND FOUND CONTAINER PLACED IN LOCATION AND INSTALLATION & CHECKED ALL EQUIPMENTS THEN CHECKED MOTOR AND COMPRESSOR ALL WORKING GOOD | CONTAINER RUNNING IN GOOD CONDITION | NO |  |  | https://drive.google.com/open?id=1rvmVRuYI0YXm4YAftvadaYxMR7erKJH1 | NA | No | No | Can be done on next PM | NO
OCT047 | 2024-10-24 15:12 | operation@crystalgroup.in | Crystal | SANDEEP | - | YARD INCHARGE | CGMU2988654 | PREPARING CONTAINER FOR DISPATCH | PUSHPA MA'AM |  |  | Preventive Maintenance |  |  |  | 2024-10-24 15:26 | operation@crystalgroup.in | CRYSTAL | CGMU2988654 | 10-REEFER | CARRIER THINLINE | MACHINE INSPECTION | STOCK | FOC | CARRIER THINLINE UNIT CHECKED & FOUND COMPRESSOR INTERNAL NOISY & HOW PUMPING NOT FIT FOR -20 DEGREE C TO -25 DEGREE C COMPRESSOR OIL BLACK & DIRTY. NEED TO FLASH OUT SYSTEM WITH NITROGEN | IF RELEASE FOR MINUS CARGO NOT FIT -20. WE USED ONLY CHILLED PLUSE CARGO | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT047 | Carrier - Thinline | Thinline | 2907L50458 | LSM60197481 |  | Used |  | SHAHBUDDIN |  | PREPARING CONTAINER FOR DISPATCH | 2024-10-24 16:19 | operation@crystalgroup.in | YES | OCT081 | 24.10.24 | Consumables, Spares, FOC | CRYSTAL | JNPT | CGMU2988654 | DEPOT | FOC | CARRIER-THINLINE | 2024-11-25 10:57 | operation@crystalgroup.in | YES | NOV049 | NA |  |  | 2024-11-25 10:58 | operation@crystalgroup.in | YES | NOV049 | ARRENGING AT SITE | [5 empty] | 2024-11-25 11:03 | 2024-10-24 |  |  |  |  | CGMU2988654 |  |  |  | Carrier |  | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | [5 empty] | CARRIER THINLINE UNIT CLEANED AND FOUND COMPRESSOR INTERNALLY NOISY & NOT FIT FOR -20 TO -21 DEGREE C, COMPRESSOR OIL BLACK AND DIRTY NEED TO FLASHOUT SYSTEM WITH NITROGEN | ONLY USE FOR PLUS TEMPERATURE NOT INUS | YES |  |  | https://drive.google.com/open?id=1dbwRhpDLZRuvtz7dgWrbNXqZHnKfsNq2 | NA | Yes | No | Can be done on next PM | SPARES
OCT048 | 2024-10-25 15:16 | pushpa.shetty@crystalgroup.in | GCMMF | Santosh | 9323395541 | Warehouse | CXRU 1056669 | CONTAINER NOT WORKING | Pushpa |  |  | Running with issues |  |  |  | 2024-10-29 10:09 | operation@crystalgroup.in | GCMMF | CXRU1056669 | 40-REEFER | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | MAIN MCB IS 32A AND ITS TRIPPED | NEED TO CHANGE MAIN CONTACTOR. CURRENT COMPONENT IS 32A AND WE REQUIRED MINIMUM 50A . NOT ABLE TO CHECK IN DETAIL BECAUSE NO POWER CONNECTION SUPPLY PROPER | -NA- |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT048 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | PRAVIN, UMESH |  | CONTAINER NOT WORKING | 2024-10-29 10:24 | operation@crystalgroup.in | NO | [9 empty] | 2024-10-29 10:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-10-29 10:30 | operation@crystalgroup.in | NO | [7 empty] | 2024-10-29 10:39 | 2024-10-28 |  |  |  |  | CXRU1056669 |  |  |  | Daikin | NA | [31 empty] | MAIN MCB IS 32A AND ITS TRIPPING | NEED TO CHANGE MAIN CONTACTOR CURRENT COMPONENT IS 32A AND WE REQUIRED MINIMUM 50A NOT ABLE TO CHECK IN DETAIL BECAUSE NO POWER CONNECTION SUPPLY | NO |  |  | https://drive.google.com/open?id=1yfFknK_IVEIeT5WZLF4UxkKkF2iRucVy | NA | No | No | Can be done on next PM | CLIENT NEED TO CHANGE MCB
OCT050 | 2024-10-28 18:11 | operation@crystalgroup.in | lands flavour | RAMIZ | 88281 29970 | TECHNICIAN | TRIU6616594 | TEMP NOT GOING BELOW -12 DEGREE | RAMIZ |  |  | Running with issues |  |  |  | 2024-10-29 12:07 | operation@crystalgroup.in | LANDS FLAVOUR | TIRU6616594 | 40-REEFER | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLDOWN | NEED TO REPLACE SUPPLY SENSOR AND DEFROST SENSOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT050 | [7 empty] | NA | No | TEMP NOT GOING BELOW -12 DEGREE | 2024-10-29 12:38 | operation@crystalgroup.in | YES | OCT085 | 29.10.24 | Spares, FOC | LANDS FLAVOURS | BANGLORE | TRIU6616594 | SITE | FOC | CARRIER-THINLINE | 2024-12-31 14:48 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-31 14:49 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
OCT049 | 2024-10-29 10:05 | operation@crystalgroup.in | GCMMF | Santosh | 9323395541 | Warehouse | GESU9440129 | MACHINE SHUT DOWN | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-29 10:15 | operation@crystalgroup.in | GCMMF | GESU9440129 | 40-REEFER | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | MAIN MCB IS 32A | WE FOUND THAT MAIN POWER SUPPLY CONNECTION IS WRONG PHASE CONNECTION IS NEUTRAL BECAUSE OF THIS CONNECTION MACHINES CONTROLLER IS DAMAGED & NOT WORKING NEED TO CHANGE MAIN CONTACTOR ALSO EXISTING IS 32A WE REQUIRED 50 A MINIMUM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT049 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ | No | MACHINE SHUT DOWN | 2024-11-25 15:06 | operation@crystalgroup.in | YES | NOV044 | 16.10.24 | Spares, FOC | GCMMF | GOREGAON | GESU9440129 | SITE | FOC | CARRIER-THINLINE | 2025-01-17 19:32 | operation@crystalgroup.in | YES | JAN018 | NA |  |  | 2025-01-22 11:44 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
OCT051 | 2024-10-30 09:58 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | Manager | APRU5091340 | COMPRESSOR MAKING NOISE | PRAVIN |  |  | Running with issues |  |  |  | 2024-10-30 10:02 | operation@crystalgroup.in | LAURUS UNIT 3 | APRU5091340 | 40-REEFER | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND COMPRESSOR HEAVY BUBBLING DUE TO COMPRESSOR CONTACTING ROD BROKEN NEED TO REPLACE | WE SUGGEST TO REPLACE CONTAINER IN THIS SITE CONDENSOR COIL LEAKKEGE DUE TO COMPRESSOR BUBBLING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT051 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA |  | COMPRESSOR MAKING NOISE | 2024-11-07 16:55 | operation@crystalgroup.in | YES | NOV006 | 07.11.24 | Spares, FOC | LAURUS UNIT 3 | PARWADA | APRU5091340 | SITE | FOC | CARRIER-THINLINE | 2024-11-25 11:09 | operation@crystalgroup.in | YES | NOV006 | YES |  |  | 2024-11-25 11:10 | operation@crystalgroup.in | YES | NOV006 | TECHNICIAN | [5 empty] | 2024-11-25 11:16 | 2024-10-30 |  |  |  |  | APRU5091340 |  |  |  | Carrier | [33 empty] | UNIT REPLACE | UNIT REPLACE |  |  |  | NA | Yes | Yes | Urgent | UNIT REPLACE
NOV001 | 2024-11-01 13:13 | sushma.poojari@crystalgroup.in | DSV Solutions Pvt Ltd | Somnath Shewale | 8309780641 | Manager Operations | TITU8258978 | FLUCTUATIONS IN TEMEPRATURE | Sushma Poojari |  |  | Running with issues |  |  |  | 2024-11-04 15:34 | operation@crystalgroup.in | DSV | TITU8258978 | 20-REEFER | TK-MP4000 | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | COMPRESSOR CONTACTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV001 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN |  | FLUCTUATIONS IN TEMEPRATURE | 2024-11-04 16:56 | operation@crystalgroup.in | YES | NOV001 | 04.11.24 | Spares, FOC | DSV Air & Sea Pvt. Ltd. | HYDERABAD | TITU8258978 | SITE | FOC | TK-MP4000 | 2024-11-04 16:55 | operation@crystalgroup.in | YES | NOV001 | NO |  |  | 2024-11-04 16:54 | operation@crystalgroup.in | YES | NOV001 | ARRENGING AT SITE | [5 empty] | 2024-11-04 16:52 | 2024-11-03 |  |  |  |  | TITU8258978 |  |  |  | Thermo king | -35 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  |  | 401/402/401 | Not done | UNIT NOT WORKING | CHECKED AND FOUND CMPRESSOR CONTACTOR BURNED OUT SETUP NEED TO REPLACE AFTER REPLACED RUN UNIT NEED TO FURTHR CHECK FAULT | YES |  |  | https://drive.google.com/open?id=1JPlly3EhRa6HMFE3YS923eArq-goy3Eo | TRIP054 | Yes | No | Urgent | REPLACEMENT
NOV005 | 2024-11-04 15:02 | viru0068@gmail.com | Navin Fluorine | Ketan | 6357662623 | N/a | CCLU1031878 | MACHINE SHUT DOWN | Sandeep /Virender Kumar |  |  | Running with issues |  |  |  | 2024-11-06 18:33 | operation@crystalgroup.in | NAVIN FLORINE | CCLU1031878 | 20-REEFER | CARRIER THINELINE | SERVICE-AT SITE | LEASE | FOC | WE HAVE ATTAND THIS UNIT AND FOUND FILTER DRIER CHOWK COMPRESSOR OVERHEATING AND CONDENSOR COIL HEAVY DIRTY TO WORK R/S EVP MOTOR HEAVY NOISE | WE HAVE REPLACE FILTER DRIER GAS REFILL 3KG CONDENSOR MOTOR REPLACE R/S EVP MOTOR REPLACE CONDENSOR COIL WASH WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV005 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA |  | MACHINE SHUT DOWN | 2024-11-07 15:38 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-07 09:49 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 09:50 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 10:02 | 2024-11-06 |  |  |  |  | CCLU1031878 |  |  |  | Carrier | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - & 16.0B | 14.0A/13.7A/13.9A | 420V/415V/417V | Short | WE HAVE ATTEND THIS UNIT AND FOUND FILTER DRIER CHOWK COMPRESSOR OVER HEATED AND CONDENSOR COIL HEAVY DIRTY TO WORK R/S EVP MOTOR HEAVY NOISE | WE HAVE REPLACE FILTER DRIER , GAS REFIL 3 KG, CONDENSOR MOTOR REPLACE R/S EVP MOTOR REPLACE CONDENSOR COIL WASH WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://drive.google.com/open?id=1KuN--SQFsol4Vpa76_CDdE-18cllPjPd | TRIP055 | No | No | Can be done on next PM | NA
NOV002 | 2024-11-04 15:16 | operation@crystalgroup.in | QUICK SUPPLY RELIANCE | SATISH | 91825 61332 | NA | CICU2779920 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-04 15:39 | operation@crystalgroup.in | QUICK SUPPLY RELIANCE | CICU2779920 | 10-REFEER | THERMOKING MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENRAL CHECKUP | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV002 | Thermoking | Magnum Plus | E0GM030270 | ABC782800322010477 |  | BrandNew |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-04 15:57 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-04 15:59 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-04 16:00 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-04 16:09 | 2024-11-01 |  |  |  |  | CICU2779920 |  |  |  | Thermo king | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 & 18 BAR | 9.9/9.8/9.9 | 405/405/405 | Short | PM SERVICE & GENRAL INSPECTION | UNIT CHECKED OPERATION, MAIN VOLTAGE, ALL MOTOR AMP & ROTATION ALL SENSOR RADING & PARAMETERS SENSOR CONNECTOR PRESSURE CLEAN AND CONDENSOR COIL UNIT PERFORM TEST AND PASS ALL DRIER UNIT WORKING GOOD CONDITION | NO |  |  | https://drive.google.com/open?id=16JYQ-DsviOcH6X1f0AARnfggvYrAW4yn | TRIP054 | No | No | Can be done on next PM | NA
NOV003 | 2024-11-04 15:25 | operation@crystalgroup.in | Zenfold Pharma | K. SUNIL. KUMAR | DY. MANAGER | 8008332277 | TRIU6618637 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-04 15:46 | operation@crystalgroup.in | ZENFOLD PHARMA | TRIU6618637 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM / REPLACEMENT PARTS | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV003 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040284 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-04 15:58 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-04 15:59 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-04 16:00 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-04 16:17 | 2024-11-02 |  |  |  |  | TRIU6618637 |  |  |  | Carrier |  | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 & 180 | 12.3/12.4/13.3 | 405/406/405 | Short | PM & GENRAL INSPECTITON DISPLAY FOR REPLACEMENT COMPRESSOR OUT ADDING | REPLACE DISPLAY ADDED OIL 1/2 LTR FOR COMPRESSOR RUN UNIT CHECKED OPERATION FOUND WORKING AS NORMAL CHECKED VOLTAGE/ AMP. ALL MOTOR ROTATION GAS LEVEL ALL PARAMETER PERFORM UNIT SHORT PAS WITH NO ALARM | NO |  |  | https://drive.google.com/open?id=1UJqot3qrOfS5zETpK6aat6IY8rcLhMwd | TRIP054 | No | No | Can be done on next PM | NO
NOV004 | 2024-11-04 15:27 | operation@crystalgroup.in | BIOCON | PRASAD | 9985339501 | NA | TDRU5800414 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-04 15:48 | operation@crystalgroup.in | BIOCON | TDRU5800414 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM / GENRAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV004 | Daikin | Daikin | A001807 | LVE10EA36A |  | Refurbished | JSGA623040182 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-04 15:58 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-04 15:59 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-04 16:01 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-04 16:35 | 2024-11-02 |  |  |  |  | TDRU5800414 |  |  |  | Daikin | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 & 190 | 9.2/9.3/9.4 | 412/413/412 | Short | PM & GENRAL INSPECTION SENSORS FOR REPLACEMENT | UNIT RUN & CHECKED OPERATION MAIN VOLTAGE ALL MOTOR AMP ROTATION CHECKED AND REPALCE DISCHARGE SENSOR REQUIRED SUCTION GAS SENSOR ETS SENSOR UNIT OBSERVE FOUND NO ALARM UNIT PERFORM SHORT PTI AND COMPRESSOR STILL RUNNING SHORT PTI PASS NO ALARM NOTE :- RECOMMEND TO KEP GAP FRONT BOTTOM AND BOTTOM INSIDE FOR PROPER AIR CIRCULATION | NO |  |  | https://drive.google.com/open?id=1V-qtCQoS1XECclyFiC_6-45gxNWIsacH | TRIP054 | No | No | Can be done on next PM | NO
NOV006 | 2024-11-04 18:22 | operation@crystalgroup.in | SOFT BOX | Satish Kondapalli | 8977711235 | NA | GRMU3707470 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-05 14:16 | operation@crystalgroup.in | SOFTBOX | GRMU3707470 | 20-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | IOT INSTALLATION DONE, DISPLAY PATCH/BLUR | NEED TO REPLACE DISPLAY | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV006 | Daikin |  |  |  |  | used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-07 10:05 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-07 10:05 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 10:05 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 10:13 | 2024-11-04 |  |  |  |  | GRMU3707470 |  |  |  | Daikin | -21 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 & 180 | 9.8/9.9/9.8 | 406/405/406 | Short | IOT INSTALATION ONLY GENERAL CHECKUP | IOT INSTALLATION DONE RUN UNIT CHILLED OPERATION VOLTAGE ALL SENSOR READING & PARAMETERS GASS LEVELS UNIT WORKING AS SATISFACTORY IOT INSTALLATION & CONNECTED TO SYSTEM | NA |  |  | https://drive.google.com/open?id=1nXJg095n__LgqlSIqGxQ4nThF6vZUrK4 | TRIP054 | No | No | Can be done on next PM | NA
NOV007 | 2024-11-04 18:24 | operation@crystalgroup.in | SOFTBOX | Satish Kondapalli | 8977711235 | NA | TITU8257288 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-05 14:18 | operation@crystalgroup.in | SOFTBOX | TITU8257288 | 20-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | IOT INSTALLATION DONE, DISPLAY PATCH/BLUR | NEED TO REPLACE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV007 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-07 10:15 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-07 10:16 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 10:16 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 10:21 | 2024-11-04 |  |  |  |  | TITU8257288 |  |  |  | Thermo king | -25 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 & 19 | 9.9/9.8/9.0 | 406/407/406 | Short | IOT INSTALLATION ONLY | IOT INSTALLATION DONE CHECKED & RUN UNIT OPERATIONAL FOUND WORKING AS NORMAL CHECKED SENSOR VALVE PARAMETRS AND GAS LEVEL IOT INSTALLATION CONNECTED UNIT WORKING AS FINE | NA |  |  | https://drive.google.com/open?id=1MdmSX0IgkW6bRAA0O0Q4n2YV-5i53rzc | TRIP054 | No | No | Can be done on next PM | NA
NOV008 | 2024-11-06 09:20 | operation@crystalgroup.in | DSV LOGISTIC | SAGAR | 9030909007 | ASSOCIATE | TITU8258978 | CONTACTOR INSTALLATION | PRAVIN |  |  | Installation |  |  |  | 2024-11-06 09:47 | operation@crystalgroup.in | DSV | TITU8258978 | 20-REEFER | THERMOKING MP4000 | REPAIR | LEASE | FOC | UNIT NOT WORKING | REPLACED COMPRESSOR CONTACTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV008 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN |  | CONTACTOR INSTALLATION | 2025-02-04 10:06 | operation@crystalgroup.in | YES | NOV100 | 2024-11-25 | Spares, FOC | DSV Air & Sea Pvt. Ltd. | Hyderabad | TITU8258978 | SITE | FOC | TK-MP4000 | 2024-11-07 10:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 10:30 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 10:37 | 2024-11-05 |  |  |  |  | TITU8258978 |  |  |  | Thermo king | -32 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7 & 19 BAR | 9.9/9.8/9.9 | 405/404/405 | Short | UNIT NOT WORKING DISPLAY FADED PM SERVICE KEYPAD TEAR COMPRESSOR CONTACTOR BURNT | REPLACED COMPRESSOR CONTACTOR SECURE WIRING RUN UNINT CHECKED OPERATION MAIN WIRING ALL SENSOR RERADING & PARAMETER GAS LEVEL & PRESSURE UNIT PM SERVICE CELAN CONDENSOR COIL UNIT PASS TEST | NO |  |  | https://drive.google.com/open?id=167pfTOdVcQhm_P6XlWev3IBcIDGHhNLI | TRIP054 | No | No | Can be done on next PM | NA
NOV009 | 2024-11-06 09:23 | operation@crystalgroup.in | DHL Supply Chain pvt Ltd | NIKHIL | 9885755890 | EXECUTIVE | DFOU6120281 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-06 09:49 | operation@crystalgroup.in | DHL | DFOU6120281 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM & GENERAL MAINTENANCE | DRY SERVICE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV009 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-06 09:50 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-06 09:50 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-06 09:51 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-06 10:05 | 2024-11-05 |  |  |  |  | DFOU6120281 |  |  |  | Daikin | 2 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 & 180 | 9.9 / 9.8 / 9.8 | 400 / 401/ 400 | Short | PM SERVICE & GENERAL INSPECTION DRY PM SERVICE ONLY ( WITH AIR PRESSURE CLEAN CONDENSOR COIL ) DUE TO CARRY INSIDE NOT ALLOWED WATER CLEANING) | UNIT RUN & CHECKED OPERATION, MAIN voltage all motor amps & rotation all sensor reading & parameters gas levels & pressure unit working as satisfactory with alarm unit pti pass | no |  |  | https://drive.google.com/open?id=1BpoIFJzbKusW3fFL1BQLm7OQKYSla6AQ | TRIP054 | No | No | Can be done on next PM | na
NOV010 | 2024-11-06 09:42 | operation@crystalgroup.in | RELIANCE | RAJVIR YADAV | 88268 18750 | -NA- | CXRU1045453 | TEMPERATURE NOT PULLING DOWN | PRAVIN |  |  | Running with issues |  |  |  | 2024-11-07 15:17 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN LAST TEMPERATURE -14.3 FOUND ICE FOUNDATION ON EVAPORATOR COIL BLOCK SUPPLY AIR FLOW | NEED TO CLEAN EVP COIL AND BUFFET PLATE ARM + BAR FLOOR DUE TO CARGO LOADED NO POSSIBLE CLEAN THIS ARE REEFER UNIT RUNNNING NORMAL TEMPERATURE ISSUE STILL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV010 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ |  | TEMPERATURE NOT PULLING DOWN | 2024-11-07 15:19 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-07 15:19 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 15:20 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 15:36 | 2024-11-06 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -25 | Clean | Clean |  | Okay |  | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5 & 9.8 | 7.9/7.9/7.9 | 410/411/410 | Not done | TEMPERATURE NOT PULLING DOWN LAST TEMPERATURE -14.3 FOUND ICE FOUNDATION ON EVAPORATOR COIL BLOCK SUPPLY AIR FLOW | "NEED TO CLEAN EVP COIL AND BUFFET PLATE ARM + BAR FLOOR DUE TO CARGO LOADED NO POSSIBLE CLEAN THIS ARE REEFER UNIT RUNNNING NORMAL TEMPERATURE ISSUE STILL" | NO |  |  | https://drive.google.com/open?id=1L4xF2S5SnsDUMRRNnc40jyYlHDQz1ODj | ON CALL | Yes | No | Can be done on next PM | CLEANING THE COIL AT CLIENTS END
NOV012 | 2024-11-06 18:35 | operation@crystalgroup.in | ITC AQUEA | SHIVA | 9849765331 | NA | MYRU4517508 | UNIT NOT WORKING | PRAVIN |  |  | Running with issues |  |  |  | 2024-11-07 11:12 | operation@crystalgroup.in | ITC AQUEA | MYRU4517508 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | UNIT NOT WORKING | NEED TO REPLACE PHASE CONTACTOR BOTH CONTACTOR DEFECTIVE UNIT NOT WORKING | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV012 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | RAMIZ |  | UNIT NOT WORKING | 2024-11-07 11:48 | operation@crystalgroup.in | YES | NOV004 | 07.11.24 | Spares, FOC | ITC AQUEA | NELLORE | MYRU4517508 | SITE | FOC | DAIKIN | 2024-11-07 12:32 | operation@crystalgroup.in | YES | NOV004 | YES |  |  | 2024-11-07 12:33 | operation@crystalgroup.in | YES | NOV004 | COURIER | [5 empty] | 2024-11-07 12:38 | 2024-11-06 |  |  |  |  | MYRU4517508 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  |  |  | Not done | UNIT NOT WORKING FOUND PHASE CONTACTOR DEFECTIVE F101 | NEED TO REPLACE PHASE CONTACTOR BOTH CONTACTOR | YES |  |  | https://drive.google.com/open?id=1F9QMLz1adWZt1A3b62B3enpXFoUg8M5G | TRIP054 | Yes | Yes | Urgent | INSTALLATION
NOV011 | 2024-11-07 10:55 | operation@crystalgroup.in | BEJAPURI DAIRY | LAKHWINDER SINGH | 9876772453 | MAINTAINENCE MANAGER | MYRU4503459 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-07 11:02 | operation@crystalgroup.in | BEJAPURI DAIRY PVT LTD | MYRU4503459 | 40-REFEER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | RUN AND CHECKED OPERATION MAINTAINANCE VOLTAGE ALL MOTOR AMP & ROTATION ELECTRICAL PANEL WIRING & HARNESS CHECKED GAS LEVEL % PRESSURE & PARAMETERS CLEAN UNIT & CONDENSOR COIL UNIT PERFORM AND PASS SHORT PTI UNIT WORKING GOOD CONDITION NOTE:- INSIDE HOUSE KEEPING NOT GOOD NEED TO CELAN MONTHLY UNIT FRONT SIDE ( MACHINE SIDE) TREE BRANCHE NEED TO CUT | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV011 | Daikin | Daikin |  |  |  | Refurbished |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-07 11:03 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-07 11:03 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-07 11:03 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-07 11:06 | 2024-11-06 |  |  |  |  | MYRU4503459 |  |  |  | Daikin | -10 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 11 & 190 | 9.8/9.9/9.8 | 409/409/409 | Short | PM SERVICE & GENERAL INSPECTION | "RUN AND CHECKED OPERATION MAINTAINANCE VOLTAGE ALL MOTOR AMP & ROTATION ELECTRICAL PANEL WIRING & HARNESS CHECKED GAS LEVEL % PRESSURE & PARAMETERS CLEAN UNIT & CONDENSOR COIL UNIT PERFORM AND PASS SHORT PTI UNIT WORKING GOOD CONDITION NOTE:- INSIDE HOUSE KEEPING NOT GOOD NEED TO CELAN MONTHLY UNIT FRONT SIDE ( MACHINE SIDE) TREE BRANCHE NEED TO CUT" | NO |  |  | https://drive.google.com/open?id=1-F1X8NKlKj1chi-uuivz3OZKUVBFwBxL | TRIP054 | No | No | Can be done on next PM | NO
NOV015 | 2024-11-07 15:42 | operation@crystalgroup.in | RELIANCE | RANVEER SINGH | 9872609126 | FM TEAM | CICU1799140 | ALARM FOR RETURN SENSOR TEMP | PRAVIN |  |  | Running with issues |  |  |  | 2024-11-07 15:48 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-BLAST REEFER | TK MP4000 | SERVICE-ON CALL | LEASE | FOC | ALARM FOR RETURN SENSOR, TEMP NOT PULL DOWN | NEED TO REPLACE RETURN SENSOR THE REEFER UNIT IN NORMAL CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV015 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH |  | ALARM FOR RETURN SENSOR TEMP | 2024-11-07 16:08 | operation@crystalgroup.in | YES | NOV005 | 07.11.24 | Spares, FOC | RELIANCE | RAJPURA | CICU1799140 | SITE | FOC | TK-MP4000 | 2024-11-25 15:11 | operation@crystalgroup.in | YES | NOV005 | YES |  |  | 2024-11-25 15:12 | operation@crystalgroup.in | YES | NOV005 | COURIER | [5 empty] | 2024-12-23 16:10 | 2024-11-07 |  |  |  |  | CICU1799140 |  |  |  | Thermo king | -40 | [31 empty] | TEMP NOT PULL DOWN ALARM FOR TEMP SENSOR | NEED TO REPLACE RETURN SENSOR | Yes | https://drive.google.com/open?id=1nck4gR2ZpFngow6DJHGMVspJSx9PDwtZ |  |  | NA | Yes | Yes | Can be done on next PM | CHANGE SNESOR | RETURN SENSOR | operation@crystalgroup.in
NOV013 | 2024-11-08 09:49 | operation@crystalgroup.in | PRAYAGH CONSUMER | MURALI KRISHA | 9618263659 | ELE DY MANAGER | MYRU4500552 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-08 10:20 | operation@crystalgroup.in | PRAYAGH COSUMER | MYRU4500552 | 40-REEFER | TK MP-3000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE AND GENERAL INSPECTION DOOR OPEN AND CLOSING ISSUE COMPRESSOR CONTACTOR & LIGHTING C.B FELT DOWN CONTR DOOR HINGES POINT GREECING & OILING DOOR OPEN & CLOSING SMOOTH RUNN UNIT CHECK OPERATION MAIN VOLTAGE ALL MOTOR AMP & ROTATION ALL SENSOR READING & PARAMETER GAS LEVEL AND PRESSURE UNIT ALL OVER WORKING AS SATISFACTORY. UNIT PASS TEST PTI FULL | SECURED MRB WIRING AND COMPRESSOR CONTOR & LIGHT C.B. CLEAN UNIT & CONDENSOR COIL WITH FRESH NORMAL WATER UNIT WORKING FINE & MAINTAIN SET TEMP WITH NO ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV013 | Thermoking | Thermoking | M003285 | LXECOE136A2 | 24C1 | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-08 10:21 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-08 10:22 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-08 10:22 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-08 10:28 | 2024-11-07 |  |  |  |  | MYRU4500552 |  |  |  | Thermo king | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 & 180 PSI | 9.7/9.8/9.7 | 408/407/407 | Short | "PM SERVICE AND GENERAL INSPECTION DOOR OPEN AND CLOSING ISSUE COMPRESSOR CONTACTOR & LIGHTING C.B FELT DOWN CONTR DOOR HINGES POINT GREECING & OILING DOOR OPEN & CLOSING SMOOTH RUNN UNIT CHECK OPERATION MAIN VOLTAGE ALL MOTOR AMP & ROTATION ALL SENSOR READING & PARAMETER GAS LEVEL AND PRESSURE UNIT ALL OVER WORKING AS SATISFACTORY. UNIT PASS TEST PTI FULL" | "SECURED MRB WIRING AND COMPRESSOR CONTOR & LIGHT C.B. CLEAN UNIT & CONDENSOR COIL WITH FRESH NORMAL WATER UNIT WORKING FINE & MAINTAIN SET TEMP WITH NO ALARM" | NO |  |  | https://drive.google.com/open?id=1jPPenvoCYqDYKAP5-wRcWiL94lpQ6Qje | TRIP054 | No | No | Can be done on next PM | NA
NOV014 | 2024-11-08 09:54 | operation@crystalgroup.in | DSV LOGISTIC | SAGAR | 9030909007 | ASSOCIATE | TITU8259260 | REPAIR QUATATION REQUEST FOR SALES CONTAINER | PUSHPA |  |  | Running with issues |  |  |  | 2024-11-08 10:39 | operation@crystalgroup.in | DSV | TITU8259260 | 20-REEFER | THERMOKING MP4000 | SERVICE-AT SITE | SALE | CHARGEABLE | CUSTOMER REQUEST REPAIR AND QUOTATION UNIT MP4000 PM SERVICE | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV014 | [7 empty] | SHAHBUDDIN | Yes | REPAIR QUATATION REQUEST FOR SALES CONTAINER | 2024-11-11 10:57 | operation@crystalgroup.in | YES | NOV056 | 11.11.24 | Spares, Paid | DSV Air & Sea Pvt. Ltd. | HYDERABAD | TITU8259260 | SITE | PAID | TK-MP4000 | 2024-11-19 18:30 | [6 empty] | 2024-11-19 18:31 | [9 empty] | 2025-01-17 18:12
NOV016 | 2024-11-08 09:56 | operation@crystalgroup.in | RELIANCE | SUBHAM | 9335457649 | DUTY ENG INCHARGE | TRIU6618663 | UNIT TRIPING OFF & DISPLAY FADED | PUSHPA |  |  | Running with issues |  |  |  | 2024-11-08 10:55 | operation@crystalgroup.in | RELIANCE | TRIU6618663 | 20-REEFER | CARRIER | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPING OFF DISPLAY FADED | CHECKED AND FOUND EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERATURE DISCONNECTED GR COIL WIRING NEED REPLACED DISPLAY ( CARRIER ) FADED UNIT RUN & MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV016 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN | Yes | UNIT TRIPING OFF & DISPLAY FADED | 2024-11-11 11:19 | operation@crystalgroup.in | YES | NOV057 | 11.11.24 | Spares, FOC | RELIANCE | JAMNAGAR | TRIU6618663 | SITE | FOC | CARRIER-THINLINE | 2024-12-24 10:29 | operation@crystalgroup.in | YES | NOV057 | YES |  |  | 2025-01-04 13:28 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-13 13:48 | 2024-11-07 |  |  |  |  | TRIU6618663 |  |  |  | Carrier | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B/10.5b | 12,1/12/12.1 | 401/401/402 | Not done | "UNIT TRIPING OFF DISPLAY FADED" | "CHECKED AND FOUND EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERATURE DISCONNECTED GR COIL WIRING NEED REPLACED DISPLAY ( CARRIER ) FADED UNIT RUN & MAINTAIN TEMP" | Yes | https://drive.google.com/open?id=1DsOyaPzgDm8E7tiEPDSRVu1QcQS4-YNi |  |  | NA | Yes | Yes | Urgent | need to fix heater coil & Display | heater coil 6 nos & display | service@crystalgroup.in
NOV017 | 2024-11-08 10:00 | operation@crystalgroup.in | RELIANCE | SUBHAM | 93354 57649 | DUTY ENG INCHARGE | CCLU1031918 | UNIT TRIPPING OFF | PUSHPA |  |  | Running with issues |  |  |  | 2024-11-08 10:57 | operation@crystalgroup.in | RELIANCE | CCLU1031918 | 20-REEFER | CARRIER | SERVICE-ON CALL | LEASE | FOC | UNIT CARRIER THINLINE UNIT TRIPPING OFF | CHECKED EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERLY DISCONECTED WIRING & MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV017 | Carrier - Thinline | Thinline |  |  |  | brand New |  | SHAHBUDDIN | Yes | UNIT TRIPPING OFF | 2024-11-11 11:33 | operation@crystalgroup.in | YES | NOV058 | 11.11.24 | Spares, FOC | RELIANCE | GUJRAT | CCLU1031918 | SITE | FOC | CARRIER-THINLINE | 2024-12-24 10:31 | operation@crystalgroup.in | YES | NOV058 | YES |  |  | 2025-01-04 13:29 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-13 13:56 | 2024-11-07 |  |  |  |  | CCLU1031918 |  |  |  | Carrier | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B/12.1B | 12.1/12/12.1 | 401/402/401 | Not done | UNIT CARRIER THINLINE UNIT TRIPPING OFF | CHECKED EVAPORATOR HEATER COIL GROUNDED NEED TO REPLACE ASAP TEMPERLY DISCONECTED WIRING & MAINTAIN TEMP | Yes | https://drive.google.com/open?id=1OGrcPmdA8dotRLX_crfuDTzr0gsKkJDd |  |  | NA | Yes | Yes | Urgent | need to fix heater coil 4 nos | Heater coil 4 nos | service@crystalgroup.in
NOV018 | 2024-11-08 10:02 | operation@crystalgroup.in | NEWLY WEDS FOOD PVT LTD | RAMER SINGH | 8303477645 | DUTY ENG. | MYRU4512527 | SET TEMP ISSUE | PUSHPA |  |  | Running with issues |  |  |  | 2024-11-08 10:59 | operation@crystalgroup.in | NEWLY WEDS FOODS PVT LTD | MYRU4512527 | 40-REFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | TEMP SENSOR OUT OFF RANGE SET TEMP ISSUE DISPLAY COVER BROKEN | REQUIRED VISIT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV018 | [7 empty] | VIRENDRA | Yes | SET TEMP ISSUE | 2024-11-11 11:48 | operation@crystalgroup.in | YES | NOV059 | 11.11.24 | Spares, Paid | NEWLY WEDS FOOD PVT LTD | BARODA | MYRU4512527 | SITE | PAID | DAIKIN LXE10E | 2025-01-13 16:41 | operation@crystalgroup.in | YES | NOV059 | YES |  |  | 2025-09-29 17:31 | crm@crystalgroup.in | NO
NOV019 | 2024-11-09 14:26 | operation@crystalgroup.in | HETERO UNIT 3 | G.V. PHAVI | 9154268772 | EXECUTIVE | APRU5091041 | PREVENTIVE MAINTENANCE | PRAVIN |  |  | Preventive Maintenance |  |  |  | 2024-11-09 14:46 | operation@crystalgroup.in | HETERO UNIT 3 | CXRU1026520 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV019 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-09 14:54 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-09 14:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-09 14:57 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-08 22:57 | 2024-11-08 |  |  |  |  | CXRU1026520 |  |  |  | Daikin | + 5 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190 PSIG | 9.9/9.8/9.8 | 412/412/412 | Short | UNIT WORKING FINE & MIANTANING SET TEMP | PM DONE | NO |  |  | https://drive.google.com/open?id=1ayImZzr6AfzKxKDqIsn75vvWLOx2plTl | TRIP054 | No | No | Can be done on next PM | NO
NOV021 | 2024-11-09 14:27 | pravin.shinde@crystalgroup.in | Hetero 3 | Kumar | 9154268772 | executive | PCIU6016370 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-09 14:43 | pravin.shinde@crystalgroup.in | Hetero 3 | APRU5091041 | 40ft | carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | pm | na | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV021 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-09 14:55 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-09 14:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-09 14:58 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-08 23:37 | 2024-11-08 |  |  |  |  | APRU5091041 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  |  |  | Okay | Okay | Okay | Done | Clean |  | 8/180 | 13.2/13.1/13.2 | 412/412/412 | Short | Unit working is fine with no alarm | PM DONE | NO |  |  | https://drive.google.com/open?id=1xJkpcG0GcrpOtQhpNApdjYAy2pXrV-Of , https://drive.google.com/open?id=1eJi_XI3kPwrfOk8BIYn5c26f1-24G18V | TRIP054 | No | No | Can be done on next PM | NA
NOV020 | 2024-11-09 14:32 | operation@crystalgroup.in | HETERO UNIT 3 | G V PHARI | 9154268772 | EXECUTIVE | CXRU1030427 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-09 14:47 | operation@crystalgroup.in | HETERO UNIT 3 | CXRU1030427 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV020 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-09 14:54 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-09 14:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-09 14:57 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-08 22:34 | 2024-11-08 |  |  |  |  | CXRU1030427 |  |  |  | Daikin | + 5 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/185 | 9.8/9.9/9.8 | 412/411/411 | Short | Unit working as fine | PM DONE AND UNIT WORKING AS SATISFACTION WITH NO ALARM | NO |  |  | https://drive.google.com/open?id=1ESYMtHItgG_hxqVVDEdb8AMEAuE925FY | TRIP054 | No | No | Can be done on next PM | NA
NOV022 | 2024-11-09 14:33 | operation@crystalgroup.in | HETERO UNIT 3 | C G V PHARI | 9154268772 | EXECUTIVE | PCIU6016370 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-09 14:50 | operation@crystalgroup.in | HETERO UNIT 3 | PCIU6016370 | 10-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | pm | na | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV022 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-09 14:55 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-09 14:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-09 14:58 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-08 23:22 | 2024-11-08 |  |  |  |  | PCIU6016370 |  |  |  | Daikin | + 8 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/195 | 9.9/9.8/9.9 | 412/412/412 | Short | UNIT WORKING AS FINE | PM DONE | NO |  |  | https://drive.google.com/open?id=1Ez0_2vV09gdNdgH962AGlG79xWBMREJ2 | TRIP054 | No | No | Can be done on next PM | NA
NOV023 | 2024-11-09 14:35 | operation@crystalgroup.in | CELON LABORATORIES PRIVATE LIMITED | krishnamurthy | 8466979524 | EXECUTIVE | TRIU6616871 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-09 14:52 | operation@crystalgroup.in | CELON LAB | TRIU6616871 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV023 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-09 14:55 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-09 14:57 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-09 14:59 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-09 18:24 | 2024-11-09 |  |  |  |  | TRIU6616871 |  |  |  | Carrier | + 5 C | Clean | Clean |  | Okay | Clean |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190PSIG | 13.1/13.2/13.1 | 405/407/407 | Short | UNIT WORKING AS SATISFACTORY | REPLACED FADED DISPLAY& SUPPLY AIR SENSOR FOR CONTROLLER & DATACORDER CONTROLLER | NA |  |  | https://drive.google.com/open?id=1M6ccH2rNjW7LOOxiBs9Ysze05ewZyQrB, https://drive.google.com/open?id=1a92XLkrHy_dQVygEFVNVJutm6As_Rd_q | TRIP054 | No | No | Can be done on next PM | NO
NOV024 | 2024-11-11 11:57 | operation@crystalgroup.in | RELIANCE | AVINASH | 9281026402 | SHIFT INCHARGE | CICU1799177 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-11 12:01 | operation@crystalgroup.in | RELIANCE | CICU1799177 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV024 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 |  | BRand NEW | JSGA622180057 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-11 12:01 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-11 12:02 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-11 12:02 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-10 19:11 | 2024-11-10 |  |  |  |  | CICU1799177 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0,9/19Bar | 10.4/10.5/10.4 | 410/410/410 | Short | UNIT WORKING AS SATISFACTORY | PM DONE ,CLEANING INSIDE & OUT SIDE UNIT | NO |  |  | https://drive.google.com/open?id=1KW0WsCA_N9B5zbBz0IOuzYNApz8QkDXK, https://drive.google.com/open?id=1wrnY5nxUO6DT9Y1Pz1A14lsJB7kET-_M, https://drive.google.com/open?id=18FQFwOAxbrRmd_UYhIa00FIXQU1y5px6 | TRIP054 | No | No | Can be done on next PM | NO
NOV026 | 2024-11-11 15:38 | operation@crystalgroup.in | DSV LOGISTIC | ramesh | 7799437098 | _ | TITU9930006 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-11 15:40 | operation@crystalgroup.in | DSV | TITU9930006 | 40-REEFER | THERMOKING MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM AND GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV026 | Thermoking | Plus | 14D8550HT | EOG1000568 |  | brand New |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-11 15:41 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-11 15:42 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-11 15:42 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-11 14:19 | 2024-11-11 |  |  |  |  | TITU9930006 |  |  |  | Thermo king | + 2 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/20BAR | 9.8/9.9/9.8 | 406/407/406 | Short | UNIT WORKING AS STATISFACTORY | NO | NO |  |  | https://drive.google.com/open?id=1ew4bfzMASiC2jVaAXJ9ilzP5KoSe2u9i, https://drive.google.com/open?id=1DGqkWyP1hVlDmdBI7-Y-1qbTJKaP5e_d | TRIP054 | No | No | Can be done on next PM | NO
NOV025 | 2024-11-12 11:57 | operation@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | SJKU4000104 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-12 11:58 | operation@crystalgroup.in | DSV | SJKU4000104 | 40-REEFER | TK MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV025 | Thermoking | MP-4000 |  |  |  | Refurbished |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-12 12:01 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-12 12:01 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-12 12:01 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-11 17:15 | 2024-11-11 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/20bar | 9.8/9.9/9.8 | 406/406/406 | Short | FOUND UNIT WORKING FINE & MAINTANING SET TEMP. | PM DONE | NO |  |  | https://drive.google.com/open?id=1LggrXIG9bM655Dw6w1aJzh2xRP6KrOcC , https://drive.google.com/open?id=1mZXTUFyEjLHKue2MbqlQmMgfRyXRKnnU | TRIP054 | No | No | Can be done on next PM | NO
NOV028 | 2024-11-12 12:19 | operation@crystalgroup.in | Dr. REDDY FTO 9 | K RAM | 9966816434 | FM TEAM | CICU1920740 | TEMERATURE NOT PULLING DOWN | RAHUL |  |  | Running with issues |  |  |  | 2024-11-12 12:29 | operation@crystalgroup.in | Dr. REDDY FTO-9 | CICU1920740 | 40-REEFER | TK MP4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | NA | NO` |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV028 | Thermoking | Magnum Plus | E0GM018643 | ABC782800320490059 |  | BrandNew |  | RAMIZ |  | TEMERATURE NOT PULLING DOWN | 2024-11-12 12:30 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-12 12:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-12 12:30 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-12 12:38 | 2024-11-07 |  |  |  |  | CICU1920740 |  |  |  | Thermo king | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2.1 & 15.3 | 8.1/8.2/8.1 | 404/403/404 | Short | FOUND SUPPLY TEMPERATURE SENSOR DEFECTIVE TEMPERATURE NOT PULLING DOWN WRONG POSITION OF SUPLLY TEMPERATURE TEMPERATURE ( BY CLIENT ) | CONNECTION PORTION OF SUPPLY TEMPERATURE SENSOR AFTER WORKING THE REEFER UNIT WORKING SOUND AND GOOD CONDITION STILL UNDER OBSERVATION | NA |  |  | https://drive.google.com/open?id=14GmBoDk-FWHRKp3aPry_XQm4WLROEtBN | NA | No | No | Can be done on next PM | NA
NOV027 | 2024-11-12 12:24 | operation@crystalgroup.in | Transys Global (TGF) | SRI RANGANADH | 9703736718 | MANAGER | TITU8259378 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-13 09:55 | operation@crystalgroup.in | TGF TRANSYS GLOBAL | TITU8259378 | 20-REEFER | TK MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM SERVICE & GENERAL INSPECTION | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV027 | Thermo King MP-4000 | MP 4000 |  |  |  | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-13 09:55 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-13 09:56 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-13 09:56 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-12 17:29 | 2024-11-12 |  |  |  |  | TITU8259378 |  |  |  | Thermo king | -22C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7/19bar | 9.9/9.9/9.9 | 400/400/400 | Short | UNIT WORKINGAS FINE & MAINTANING SET TEMP. | NO | NO |  |  | https://drive.google.com/open?id=1UuOl8pNs9ehnX0KLhc8xsvsHFMW5n3BL, https://drive.google.com/open?id=12D4E0EseD6jLVLn7zUcTPbK7tySDK41_ | TRIP054 | No | No | Can be done on next PM | NO
NOV029 | 2024-11-13 10:02 | operation@crystalgroup.in | VEMLA FEEDS | A SHIV KUMAR | 8985557128 | REFRIGERATION OPERATOR | CICU1442256 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-14 10:51 | operation@crystalgroup.in | VIMAL FEEDS | CICU1442256 | 40-REEFER BLAST 5 UNIT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV029 | Thermoking | EOG5003933 | EOG5003933 | 220916, 3.29.00 |  | brand New |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-14 10:51 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-14 10:51 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-14 10:52 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-13 18:23 | 2024-11-13 |  |  |  |  | CICU1442256- FIVE WAY UNIT TK |  |  |  | Thermo king | - 40 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19 bar x5 | 9.9/9.8/9.8 x 5 | 405/405/405 x 5 | Short | ALL FIVE UNIT TK IS WORKING FINE & MAINTAINING SET TEMP. | NO | NO |  |  | https://drive.google.com/open?id=12l256gaCjMYxFJfoVqv5unhxwocFmBQg , https://drive.google.com/open?id=1Tdoo0X_AVZ87W_jDN3yU1d20wWj1DdVp | TRIP054 | No | No | Can be done on next PM | NO
NOV030 | 2024-11-13 18:35 | operation@crystalgroup.in | RELIANCE | RANVIR SINGH | 9872609128 | FM TEAM | CXRU1045453 | MOTOR NOT WORKING | RAMIZ |  |  | Running with issues |  |  |  | 2024-11-13 18:42 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULLING DOWN | NEED TO REPLACE EVAPORATOR MOTOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV030 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | RAMIZ |  | MOTOR NOT WORKING | 2024-11-13 18:47 | operation@crystalgroup.in | YES | NOV065 | 13.11.24 | Spares, FOC | RELIANCE | RAJPURA | CXRU1045453 | SITE | FOC | DAIKIN | 2024-12-23 16:43 | operation@crystalgroup.in | YES | NOV065 | NA |  |  | 2024-12-23 16:43 | operation@crystalgroup.in | NO | [7 empty] | 2024-12-24 10:38 | 2024-11-13 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -20 | [31 empty] | TEMP PULLING DOWN SLOWLY | NEED TO REPLACE EVP MOTOR | Yes | https://drive.google.com/open?id=1pVQm4j6mZUm6Przhlj5gqIUpQ7hqrpdV |  |  | NA | Yes | Yes | Urgent | NEED TO CHANGEMOTOR | EVP MOTOR | operation@crystalgroup.in
NOV034 | 2024-11-15 15:32 | operation@crystalgroup.in | ZEPTO | NARENDRA | 9717519295 | MANAGER | GESU9460634 | DOOR NOT CLOSING | NINAD |  |  | Running with issues |  |  |  | 2024-11-19 16:51 | operation@crystalgroup.in | ZEPTO | GESU9460634 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | DOOR NOT CLOING DUE TO CONTAINER ALIGNMENT WRONG , IMPROPER GROUND LEVEL | NEED TO LIFT THE CONTAINER AND KEEP IN PROPER GROUND LEVEL | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV034 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ | No | DOOR NOT CLOSING | 2024-12-18 11:51 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-23 17:09 | operation@crystalgroup.in | NO |  |  |  |  | 2024-12-23 17:09 | operation@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
NOV035 | 2024-11-16 22:07 | operation@crystalgroup.in | Aspiro pharma ltd | V. YASHWANTH REDDY | 9100345480 | TR OFFICER | CAIU5422720 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-16 22:42 | operation@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV035 | DAikin |  |  |  |  | Used | JSGA622340482 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-16 22:45 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-16 22:50 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-16 22:52 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-15 17:16 | 2024-11-15 |  |  |  |  | CAIU5422720 |  |  |  | Daikin | + 4 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/190 PSIG | 9.7/9.8/9.8 | 400/401/400 | Short | UNIT WORKING AS FINE & FOUND NO ALARM | PM & SERVICE WITH GENRAL CHECK UP DONE | NO |  |  | https://drive.google.com/open?id=1IK2OtJLANN9TV_bF_CtTOXaGlVnVcBqI , https://drive.google.com/open?id=1-IOj3ohPSCO-hqQyjmGpCS4ahD3CiVWt | TRIP054 | No | No | Can be done on next PM | NO
NOV036 | 2024-11-16 22:09 | operation@crystalgroup.in | Aspiro pharma ltd | V. YASHWANTH REDDY | 9100345480 | TR OFFICER | CGMU2991560 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-16 22:44 | operation@crystalgroup.in | ASPIRO PHARMA | CGMU2991560 | 20-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | NA | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV036 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-16 22:49 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-16 22:50 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-16 22:52 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-15 18:22 | 2024-11-15 |  |  |  |  | CGMU2991560 |  |  |  | Carrier | - 25C. | Clean | Clean |  | Noisy | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/9 180/190 PSIG | 12.3/12.4/12.4 | 400/400/400 | Full | THIS IS DUAL CARRIER THIN LINE UNIT: MAIN UNIT HAVING EVP MOTOR OVER HEAT WITH NOSISY AND UNIT II REQUIRED CONTROLLER ML3- CONTROLLER SOFTWARE PROGRAMM NOT FUNCTIONAL. NEED TO REPLACED | PM SERVICE DONE ,WITH EVP SERVICING DONE | NO |  |  | https://drive.google.com/open?id=1uoAg8m5Nv9YLAyHdMJSuwm-kArHG-3g4 , https://drive.google.com/open?id=1LRSEB8QPqwUnJH5ryvzdXdr-K-TFD2_B | TRIP054 | Yes | No | Can be done on next PM | NEED TO REPLACED ML3 - CARRIER CONTROLLER WITH LATES SOFTWARE AND EVP MOTOR OVER HEAT
NOV037 | 2024-11-16 23:22 | operation@crystalgroup.in | DR. REDDY CTO 3 | S/C BABAVALI | - | V3 TEAM MEMBER | GSOU6384240 | INSTALLATION | NINAD |  |  | Installation |  |  |  | 2024-11-16 23:24 | operation@crystalgroup.in | DR REDDY CTO3 | GSOU6384240 | 40-REEFER | CARRIER THINLINE | INSTALLATION | LEASE | FOC | INSTALLATION | NO | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV037 | Carrier | Carrier Thinline | SSB60749120 |  | ML-3 | used | JSGA622340472 | SHAHBUDDIN |  | INSTALLATION | 2024-11-16 23:25 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-16 23:25 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-16 23:26 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-16 18:32 | 2024-11-16 |  |  |  |  | GSOU6384240 |  |  |  | Carrier | + 6 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190 | 12.8/12.9/12,9 | 406/405/406 | Short | Dr.Reddy CTO - 3 New unit instalation & training done with container service,& PTI After Instalation container handed over to Mattrial section through Eng. Section for Mapaing. | As above | NO |  |  | https://drive.google.com/open?id=1JigwJlPk7YntKMSHFfjYxJoTtgHLBsIR , https://drive.google.com/open?id=1svchu7TJhTQTpWWOAAr2mirm3pZS-Pyx , https://drive.google.com/open?id=1B70tZpcEoUWv_MamL5eU39SNV9MCEaFt , https://drive.google.com/open?id=1ae_GN3qNOOBbR16cJRZ6m26HXywvscSm | TRIP054 | No | No | Can be done on next PM | NO
NOV038 | 2024-11-18 11:12 | operation@crystalgroup.in | Jubliant Consumer Pvt Ltd | ATUL | 9650818692 | NA | GRMU3607418 | CONTAINER NOT WORKING | NINAD |  |  | Running with issues |  |  |  | 2024-11-19 18:13 | operation@crystalgroup.in | jublient | GRMU3607418 | 20-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | E109, E607, TEMPERATURE NOT PULLDOWN | FILTER DRIER CHOKE, REPLACE IT ,& CHARGE GAS | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV038 | Daikin |  |  |  |  | Used |  | RAMIZ& ON SITE TECH |  | CONTAINER NOT WORKING | 2024-11-21 19:12 | operation@crystalgroup.in | YES | NOV072 | 21.11.24 | Consumables, Spares, FOC | JUBLIENT | NOIDA | GRMU3607418 | SITE | FOC | DAIKIN | 2024-11-21 19:13 | operation@crystalgroup.in | YES | NOV072 | YES |  |  | 2024-11-21 19:24 | operation@crystalgroup.in | YES | NOV072 | ARRENGING AT SITE | [5 empty] | 2024-11-21 19:30 | 2024-11-19 |  |  |  |  | GRMU3607418 |  |  |  | Daikin | [32 empty] | FOUND EXPANSION COIL DEFECTIVE | REPLACE FILTER DRIER AND VACCUME DONE AND CHARGE R134A GAS 5.2 KG, | YES |  |  | https://drive.google.com/open?id=1ff8SSHNmeB5sMGHdOIzT-lP6giz5g85m | NA | Yes | Yes | Urgent | EXPANSION VALVE COIL
NOV039 | 2024-11-18 11:29 | operation@crystalgroup.in | SYMBIOTEC | BALKRISHNA | 77479 37030 | OPERATION HEAD | TCLU1904607 | COMPRESSOR MALFUNCTION | NINAD |  |  | Running with issues |  |  |  | 2024-11-19 18:21 | operation@crystalgroup.in | SYMBIOTEC | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | UNIT LOW PRESSURE TRIPPING ALARM E109, | SUSPECTED LEAK | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV039 | Daikin | Daikin |  |  |  | Used |  |  |  | COMPRESSOR MALFUNCTION | 2024-12-18 11:52 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-18 16:01 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-18 16:01 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
NOV061 | 2024-11-19 16:53 | operation@crystalgroup.in | RELIANCE | DEEPAK | 8962570559 | SITE MANAGER | MYRU451588 | ICE FORMATION, UNIT NOT WORKING TEMPERATURE NOT PULLDOWN | ANUJ |  |  | Running with issues |  |  |  | 2024-11-19 16:57 | operation@crystalgroup.in | RELIANCE | MYRU451588 | 40-REEFER | DAIKIN | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT PULL DOWN ,COPRESSOR CONTACTOR TERMINAL SHORT CIRCUIT | TERMINAL BURNT HAS REPLACED AND FIXED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV061 | [7 empty] | RAMIZ |  | ICE FORMATION, UNIT NOT WORKING TEMPERATURE NOT PULLDOWN | 2024-11-19 18:30 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-19 18:30 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-19 18:31 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-19 18:36 | 2024-11-19 |  |  |  |  | MYRU451588 |  |  |  | Daikin | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1B & 13.5 B | 10.1/10.0/10.1 AMP | 411/410/411 | Not done | FOUND UNIT NOT WORKING AL F803, COMPRESSOR CONTACTOR TERMINAL CONNECTION SHORT CIRCUIT | FIX THE TERMINAL CONNECTION AND RUN THE CONTAINER AFTER WAITING THE REEFER UNIT WORKING SOUND AND GOOD CONDITION | NO |  |  | https://drive.google.com/open?id=1hkz_ETHQ_B4JbuR-bns5pwerJx_LzwPw | NA | No | No | Can be done on next PM | NA
NOV062 | 2024-11-25 16:34 | operation@crystalgroup.in | Lupin Limited | Santhosha Shetty | 9029942711 | Manager Distribution | TRIU6681882 | ALARM CODE VISIBLE | NINAD |  |  | Running with issues |  |  |  | 2024-11-25 16:56 | service@crystalgroup.in | Lupin Ltd | TRIU6681882 | 20FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | ALARM 22 & 53 , FOUND R/ S EVAPROTER MOTOR DEFECTIVE | NEED TO REPLACED R/S EVAPROTER MOTOR. | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV062 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040302 | SHAHBUDDIN |  | ALARM CODE VISIBLE | 2024-12-23 17:17 | operation@crystalgroup.in | YES | NOV099 | 2024-11-25 | Spares, FOC | LUPIN LTD | BHIVANDI | TRIU6681882 | SITE | FOC | CARRIER-THINLINE | 2024-12-23 17:17 | operation@crystalgroup.in | YES | NOV099 | YES |  |  | 2024-12-23 17:18 | operation@crystalgroup.in | YES | NOV099 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2024-11-25 17:43 | 2024-11-25 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | 25 | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | 410/411/410 | Not done | AL 22 R/S EVAPROTER FAN MOTOS NOT WOEKING.AL 53 | NEED TO REPLACE EVAPROTER | YES |  |  | https://drive.google.com/open?id=1XZSGa9mis7wn5YnPMW08Htt963fLMOzS | NA | No | Yes | Urgent | NA
NOV040 | 2024-11-25 17:10 | operation@crystalgroup.in | ITC NELLOR | SHIVA | 9849765331 | MANAGER | MYRU4517508 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 11:57 | operation@crystalgroup.in | ITC | MYRU4517508 | 40-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PREVENTIVE MAINTENANCE & SPARES INSTALLATON | SPARES REQUIRED IN NEXT VISIT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV040 | Daikin | Daikin | M002805 | LXE10E136A | NOT AVAILABLE | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 12:10 | operation@crystalgroup.in | YES | NOV075 | 26.11.24 | Spares, FOC | ITC | GUNTUR | MYRU4517508 | SITE | FOC | DAIKIN | 2025-01-07 17:35 | operation@crystalgroup.in | YES | NOV075 | YES |  |  | 2025-01-08 11:56 | mum.depot@crystalgroup.in | YES | N0V075 | TECHNICIAN |  |  | NA |  |  | 2024-11-18 18:10 | 2024-11-18 |  |  |  |  | MYRU4517508 |  |  |  | Daikin | -18.0C | Clean | Clean | https://drive.google.com/open?id=1uLJqXmhM5Cq5msxHaUlCWQ8Pu0C7dDPE | Okay | Clean | Okay | Okay |  | Okay | https://drive.google.com/open?id=1HRGXxKhg9C1QvDOhUJPPomFB8vcyb6-J | Okay | https://drive.google.com/open?id=1kfA3HN3wQnGE1PMvSCiRpQjUesbfAXtt | Okay | https://drive.google.com/open?id=1dvH8szqpc6oAFhQ6M7B7fWRmqf2-h_Ws | Okay |  | Okay | Okay | https://drive.google.com/open?id=18lPxVsnSX9vpWV_hCHTXXWgurhIaKjJO | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1800kpa,212kpa | 11.0A,10.7A,10.9A | 400 v | Not done | Container run in sound condition without any Alaram | PCC1 PCC2 Contactor replace | Sheet key, fuse 10A |  |  | https://drive.google.com/open?id=1Z4xrfH5CyDV7QzGcEQXIqbTtrWhWL6lr , https://drive.google.com/open?id=1u5OcKIiTokNcfG5RtHhe13WQUEHHHQjT | 56 | No | No | Can be done on next PM | Next pm need bufle plate fix and fuse 10A and sheet key raper need to change
NOV041 | 2024-11-25 17:50 | operation@crystalgroup.in | NSR TRADERS | KAMARAJU | 9903999266 | MANAGER | TCLU1112683 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 12:38 | operation@crystalgroup.in | NSR TRADERS | TCLU1112683 | 40-REEFER | TK MP3000 | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | WE HAVE ATTENDED THE UNIT AND FOUND DISPLAY NOT SHOWING SET POINT HEATER RELAY AND SOCKET BURNT KEYPAD DAMAGER FILTER DRIER RUSTED | WE HAVE CLEAN CONDENSOR COIL WITH NORMA WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM ALL WORK NEED TO DONE ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV041 | [7 empty] | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 12:50 | operation@crystalgroup.in | YES | NOV076 | 26.11.24 | Spares, Paid | NSR TRADERS | TUNI | TCLU1112683 | SITE | PAID | TK-MP3000 | 2025-01-07 17:33 | operation@crystalgroup.in | YES | NOV076 | YES | https://drive.google.com/open?id=1xNhsM_GN8sBJB4Jt6DZUsWCvkHMku4Eh |  | 2025-01-17 12:17 | mum.depot@crystalgroup.in | YES | NOV076 | COURIER | TRACKING NO:- 16453389654 | PATELCOURIER |  |  |  | 2024-11-19 10:51 | 2024-11-19 |  |  |  |  | TCLU1112683 |  |  |  | Thermo king | -5.0C | Dirty | Clean | https://drive.google.com/open?id=1OVHJU1ZQSAHNwKV-G_FazXUjzjuXMnF_ | Okay | Clean | Okay | Okay |  | Okay | https://drive.google.com/open?id=12d9531c_lxW406WUWZtmMwDlycR8Z_UE | Partially defective | https://drive.google.com/open?id=12Xct9mSuVSpa71MR5av30Gt6YhmXYZWv | Need to replace | https://drive.google.com/open?id=15BLBsQBi44Le5Qd7YwJGW0p012iLBX8a | Okay |  | Okay | Okay | https://drive.google.com/open?id=1ElYdb3jGHgRDHOvq7_MCK-08xuNNBF5k | Okay | https://drive.google.com/open?id=1K7EhrMr1tEZu-gsJyK1zG-K0457wTObf | Okay | Okay | Okay | Done | Rusty | https://drive.google.com/open?id=1UTCSs3zEr2a8wgyxe_LU4mTxNbyO6TTs | N/a | 7.3A,7.0A,7.1A | 426V, 421V,423V | Not done | Fillter Drier rusted to replace , heater relay socket and relay burn, relay board need to replace, display set point not showing to replace, keypad damage to replace, vaccum and gas need to refill R-404a 4kg | All work need to done | Fillter Drier, R-404a 4kg,relay board, display, keypad |  |  | https://drive.google.com/open?id=1wzOUoIvhMbnVS5doye15J3ZCB7_HQhip , https://drive.google.com/open?id=1SgMyvVCLsY1FaDOpFhhOyApccJ6COwkx | 56 | No | No | Urgent | N/a
NOV042 | 2024-11-25 18:43 | operation@crystalgroup.in | Laurus Unit 3 | Somi Reddy | 99631 98979 | MANAGER | MYRU4519115 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 14:44 | operation@crystalgroup.in | LAURUS UNIT 3 | MYRU4519115 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAEV REPLACED AMBIENT SNESOR 2 NOS SAS SENSOR 1 NOS AND CLEAAN CONDENSOR WITH NORMAL WATER CONTAINER RUNNING SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV042 | Daikin | Daikin | 806162 | LXE10E136A2 |  | Refurbished |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 14:44 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 14:44 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 14:44 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:01 | 2024-11-20 |  |  |  |  | MYRU4519115 |  |  |  | Daikin | +20.0C | Clean | Clean |  | Okay | Clean |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 74KPA 1024KPA | 8.8A,8.3A,8.5A | 386V,388V,390V | Not done | Container run in sound condition without any Alaram | AMBINT sensor replace, SGS sensor condenser coil wash | N/a |  |  | https://drive.google.com/open?id=1Ub8lRgfiatSv2aremodjOdr8oVIDrpOg, https://drive.google.com/open?id=1YdSek_TPvCOUk6N5IEUNQlseZYJR-I76 | TRIP NO 056 | No | No | Can be done on next PM | N/a
NOV043 | 2024-11-25 18:46 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | KKFU6711724 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 15:12 | operation@crystalgroup.in | LAURUS UNIT 3 | KKFU6711724 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER AND CLEAR ALARM AA54. CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV043 | Carrier - Thinline | Thinline | 4515UD3741 | LSX60253415 |  | used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 15:37 | operation@crystalgroup.in | YES | NOV077 | 26.11.24 | Spares, FOC | LAURUS UNIT 3 | PARWADA | KKFU6711724 | SITE | FOC | CARRIER-THINLINE | 2025-01-07 17:42 | operation@crystalgroup.in | YES | NOV077 | YES |  |  | 2025-01-08 14:43 | mum.depot@crystalgroup.in | YES | NOV077 | TECHNICIAN |  |  | NA |  |  | 2024-11-21 20:07 | 2024-11-20 |  |  |  |  | KKFU6711724 |  |  |  | Carrier | +20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay |  | Clean |  | 0.5B 10.3B | 10.2A,9.9A,10.3A | 402V,399V,400V | Not done | Container run in sound condition without any Alaram | N/a | Supply sensor 2nos |  |  | https://drive.google.com/open?id=1DEfNPp4-RfXS_IwFaKmouDOE1aSRmJVC, https://drive.google.com/open?id=1SkeqCx0FqkA7yDsG3It37PJaxIwCfxaX | Trip no 056 | No | No | Can be done on next PM | N/a
NOV044 | 2024-11-25 18:50 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | KKFU6710768 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 15:42 | operation@crystalgroup.in | LAURUS UNIT 3 | KKFU6710768 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSER COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONSDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV044 | [7 empty] | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 15:42 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 15:42 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 15:43 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:14 | 2024-11-20 |  |  |  |  | KKFU6710768 |  |  |  | Carrier | +19.9C | Clean |  |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.0B 11.3B | 10.0A,9.7A,9.9A | 396V,393V,395V | Not done | Container run in sound condition without any Alaram | Condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1B-TNUBrOc0BscmZlVVXgQkI26VJLT7Pn, https://drive.google.com/open?id=1sZT2wF0gW1SKnLwenrg2tkcBiKGuJ8qv | Trip no 044 | No | No | Can be done on next PM | N/a
NOV045 | 2024-11-25 18:51 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | TDRU7153256 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 15:46 | operation@crystalgroup.in | LAURUS UNIT 3 | TDRU7153256 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALALRM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV045 | Daikin | Daikin |  |  |  | used | JSGA623040290 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 15:46 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 15:46 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 15:46 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:22 | 2024-11-20 |  |  |  |  | TDRU7153256 |  |  |  | Daikin | +4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 66KPA 1173KPA | 9.5A,9.2A,9.3 | 383V,385V,387 | Not done | Container run in sound condition without any Alaram | Condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1ypuxw08nvfNG9hccrbjZ7PMUCFhU8kEm, https://drive.google.com/open?id=1hkM6RBwkk8jKBUO5ol2yqc29e806BOwz | Trip no 056 | No | No | Can be done on next PM | N/a
NOV046 | 2024-11-25 18:52 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | BMOU9784137 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 15:49 | operation@crystalgroup.in | LAURUS UNIT 3 | BMOU9784137 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HACE REPLACED SUPPLY SENSOR 2 NOS OUTLET SENSOR 1 NOS RETURN SENSOR 1 NOS CONDNSOR COIL WARN WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV046 | Daikin |  |  |  |  | used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 15:49 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 15:49 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 15:50 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:29 | 2024-11-21 |  |  |  |  | BMOU9784137 |  |  |  | Daikin | +3.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10KPA 1307KPA | 10.9A,10.5A,10.7A | 387V,383V,387V | Not done | Container run in sound condition without any Alaram | Supply sensor replace 2nos, outlet sensor replace 1nos, return sensor replace 1nos and condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1G-TDjvDf9B33xDqJlMC85tr36ASgjma9, https://drive.google.com/open?id=1_yyw-TLL-tk6LM8cKO5PnpGtgoXlW7Vh | Trip no 056 | No | No | Can be done on next PM | N/a
NOV047 | 2024-11-25 18:54 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | APRU5091340 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 15:54 | operation@crystalgroup.in | LAURUS UNIT 3 | APRU5091340 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | UNIT INSTALLATION | WE HAVE REPLACED MAIN UNIT WITH NEW ONE AND RUN CONTIANER , CONTAINER RUNNING IN GOOD CONDITION WITHOUT ANY ALARM PRESENT TEMP 15 TO 25 C THIS UNIT IS MAINTAINING TEMP | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV047 | Carrier - Thinline | Thinline | 1106L0930 | KSU60108845 |  | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 15:56 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 15:57 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 15:59 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:36 | 2024-11-21 |  |  |  |  | APRU5091340 |  |  |  | Daikin | +25.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 49KPA 842KPA | 8.0A,7.7A,7.9A | 388V,383V,385V | Not done | Container run in sound condition without any Alaram | Old unit remove and new unit fitted and complete silicone work | N/a |  |  | https://drive.google.com/open?id=1EeGhzlBOqZLKcGRrFqbdunPiq629wf9H, https://drive.google.com/open?id=1dk2OLlkKIfmaPo_YAYMBkhUvH2srGNJf, https://drive.google.com/open?id=14vPzRwH1-Smuw6Mh_whzv_pSCcash_Im, https://drive.google.com/open?id=1mg82vKUmnqJSp6Z9w_oLpE_Bx5t_EQlR | Trip no 056 | No | No | Can be done on next PM | N/a
NOV048 | 2024-11-25 18:56 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | MYRU4505847 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:02 | operation@crystalgroup.in | LAURUS UNIT 3 | MYRU4505847 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE INSPECTION THIS UNIT AND FOUND CONTAINER WITHOUT ANY ALARM ANY ALARM AND MAITAIN TEMP +20.7C | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV048 | Daikin | Daikin |  |  |  | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 16:03 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 16:03 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 16:06 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:41 | 2024-11-21 |  |  |  |  | MYRU4505847 |  |  |  | Daikin | +21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 50KPA 900KPA | 8.1A,7.9A,8.0A | 402V,400V,401V | Not done | We have observed this unit and found container run in sound condition without any Alaram | N/a | N/a |  |  | https://drive.google.com/open?id=1-bjj-5_cCej_x_juoBUKaNzCaKKohuMn, https://drive.google.com/open?id=1vjVER8hdIyWzTKfrDxlbvNJ4H3hEttK9 | Trip no 056 | No | No | Can be done on next PM | N/a
NOV049 | 2024-11-25 18:58 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | TCLU1912290 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:09 | operation@crystalgroup.in | LAURUS UNIT 3 | TCLU1912290 | 20-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THE UNIT AND FOUND CONATAINER SHOWING ALARM E406 SG SENSOR FAILURE | WE HAVE REPLACED SGS SENSOR CLEAN CODENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV049 | Daikin |  |  |  |  | used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 16:09 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 16:09 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 16:10 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:46 | 2024-11-21 |  |  |  |  | TCLU1912290 |  |  |  | Daikin | -20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 15KPA 1200KPA | 8.0A,7.7A,7.9A | 409V,405V,407V | Not done | We have found in this unit SGS sensor df to replace | We have replaced SGS sensor and condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1FysK5FA0azBUXEo8IcfnE0jJKKjLWZyi, https://drive.google.com/open?id=1VaIUk4ifF2YBjIcVf54Odvblki09gwjj | Trip no 056 | No | No | Can be done on next PM | N/a
NOV050 | 2024-11-25 18:59 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | DFOU6120384 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:14 | operation@crystalgroup.in | LAURUS UNIT 3 | DFOU120384 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PEVENTIVE MAINTENANCE | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER AND SHEET KEY JACK PROPER FILTER NOW CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV050 | [7 empty] | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 16:14 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 16:15 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 16:15 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:52 | 2024-11-21 |  |  |  |  | DFOU6120384 |  |  |  | Daikin | +22.0C | Clean | Clean |  | Okay | Clean |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 35KPA 905KPA | 9.5A,9.1A,9.3A | 401V,397V,399V | Not done | We have found in this container sheet key not working due to sheet key jack not fitted properly | We have fix Sheet Key jack properly and condenser coil wash with normal water and container run in sound condition without any Alaram | N/a |  |  | https://drive.google.com/open?id=1m-EIwH8V-lBe91bnHWMmH02ms16kyZ8j, https://drive.google.com/open?id=1g2rfDtj0q7xFIKwtr-y8IW7YbIzv-dON | Trip no 056 | No | No | Can be done on next PM | N/a
NOV051 | 2024-11-25 19:01 | operation@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | MANAGER | SUDU6257274 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:18 | operation@crystalgroup.in | LAURUS UNIT 3 | SUDU6257274 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | WE HAVE REPLACE HUMIDITY SENSOR AND CONDENSOR COIL WASH WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV051 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 16:28 | operation@crystalgroup.in | YES | NOV078 | 26.11.24 | Consumables, FOC | LAURUS UNIT 3 | PARWADA | SUDU6257274 | SITE | FOC | CARRIER-PRIMLINE | 2025-01-07 17:43 | operation@crystalgroup.in | YES | NOV078 | YES |  |  | 2025-01-08 12:24 | crm@crystalgroup.in | NO | [7 empty] | 2024-11-21 20:58 | 2024-11-21 |  |  |  |  | SUDU6257274 |  |  |  | Carrier | +2.0C | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.7B 9.3B | 6.8A,6.3A,6.5A | 414V,411V,413V | Not done | We have found in this container both evp motor create noise | We have replaced humidity sensor and condenser coil wash with normal water | Evp motor bearing 4nos and software need to update |  |  | https://drive.google.com/open?id=1vWBUU4AUWUeVRux5glKXsC5ehgcQFqY1, https://drive.google.com/open?id=1klCh0Kbup2DjdXzONfAjfkEK7yD-2nTX | Trip no 056 | No | No | Can be done on next PM | N/a
NOV052 | 2024-11-25 19:03 | operation@crystalgroup.in | LAURUS UNIT 6 | VENU BABU | 8913072380 | MANAGER | TITU9930011 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:37 | operation@crystalgroup.in | LAURUS UNIT 3 | TITU9930011 | 40-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | WE ATTENDED THIS CONTAINER AND FOUND CONDENSOR COIL NORMAL DIRTY TO WARN AND SOFTWARE NEED TO UPDATE | WE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV052 | Thermoking MP-4000 | MP 4000 | 14D8568HT | EOG1000566 |  | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 16:41 | operation@crystalgroup.in | YES | NOV079 | 26.11.24 | Spares, FOC | LAURUS UNIT 6 | LALAMKONDEV | TITU9930011 | SITE | FOC | TK-MP4000 | 2025-01-07 17:47 | operation@crystalgroup.in | YES | NOV079 | YES |  |  | 2025-01-08 14:46 | mum.depot@crystalgroup.in | YES | NOV079 | TECHNICIAN |  |  | NA |  |  | 2024-11-23 19:28 | 2024-11-23 |  |  |  |  | TITU9930011 |  |  |  | Thermo king | +10.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 17.3B | 7.0A,6.5A,6.7A | 413V,410V,411V | Not done | Condenser coil normal dirty and software need to be update | condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=10ChHSgyj2TsD0HP1DrXhA1lHXRsDj4KO, https://drive.google.com/open?id=1cOi_VQD7qw5Rq2PZho1S5FqbxK2owxFR | Trip no 056 | No | No | Can be done on next PM | N/a
NOV053 | 2024-11-25 19:04 | operation@crystalgroup.in | LAURUS UNIT 6 | VENU BABU | 8913072380 | MANAGER | MYRU4509035 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:45 | operation@crystalgroup.in | LAURUS UNIT 6 | MYRU4509035 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV053 | Daikin | Daikin | 802602 | LXE10E136A |  | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 16:46 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 16:46 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 16:46 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-23 19:33 | 2024-11-23 |  |  |  |  | MYRU4509035 |  |  |  | Daikin | +3.6C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 127KPA, 895KPA | 8.8A, 8.3A, 8.5A | 409V, 405V, 407V | Not done | Condenser coil heavy dirty to wash | Condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1cQWyjcbVptrnX_37yxHkjn9JyzZFQB3V, https://drive.google.com/open?id=1DxlwxQfArEHO6pmFlBcvLkZKbNwmE7Ew | Trip no 056 | No | No | Can be done on next PM | N/a
NOV054 | 2024-11-25 19:05 | operation@crystalgroup.in | LAURUS UNIT 6 | VENU BABU | 8913072380 | MANAGER | ARCU4530675 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 16:50 | operation@crystalgroup.in | LAURUS UNIT 6 | ARCU4530675 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTENDED THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH CONDENSOR MOTOR CREATE SOUND SOMETIMES IN RUNNING CONDITION | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER RUN IN SUND CONDITION WITHOUT ANY ALARM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV054 | Carrier - Thinline | Thinline | 3403J00734 | JSL90656192 |  | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 17:04 | operation@crystalgroup.in | YES | NOV080 | 26.11.24 | Consumables, Spares, FOC | LAURUS UNIT 6 | LALAMKONDEV | ARCU4530675 | SITE | FOC | CARRIER-THINLINE | 2025-01-07 18:17 | operation@crystalgroup.in | YES | NOV080 | YES |  |  | 2025-01-08 14:53 | mum.depot@crystalgroup.in | YES | NOV080 | TECHNICIAN |  |  | NA |  |  | 2024-11-23 19:44 | 2024-11-23 |  |  |  |  | ARCU4530675 |  |  |  | Carrier | +12.0C | Clean | Clean |  | Noisy | Clean |  | Need to top up |  | Need to top up |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 7.0B | 9.7A, 9.3A, 9.5A | 402V, 397V, 399V | Not done | Condenser coil heavy dirty King valve need to replace due to leakage Display not showing properly | Condenser coil wash with normal water | King valve 1nos Brizing set 1nos N2 1nos Fillter Drier 1nos Display 1nos Brizing rod 2nos Vacuum pump 1nos R-134a 5kg |  |  | https://drive.google.com/open?id=1AiqFmQEDYc-o6KzLOfnxmXxeQiDGqNzX, https://drive.google.com/open?id=1WrY9WXmbMcifG02a3PSwcjeeftliqr4A | Trip no 056 | No | No | Can be done on next PM | This work done by next PM
NOV055 | 2024-11-25 19:10 | operation@crystalgroup.in | LAURUS UNIT 4 | PHANINDRA VERMA | 7093500971 | MANAGER | MYRU4500613 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 17:10 | operation@crystalgroup.in | LAURUS UNIT 4 | MYRU4500613 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | WE ATTEND THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HAVE CLEAN COIL WITH NORMAL WATER CONTAINER RUN IN SOUND CONDITION WITHOUT ANY ALARM | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV055 | Daikin | Daikin | M005107 | LXE10E136A2 | 24C1 | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-26 17:10 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-26 17:11 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-26 17:11 | operation@crystalgroup.in | NO | [7 empty] | 2024-11-25 19:10 | 2024-11-25 |  |  |  |  | MYRU4500613 |  |  |  | Daikin | +4.5C | Clean |  |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 63KPA, 828KPA | 8.9A,8.7A, 8.8A | 389V, 391V, 392V | Not done | Condenser coil heavy dirty | Condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1TB3J95UTgUgG7X5dFcCt_ns9d08ves4u, https://drive.google.com/open?id=15DLH0pz3ngOhXeW3uSAa4Cw0F7RXV2Cs | Trip no 056 | No | No | Can be done on next PM | N/a
NOV056 | 2024-11-25 19:12 | operation@crystalgroup.in | Laurus Synthesis | LALIT | 9441887788 | MANAGER | TRIU6680994 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 17:14 | operation@crystalgroup.in | LAURUS SYNTHESIS UNIT 2 | TRIU6680994 | 20-REEFER | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | WE HAVE ATTEND THIS UNIT AND FOUND CONTAINER SHOWING AL57 AMBIENT SENSOR DIF TO REPLACE FILTER DRIER RUSTED TO REPLACE AND CONDENSOR COIL HEAVY DIRTY | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER CONTAINER MAINTAIN TEMP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV056 | Carrier - Thinline | Thinline |  | NSG60383780 |  | Used | JSGA623040285 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 17:25 | operation@crystalgroup.in | YES | NOV081 | 26.11.24 | Consumables, Spares, FOC | LAURUS SYNTHESIS UNIT 2 | GUJAPALAM APICC | TRIU6680994 | SITE | FOC | CARRIER-THINLINE | 2025-01-07 18:18 | operation@crystalgroup.in | YES | NOV081 | YES |  |  | 2025-01-08 14:54 | mum.depot@crystalgroup.in | YES | NOV081 | TECHNICIAN |  |  | NA |  |  | 2024-11-25 19:17 | 2024-11-25 |  |  |  |  | TRIU6680994 |  |  |  | Carrier | +3.0C | Clean | Clean |  | Okay | Clean |  | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Rusty |  | 6.6B | 10.0A, 9.7A, 9.9A | 425V, 421V, 423V | Not done | Condenser coil heavy dirty to wash Ambient sensor df Fillter Drier rusted Gas less 2kg EVP motor noisy to bearing replace 4Nos | Condenser coil wash with normal water | Ambient sensor 1Nos Fillter Drier 1nos Bearing 4nos R-134a 2KG |  |  | https://drive.google.com/open?id=1fkrGEyU2z26BT8CJxAIEP2dJWRvL523-, https://drive.google.com/open?id=1o3YwHNhDdgn_2XsnGZDpD7G7fMWbcnQ- | Trip no 056 | Yes | No | Can be done on next PM | Ambient sensor need to replace
NOV063 | 2024-11-26 17:32 | operation@crystalgroup.in | ALPHA DAIRY | MUKHARJEE | 9896904405 | GM | CXRU1042080 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 17:35 | operation@crystalgroup.in | ALPHA DAIRY | CXRU1042080 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | CHECKED AND FOUND CONTAINER BREAKDOWN THEN CHECKED OTHER EQUIPMENTS AND FOUND 3 NOS SENSOR ARE FAULTY NEED TO REPLACE BETTER TO CHANGE ALL SENSOR | CONTAINER RUNNING IN GOOD CONDITION BUT NEED TO REPLACE SS, DSS , EOS FOR STARTING THE CONTAINER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV063 | [7 empty] | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2024-11-26 18:03 | operation@crystalgroup.in | YES | NOV082 | 26.11.24 | Spares, Paid | ALPHA DAIRY | HATHRUS | CXRU1042080 | SITE | PAID | DAIKIN | 2025-02-10 14:52 | operation@crystalgroup.in | YES | JAN036 | YES |  |  | 2024-11-26 14:44 | [9 empty] | 2025-01-17 18:15
NOV064 | 2024-11-26 18:09 | operation@crystalgroup.in | ALPHA DAIRY | MUKHARJEE | 9896904405 | GM | APRU5094288 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-26 18:12 | operation@crystalgroup.in | ALPHA DAIRY | APRU5094288 | 40-REEFER | CARRIER | PREVENTIVE MAINTENANCE | SALE | CHARGEABLE | CHECKED AND FOUND CONTAINER RUNNING IN GOOD CONDITION THEN CHECKED OTHER EQUIPMENTS LIKE ELECTRICAL & MECHANICAL PARTS ALL PAPRTS ARE WORKING IN GOOD CONDITION | CONTAINER RUNNING IN GOOD CONDITION | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV064 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | Ninad | No | PREVENTIVE MAINTENANCE | 2024-11-26 18:24 | operation@crystalgroup.in | YES | NOV083 | 26.11.24 | Consumables, Spares, Paid | ALPHA DAIRY | HATHRUS | APRU5094288 | SITE | PAID | CARRIER-THINLINE | 2025-01-20 09:58 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-20 09:59 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
NOV065 | 2024-11-27 10:40 | operation@crystalgroup.in | RELIANCE | ASLAM M A | 9400277542 | SITE INCHARGE | CICU2094089 | ICE FORMATION | NINAD |  |  | Running with issues |  |  |  | 2024-11-27 15:07 | service@crystalgroup.in | RELIANCE | CICU2094089 | 10 FT BLAST | THERMOKING | SERVICE-ON CALL | LEASE | FOC | TEMPERSTURE NOT PULL DOWN /ICE FORMATION | Internal hot water wash done . | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV065 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 |  | BrandNew |  | SHAHBUDDIN | Yes | ICE FORMATION | 2024-12-23 11:33 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-23 11:34 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-23 11:39 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-05 12:36 | 2024-12-27 |  |  |  |  | CICU2094089 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5B/16.3B | 10/10.1/10.1 | 404/403/404 | Short | Found ICE FORMATION internal floor ares | cleaned floor with what water | No | https://drive.google.com/open?id=1b7zPQEj3KV8uejKu9YZjf5eev7zwUVkL |  |  | NA | No | No | Can be done on next PM | na | na
NOV066 | 2024-11-27 10:56 | operation@crystalgroup.in | RELIANCE | RANVIR SINGH | 9872609126 | SITE INCHARGE | CICU1799140 | ICE FORMATION | NINAD |  |  | Running with issues |  |  |  | 2024-11-27 13:37 | operation@crystalgroup.in | RELIANCE | CICU1799140 | 10-REEFER | THERMOKING | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | SENSORS NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV066 | Thermoking MP-4000 | MP 4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW |  | UMESH |  | ICE FORMATION | 2024-11-27 14:10 | operation@crystalgroup.in | YES | NOV085 | 27.11.24 | Spares, FOC | RELIANCE | RAJPURA | CICU1799140 | SITE | FOC | TK-MP4000 | 2024-11-27 14:13 | operation@crystalgroup.in | YES | NOV085 | YES |  |  | 2024-11-27 14:14 | operation@crystalgroup.in | YES | NOV085 | COURIER | [5 empty] | 2024-12-17 12:33 | 2023-11-20 |  |  |  |  | CICU1799140 |  |  |  | Thermo king | -4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/18 BAR | 9.9/9.8/9.9 | 402/403/402 | Short | UNIT WORKING FINE | NO | No | https://drive.google.com/open?id=1jbOrAsaWBkmwNCY_yzbAd2hnYGfBTXd- |  |  | NA | No | No | Can be done on next PM | NO | NA | technician@crystalgroup.in
NOV068 | 2024-11-27 10:58 | operation@crystalgroup.in | RELIANCE | RANVIR SINGH | 9872609126 | SITE INCHARGE | CXRU1045453 | MOTOR MAKING NOISE, MOTOR WINDING BURNT | NINAD |  |  | Running with issues |  |  |  | 2024-11-27 11:01 | operation@crystalgroup.in | RELIANCE | CXRU1045453 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKEDD AND FOUND CONTAINER WORKING GOOD BUT TEMPERATURE COMING SLOW SO REAYIFY THE PROBLEM & FOUND (EVP MOTOR) L/S NOT WORKING IN LOW SPEED SO TEMPERATURE GO DOWN SLOWLY AFTR -5C | CONTAINER RUNNING GOOD BUT THEY OPEN DOOR EVERY 40 TO 45 MIN NEED TO NOT OPEN DOOR FOR ATLEAST 4 HOURS IN CONTINOUS RUNNING NEED TO CHANGE EVP MOTOR ASAP | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV068 | DAikin | LXE10E147F2 | M001754 | K31501144051 | DECOS 3F 2606 / 1 | used |  | UMESH |  | MOTOR MAKING NOISE, MOTOR WINDING BURNT | 2024-11-27 11:09 | operation@crystalgroup.in | YES | NOV084 | 27.11.24 | Spares, FOC | RELIANCE | RAJPURA | CXRU1045453 | SITE | FOC | DAIKIN | 2024-11-27 12:15 | operation@crystalgroup.in | YES | NOV084 | YES | https://drive.google.com/open?id=1o7HeeCHMJwdraKCSqk5BW5ZEktplZroW |  | 2024-11-27 12:16 | operation@crystalgroup.in | YES | NOV084 | TECHNICIAN | [5 empty] | 2025-01-17 18:15 | 2024-11-27 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1MFeWaury1Nh5rDmcDpc4Mz6dgmbMIipk |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
NOV067 | 2024-11-27 14:18 | operation@crystalgroup.in | RELIANCE | RANVIR SINGH | 9872609126 | SITE INCHARGE | TCLU1130265 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-27 14:22 | operation@crystalgroup.in | RELIANCE | TCLU1130265 | 40-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | CONTAINER RUNN IN GOOD CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV067 | Thermoking | MP-4000 |  |  |  | Refurbished |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-11-27 14:22 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-27 14:23 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-27 14:23 | operation@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:12 | 2024-11-20 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | -20*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1Q8HX44N_3XElXhfroIVa1oRdgJzNIFC0 |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
NOV069 | 2024-11-27 15:09 | operation@crystalgroup.in | ZEPTO | NARENDRA | 9717519295 | MANAGER | GESU9460634 | TEMPERATURE ISSUE DOOR NOT CLOSING | NINAD |  |  | Running with issues |  |  |  | 2024-11-27 15:34 | operation@crystalgroup.in | ZEPTO | GESU9460634 | 40-REEFER | CARRIER | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE DOOR NOT CLOSING | NEEED TO CORRECT WIRING | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV069 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | UMESH |  | TEMPERATURE ISSUE DOOR NOT CLOSING | 2024-11-27 15:34 | operation@crystalgroup.in | NO | [9 empty] | 2024-11-27 15:34 | operation@crystalgroup.in | NO |  |  |  |  | 2024-11-27 15:34 | operation@crystalgroup.in | NO | [7 empty] | 2024-12-17 12:45 | 2024-11-21 |  |  |  |  | GESU9460634 |  |  |  | Carrier | +2.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/180 PSIG | 12.8/12.9/12.8 | 406/407/406 | Short | UNIT WORKING A FINE | NA | No | https://drive.google.com/open?id=1VDXmSWqzZcSgZNilTaG0g358_b7Rrepu |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in
NOV070 | 2024-11-28 12:46 | crm@crystalgroup.in | RELIANCE | NA | 9990063655 | NA | CICU3876586 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 13:02 | crm@crystalgroup.in | RELINACE | CICU3876586 | 10FT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | "CHECKED AND FOUND CONTAINER RUNNING GOOD CONDENSOR COIL CLEANED, COMPRESSOR MOTORS AND VALVES SENSORS WORKING IN GOOD CONDITION AND TAINING PROVIDED TO MR.PRAMOD RANA." | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV070 | Thermoking | Magnum + | 22A4227AT | ABC782800322010496 | ABC782900321510417 | Brand New |  | UMESH |  | PREVENTIVE MAINTENANCE | 2024-11-28 13:12 | crm@crystalgroup.in | NO | [9 empty] | 2024-11-28 13:15 | crm@crystalgroup.in | NO |  |  |  |  | 2024-11-28 13:16 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-17 12:49 | 2024-11-23 |  |  |  |  | CICU3876586 |  |  |  | Thermo king | -30C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .0.9/20 BAR | 9.9/9.8/9.9 | 407/406/407 | Short | UNIT WORKING AS FINE | NA | No | https://drive.google.com/open?id=1ZW5m45vCdCo_huKycGwxZcL-V3GR4LvB |  |  | NA | No | No | Can be done on next PM | NO | NA | technician@crystalgroup.in
NOV071 | 2024-11-28 12:49 | crm@crystalgroup.in | RELIANCE | NA | 9990063655 | NA | CXRU1043912 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 13:10 | crm@crystalgroup.in | RELIANCE | CXRU1043912 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MEASURE | CONDENSOR CLEANED PROPERLY ,NO FAULT IN SYSTEM. CONATINER RUNNING IN GOOD CONDITION. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV071 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-11-28 13:12 | crm@crystalgroup.in | NO | [9 empty] | 2024-11-28 13:15 | crm@crystalgroup.in | NO |  |  |  |  | 2024-11-28 13:16 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-17 12:00 | 2024-11-28 |  |  |  |  | CXRU1043912 |  |  |  | Daikin | -22C | Clean | Clean |  | Okay | Clean |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay |  | Clean |  | 0/170 | 9.8/9.9/908 | 401/402/401 | Not done | UNIT WORKING AS FINE WITH AL E205 | NA | Yes | https://drive.google.com/open?id=1JmD-AI3LCYlEChwGe9skyAUouCppAAe8 |  |  | NA | Yes | Yes | Can be done on next PM | NOT | PT CT & RPP - CONTROLLER SUSECTED | technician@crystalgroup.in
NOV072 | 2024-11-28 13:24 | crm@crystalgroup.in | RELIANCE | NA | 9990063655 | NA | CXRU1040322 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 13:31 | crm@crystalgroup.in | RELIANCE | CXRU1040322 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PRENVENTIVE MEASURE | CONTAINER IN GOOD CONDITION, CONDENSER COIL CLEANED, ALL EQUIPMENTS (ELECTRICAL MECHENICAL ARE WORKING | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV072 | [7 empty] | UMESH |  | PREVENTIVE MAINTENANCE | 2024-11-28 13:32 | crm@crystalgroup.in | NO | [9 empty] | 2024-11-28 13:33 | crm@crystalgroup.in | NO |  |  |  |  | 2024-11-28 13:33 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-17 11:45 | 2024-11-23 |  |  |  |  | CXRU1040322 |  |  |  | Daikin | -22C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Need to replace |  | Okay | Okay | Okay | Done | Clean |  | -1/100 PSIG | 12.8/12.9/12.8 | 399/401/401 | Not done | WORK DONE & WORKING AS FINE | CONTAINER IS WORKING FINE | No | https://drive.google.com/open?id=1XwQfV__WvEYyMDg5S9tbW0OVov7QeY_j https://drive.google.com/open?id=1YVdLEpBiFk_z_U9jLrvZ4w6pCN2Z60ce |  |  | NA | No | No | Can be done on next PM | NO | NA | technician@crystalgroup.in
NOV073 | 2024-11-28 16:37 | operation@crystalgroup.in | Lupin Limited | AKASH GORLE | 9370588166 | WAREHOUSE MANAGER | CCLU1036859 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 17:41 | crm@crystalgroup.in | LUPIN -THANE | CCLU1036859 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE | PAY SERVICE DONE CHECKED UNIT OPERATION MAIN UINT , ALL MOTOR ,GAS LEVEL, PRESSURE UNIT CLEAN CONDENSOR COIL, CHILLED ALL SENSOR READING , WORKING AS FINE , | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV073 | Carrier |  |  |  |  | Used | JSGA623040314 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2024-11-28 17:55 | crm@crystalgroup.in | NO | [9 empty] | 2024-11-28 17:59 | crm@crystalgroup.in | NO |  |  |  |  | 2024-11-28 18:00 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:05 | 2024-11-27 |  |  |  |  | CCLU1036859 |  |  |  |  | +5*C | Clean | [22 empty] | Okay | [7 empty] | NA | NA | No | https://drive.google.com/open?id=1zQBF_zNTY1momaHZNZM-ZybfbCW45spT |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
NOV057 | 2024-11-28 16:38 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | NA | NA | APRU5000210 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 16:45 | crm@crystalgroup.in | LAURUS UNIT-1 | APRU5000210 | 40 FT | PREVENTIVE MAINTENANCE | PREVENTIVE MAINTENANCE | LEASE | FOC | ATTEND THE SITE AND FOUND , CONDENSOR COIL NORMAL, DIRTY TO WASH, KEYPAD NOT WORKING NEED TO REPLACE WITH DISPLAY | CONDESOR COIL WASHED WITH NORMAL WATER, CONTAINER RUN A SOUND WITHOUT ANY ALRAM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV057 | Carrier - Thinline | Thinline | 2594J02559 | GGCR80067211 |  | Refurbished |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-30 11:26 | operation@crystalgroup.in | YES | NOV096 | 30.11.24 | Consumables, Spares, FOC | LAURUS UNIT 1 | PARWADA | APRU5000210 | SITE | FOC | CARRIER-THINLINE | 2025-01-07 18:20 | operation@crystalgroup.in | YES | NOV096 | YES |  |  | 2025-01-08 14:58 | mum.depot@crystalgroup.in | YES | NOV096 | TECHNICIAN |  |  | NA |  |  | 2024-11-27 21:12 | 2024-11-27 |  |  |  |  | APRU5000210 |  |  |  | Carrier | +27.0C | Dirty | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8.6B | 9.1A, 9.0A, 8.7A | 402V, 399V, 400V | Not done | Condenser coil heavy dirty EVP motor noisy Display balar to replace Keypad not working EVP motor noisy | Condenser coil wash with normal water | Display 1nos Keypad 1nos Bearing 4nos Controller need to update with ml3i Software card 1nos |  |  | https://drive.google.com/open?id=1FFrg733FoBCgONwCXjOs1UeGnJOlz1Hm, https://drive.google.com/open?id=1M-bCpBJ_5n9Kv_uzhU8fnoxuzedHfFMY | Trip no 056 | Yes | No | Can be done on next PM | Display need to replace, keypad need to be replaced, motor bearing need to be replaced,and controller need to be upgrade with ml3i
NOV058 | 2024-11-28 16:47 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | NA | NA | CXRU1037308 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 17:00 | crm@crystalgroup.in | LAURUS UNIT - 1 | CXRU1037308 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE,CONTAINER SHOWING ALRAM E401 A | WASHED CONDENSOR COIL WITH NORMAL WATER REPACED SUPPLY SENSOR 2 NOS , CONTAINER RUNNING SOUND CONDITION WITHOUT ANY ALRAM. | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV058 | Daikin | LXE10E147F2 | M000334 | K31505146690 | DECOS 3F 2553 / 1 | Used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-11-28 17:01 | crm@crystalgroup.in | NO | [9 empty] | 2024-11-28 17:01 | crm@crystalgroup.in | NO |  |  |  |  | 2024-11-28 17:02 | crm@crystalgroup.in | NO | [7 empty] | 2024-11-27 21:18 | 2024-11-27 |  |  |  |  | CXRU1037308 |  |  |  | Daikin | +1.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 62KPA 1012KPA | 8.8A, 8.3A, 8.5A | 415V, 411V, 413V | Not done | Condenser coil wash heavy dirty Showing Alaram E401 | Condenser coil wash with normal water | N/a |  |  | https://drive.google.com/open?id=1s-AOUcEFQsILKq1Eh6I1i6DtwkO8j40r, https://drive.google.com/open?id=1Jc9jeDNByfTegq8XfdJOf1OAjqVjFBuo | Trip no 056 | No | No | Can be done on next PM | N/a
NOV059 | 2024-11-28 17:07 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | NA | NA | PCIU6006639 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-28 17:14 | crm@crystalgroup.in | LAURUS UNIT 1 | PCIU6006639 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTANACE , DISPLAY NOT SHOWING SET POINT , CONDENSOR COIL DIRTY | CONDENSOR COIL WITH NORMAL WATER, CONTAINER RUNINING SOUND CONDITION WITHOUT ANY ALRAM | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV059 | Daikin |  |  |  |  | used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-11-30 12:18 | operation@crystalgroup.in | YES | NOV097 | 30.11.24 | Spares, FOC | LAURUS UNIT 1 | PARWADA | PCIU6006639 | SITE | FOC | DAIKIN | 2025-01-07 18:20 | operation@crystalgroup.in | YES | NOV097 | YES |  |  | 2025-01-08 14:59 | mum.depot@crystalgroup.in | YES | NOV097 | TECHNICIAN |  |  | NA |  |  | 2024-11-27 21:24 | 2024-11-27 |  |  |  |  | PCIU6006639 |  |  |  | Daikin | -2.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 14KPA 1077KPA | 8.9A, 8.5A, 8.6A | 411V, 409V, 410V | Not done | Condenser coil heavy dirty Display df | Condenser coil wash with normal water | Display 1nos |  |  | https://drive.google.com/open?id=1oSWjjzOdjuMBo3px3UlFSvJ4bYPY2XiQ, https://drive.google.com/open?id=1lR7lUejM4E1xIJ7-HsdcirOIcqzbR7tB | Trip no 056 | Yes | No | Can be done on next PM | Display need to replace
NOV060 | 2024-11-30 12:46 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.Hastha | 8924660331 | Jr. Executive | KKFU6706142 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-11-30 12:59 | crm@crystalgroup.in | AJINOMOTO BIO | KKFU6706142 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE, | REPLACED SENSOR | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV060 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040294 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-17 13:09 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-17 13:10 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 17:39 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 19:37 | 2024-11-29 |  |  |  |  | KKFU6706142 |  |  |  | Carrier | +20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 13.0B | 10.0A, 9.7A,9.9A | 411V, 409V,410 | Not done | Supply sensor df Condenser coil normal dirty | Supply sensor replace 2nos Condenser coil wash with normal water | N/a | https://drive.google.com/open?id=1xH4WGsHTChrnOn2C0fFcsOo73wXd6crY, https://drive.google.com/open?id=1b20EOP2H12D6N7i7fMctYsGgNHWXvUBb |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
NOV075 | 2024-11-30 15:18 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HARSTHA | 8924660331 | JR.EXECUTIVE | KKFU6994964 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-03 16:16 | crm@crystalgroup.in | AJINOMOTO BIO | KKFU6994964 | 40FT | CARRIER | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | REPLACE SUPPLY SENSOR , FULLTER REPLACE AND CONDENSOR COIL WASH WITH NORMAL WATER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV075 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-31 17:30 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-07 18:21 | operation@crystalgroup.in | NO |  |  |  |  | 2025-01-14 15:29 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 19:43 | 2024-11-29 |  |  |  |  | KKFU6994964 |  |  |  | Carrier | +20.0C | Clean | Clean |  | Okay | Clean | Okay |  |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 15.8B | 10.0A, 9.7A, 9.9A | 406V, 403V, 405V | Not done | Supply sensor df 2 nos Fillter Drier rusted Qunich valve leakage Condenser coil normal dirty | Supply sensor replace 2nos Fillter Drier replace 1nos Condenser coil wash with normal water | Qunich valve carrier | https://drive.google.com/open?id=1SyAZ5eW6DVAhXV4fZb4z5Kh4wsm4RlmN, https://drive.google.com/open?id=1I9kVK4KXA8wdczkuFbmI0Lan4FDSS_Du |  |  | Trip no 056 | Yes | No | Can be done on next PM | Qunich valve need to be replaced
NOV076 | 2024-11-30 15:26 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HASTH | 8924660331 | JR.EXCUTIVE | KKFU6712079 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-12 10:58 | service@crystalgroup.in | AJINOMOTO BIO | KKFU6712079 | 40 FT | carrier thine line | SERVICE-AT SITE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV076 | Carrier - Thinline | Thinline |  | 69NT40541321 |  | brand New | JSGA623040320 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-17 13:18 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-17 13:19 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 17:37 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 19:48 | 2024-11-29 |  |  |  |  | KKFU6712079 |  |  |  | Carrier | +20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.0B, 14.2B | 10.0A, 9.6A, 9.8A | 413V, 410V, 411V | Not done | Fillter Drier rusted Condenser coil normal dirty | Fillter Drier replace 1nos Condenser coil wash with normal water | N/a | https://drive.google.com/open?id=1Sfj8JvXomQyj6oi9NNXJLmAv2bieSO1U, https://drive.google.com/open?id=14y8QJvFQJh-hcAjVEO-K7ZtNsEV_beRH |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
NOV077 | 2024-11-30 15:38 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HASTHA | 8924660331 | JR.EXECUTIVE | TITU9930069 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-12 11:03 | service@crystalgroup.in | AJINOMOTO BIO | TITU9930069 | 40 FT | THERMOKING | SERVICE-AT SITE | LEASE | FOC | FOUND CONDENSER COIL DIRTY | CLEAN CONDENSER WIT FRESH WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV077 | Thermoking | MP-4000 | NA | NA | NA | USED |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-17 17:33 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-17 17:35 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 17:38 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 19:53 | 2024-11-29 |  |  |  |  | TITU9930069 |  |  |  | Thermo king | +20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 16.4B | 6.0A, 5.7A, 5.7A | 413V, 410V, 411V | Not done | Condenser coil normal dirty Internal 1 light not working | Condenser coil wash with normal water | Led light 3nos | https://drive.google.com/open?id=1eqseCrhFNSv76lqp3aggdX7gG1zuArVE, https://drive.google.com/open?id=1ttaTatK3E0tXvKjclB2D41nGwe7jG4cg |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
NOV078 | 2024-11-30 15:40 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HASTH | 8924660331 | JR.EXECUTIVE | BMOU9766180 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-12 11:12 | service@crystalgroup.in | AJINOMOTO BIO | BMOU9766180 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | FOUND SUPPLY SENSOR 2 NOS DEFECTIVE E401 & E402 | Replaced supply sensor with new 2 nos & clean condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV078 | Daikin |  |  |  |  | used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-17 17:34 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-17 17:36 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 17:38 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 19:57 | 2024-11-29 |  |  |  |  | BMOU9766180 |  |  |  | Daikin | +4.8C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 5KPA, 909KPA | 8.7A, 8.3A, 8.5A | 403V, 400V, 401V | Not done | Supply sensor df 2 nos Condenser coil dirty | Replace supply sensor 2nos Condenser coil wash with normal water | N/a | https://drive.google.com/open?id=1GGBj9RCWMKZWI9k6gtrob_t-RADLWYCs, https://drive.google.com/open?id=1s9TomN24W_mLdYSCq-mytqXb18NjOfGV |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
NOV079 | 2024-11-30 15:50 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HARSTA | 8924660331 | JR.EXECUTIVE | HDMU5537036 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-12 11:20 | service@crystalgroup.in | AJNOMOTO BIO | HDMU5537036 | 40 ft | carrier thine line | SERVICE-AT SITE | LEASE | FOC | found less gas in system due to that compress or run continuously. | clean condenser coil with fresh water | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV079 | Carrier | Thineline |  |  |  | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-17 17:35 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-17 17:36 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 17:39 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-11-29 20:03 | 2024-11-29 |  |  |  |  | HDMU5537036 |  |  |  | Carrier | +21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8.8B | 9.0A, 9.1A, 9.2A | 415V, 413 V, I 411V | Not done | We observed this unit gas level low | N/a | First need to top up gas 2.50kg | https://drive.google.com/open?id=187G-5RULjSDtuljFIF2qXQ_L6hSC2IO6, https://drive.google.com/open?id=1Gr4c5WXtpuaejYNhX1s_5AVzQIG4ATl9 |  |  | Trip no 056 | Yes | Yes | Urgent | First need to top up gas R-134a
DEC001 | 2024-12-03 14:54 | crm@crystalgroup.in | Tanish Lab | RAVI KUMAR | 8922354192 | NA | CXRU1040451 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-03 15:10 | crm@crystalgroup.in | TANISH LAB | CXRU1040451 | 40 FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | SHEET KEY REPLACED CONDENSOR COIL WASHED WITH NORMAL WATER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC001 | DAikin | LXE10E147F2 | M001991 | K31408134485 | DECOS 3F 2551 / 1 | Used |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2024-12-13 18:20 | mum.depot@crystalgroup.in | YES | DEC014 | 2024-12-13 | Spares | Tanish Lab | MANIPETTA | CXRU1040451 | SITE | FOC | DAIKIN | 2024-12-18 15:19 | mum.depot@crystalgroup.in | YES | DEC001 | YES |  |  | 2024-12-31 16:41 | mum.depot@crystalgroup.in | YES | NA | COURIER | 1645339051 | Patel courier | courier | https://drive.google.com/open?id=1SUHn977Q5xbWLRzOnWUfWev09-sL0Hl3 |  | 2024-12-01 20:41 | 2024-12-01 |  |  |  |  | CXRU1040451 |  |  |  | Daikin | +19.6C +22.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 33KPA,189KPA, 847KPA,976KPA | 6.9A7.9A, 6.3A7.5A, 6.5A7.7A | 389V, 385V, 387V | Not done | Condenser coil dirty Sheet Key hanging Sheet Key need to be replaced | Condenser coil wash with normal water Sub zero controller setting as per container temperature | Sheet Key 1nos Bolt for keypad fixing 4nos Washer 4nos Nut 4nos | https://drive.google.com/open?id=1nHTV2wdBL7J8M38gp-sZwuVHhoo1KQx3, https://drive.google.com/open?id=1_lqogqSl2UXvfbCJePDMwQxF_uwWaUUJ |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
DEC002 | 2024-12-03 14:56 | crm@crystalgroup.in | TANISH LAB | RAVI KUMAR | 8922354192 | NA | TRLU1741601 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-03 15:14 | crm@crystalgroup.in | TANISH LAB | TRLU1741601 | 40FT | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | CLEAN CONDENSOR COIL WITH NORMAL WATER CONATINER RUN IN SOUND CONDITION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC002 | Thermoking | Thermoking |  |  |  | used |  | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-12-03 15:26 | crm@crystalgroup.in | NO | [9 empty] | 2024-12-03 15:27 | crm@crystalgroup.in | NO |  |  |  |  | 2024-12-03 15:31 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-01 20:44 | 2024-12-01 |  |  |  |  | TRLU1741601 |  |  |  | Thermo king | +18.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 17.0B | 6.3A, 5.8A, 6.0A | 390V, 389V,391V | Not done | Condenser coil normal dirty | Condenser coil wash with normal water | N/a | https://drive.google.com/open?id=17pjiiGuc2hASHypm3oIWHCGmAPeXwf-a, https://drive.google.com/open?id=1dQD-RIOXwXpL3on61sTSHAVI1xiLBmYr |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
DEC003 | 2024-12-03 14:59 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | SARUKMANGADA REDDY | NA | MANAGER | TITU7251080 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-03 15:24 | crm@crystalgroup.in | APITARLO PHARMA | TITU725080 | 40FT | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | REPLACED DISPLAY COMPRESSOR PAINT WITH SPRAY AND CONDENSOR COIL WASL WITH NORMAL WATER | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC003 | [7 empty] | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-12-03 15:26 | crm@crystalgroup.in | NO | [9 empty] | 2024-12-03 15:28 | crm@crystalgroup.in | NO |  |  |  |  | 2024-12-03 15:31 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-02 15:06 | 2024-12-02 |  |  |  |  | TITU7250080 |  |  |  | Daikin | -22.5C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 31KPA, 981KPA | 8.6A,8.3A 8.5A | 407V, 403V, 405V | Not done | Compressor rusted Display not showing temperature properly Fillter Drier rusted Condenser coil heavy dirty | Display replace 1nos Fillter Drier replace 1nos Compressor paint done Condenser coil wash with normal water | Sheet key 1nos in next pm | https://drive.google.com/open?id=1qAHWWmHPY2QiFq_hZM7w7JOy-MnkusI1, https://drive.google.com/open?id=1PSXSo4-JJxWJPsdeUN3mAiXCR2ifztpa |  |  | Trip no 056 | No | No | Can be done on next PM | N/a
NOV074 | 2024-12-05 12:36 | operation@crystalgroup.in | RELIANCE | RANVIR SINGH | 9872609126 | SITE ENGINEER | CICU3876586 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-05 12:40 | operation@crystalgroup.in | RELIANCE | CICU3896586 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | CHECKED & FOUND TEMPERATURE ISSUE TEMPERATURE NOT PULLING DOWN BELOW -11C SO CHECKED & FOUND SOME SENSOR ARE NOT WORKING SO REMOVE SENSOR AND REFIX | CONTAINER RUNNING IN GOOD CONDITION | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV074 | [7 empty] | UMESH |  | PREVENTIVE MAINTENANCE | 2024-12-05 12:40 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-05 12:40 | operation@crystalgroup.in | NO |  |  |  |  | 2024-12-05 12:41 | operation@crystalgroup.in | NO | [7 empty] | 2024-12-13 15:44 | 2024-12-05 |  |  |  |  | CICU3876586 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA/22 B | 9.8/9.9/9.8 | 405/405/406 | Short | CHECKED & FOUND TEMPERATURE ISSUE TEMPERATURE NOT PULLING DOWN BELOW -11C SO CHECKED & FOUND SOME SENSOR ARE NOT WORKING SO REMOVE SENSOR AND REFIX | AFTER WORKING THE REEFER UNIT RUNNIG IN NORMAL CONDATION | No | https://drive.google.com/open?id=12CvNqw7AYcakfVaV3-TpzTxOQ5pk_D92 |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC004 | 2024-12-05 13:23 | operation@crystalgroup.in | DR REDDY CTO 06 | KISHOR | 9676755199 | SITE PERSON | CXRU1033616 | PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-05 13:24 | operation@crystalgroup.in | DR REDDY CTO 6 | CXRU1033616 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | PREVENTIVE MAINTENANCE | ONE SENSOR REPLACED | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC004 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | VIRENDRA |  | PREVENTIVE MAINTENANCE | 2024-12-05 13:25 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-05 13:26 | operation@crystalgroup.in | NO |  |  |  |  | 2024-12-05 13:26 | operation@crystalgroup.in | NO | [7 empty] | 2024-12-06 15:50 | 2024-12-04 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | +3.0C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 82KPA 996K0A | 8.2A, 8.0A, 7.9A | 396V, 393V, 395 | Not done | Showing Alaram inlet sensor df Condenser coil heavy dirty | Replace inlet sensor Condenser coil wash with normal water | No | https://drive.google.com/open?id=1oW0cskB4ME4shj1p6Lo-me1IDCjSwdok, https://drive.google.com/open?id=1p-AVRott4Hsk-tth9CIOXP1sgCjuDd7b |  |  | Trip no 056 | No | No | Can be done on next PM | N/a | N/a
DEC007 | 2024-12-05 14:51 | operation@crystalgroup.in | SYMBIOTEC | BALKRISHNA PRAJAPATI | 7747937030 | EXECUTIVE | TCLU1904607 | FLUCTUATIONS IN TEMEPRATURE, PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-05 14:52 | operation@crystalgroup.in | SYMBIOTEC | TCLU1904607 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | BREAKDOWN | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC007 | Daikin | Daikin |  |  |  | Used |  |  |  | FLUCTUATIONS IN TEMEPRATURE, PREVENTIVE MAINTENANCE | 2024-12-05 14:58 | operation@crystalgroup.in | YES | DEC003 | 05.12.24 | Spares, Paid | SYMBIOTEC | MUKTSAR | TCLU1904607 | SITE | PAID | DAIKIN | 2024-11-19 18:30 | [6 empty] | 2024-11-19 18:31 | [9 empty] | 2025-01-17 18:12
DEC008 | 2024-12-05 15:06 | operation@crystalgroup.in | Jubliant Consumer Pvt Ltd | ATUL TYAGI | 9717318538 | MANAGER | GRMU3607418 | FLUCTUATIONS IN TEMEPRATURE, PREVENTIVE MAINTENANCE | NINAD |  |  | Preventive Maintenance |  |  |  | 2024-12-05 15:07 | operation@crystalgroup.in | JUBLIENT | GRMU3607418 | 20-REEFER | DAIKIN | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE ISSUE | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC008 | Daikin |  |  |  |  | Used |  | VIRENDRA | Yes | FLUCTUATIONS IN TEMEPRATURE, PREVENTIVE MAINTENANCE | 2024-12-05 15:16 | operation@crystalgroup.in | YES | DEC004 | 05.12.24 | Consumables, Spares, FOC | JUBLIENT | NOIDA | GRMU3607418 | SITE | FOC | DAIKIN | 2024-12-16 18:28 | mum.depot@crystalgroup.in | YES | DEC008 | YES |  |  | 2024-11-26 14:44 | [9 empty] | 2025-01-17 18:15
DEC009 | 2024-12-06 12:34 | operation@crystalgroup.in | RELIANCE | MOHIT RAI | 9023419864 | ASSISTANT MANAGER | CICU2779935 | FLUCTUATIONS IN TEMEPRATURE, MATERIAL IS NOT FREEZING | NINAD |  | Ahmedabad | Running with issues |  |  |  | 2024-12-06 17:58 | service@crystalgroup.in | RELIANCE | CICU2779935 | 10FT | MP4000 | SERVICE-ON CALL | LEASE | FOC | FLUCTUATIONS IN TEMEPRATURE, PCM IS NOT FREEZIN. WRONG STACK PCM FRO BLAST | GIDE TO KEEP RIGHTLY PCM STACK . UNDER OVSERVATION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC009 | Thermoking | Magnum Plus | E0GM030274 | ABC782800322010476 |  | BrandNew |  | RAMIZ | No | FLUCTUATIONS IN TEMEPRATURE, MATERIAL IS NOT FREEZING | 2024-12-13 18:23 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-18 15:24 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-18 15:25 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-21 18:08 | 2025-02-19 |  |  |  |  | CICU2779935 |  |  |  | Thermo king | -40*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /20.3 | 9.8/9.8/9.7 | 412/411/412 | Not done | NA | NA | No | https://drive.google.com/open?id=18qLPRktP1JuF2cuj09ljrE0rZhjNjLtj, https://drive.google.com/open?id=1nGhf8gWDp8Ob9U3kQ7mdOZ8ND8hJN83c |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
DEC010 | 2024-12-06 12:39 | operation@crystalgroup.in | RELIANCE | MOHIT RAI | 9023419864 | ASSISTANT MANAGER | CICU2779909 | MATARIAL IS NOT FREEZING | NINAD |  | Ahmedabad | Running with issues |  |  |  | 2024-12-06 18:00 | service@crystalgroup.in | RELIANCE | CICU2779909 | 10 FT | MP4000 | SERVICE-ON CALL | LEASE | FOC | FLUCTUATIONS IN TEMEPRATURE, PCM IS NOT FREEZIN. WRONG STACK PCM FRO BLAST | GIDE TO KEEP RIGHTLY PCM STACK . UNDER OVSERVATION | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC010 | Thermoking | Magnum Plus | E0GM030263 | ABC782800322010201 |  | BrandNew |  | RAMIZ | No | MATARIAL IS NOT FREEZING | 2024-12-13 18:23 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-18 15:24 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-18 15:25 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-21 18:03 | 2025-02-19 |  |  |  |  | CICU2779909 |  |  |  | Thermo king | -35*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /20.9 | 9.7/9.7/9.6 | 417/416/417 | Not done | NA | NA | No | https://drive.google.com/open?id=1V39tq_6nYkXMImuY36G-LJXh0FMYS675, https://drive.google.com/open?id=1jHwHMbWle4-a0zVWHc_H1Mq-ZS-NvuQb |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
DEC011 | 2024-12-06 17:22 | operation@crystalgroup.in | Gennova Biopharmaceuticals Ltd | PRAKASH RAUT | 9860979609 | SR MANAGER | CICU1938565 | OQ (DOCUMENTATION) | NINAD | NA |  | Running with issues |  |  |  | 2024-12-12 10:26 | service@crystalgroup.in | GENNOVA BIOPHARMA | CICU1938565 | 20FT | THERMOKING | INSTALLATION | LEASE | FOC | OQ (DOCUMENTATION) | OQ (DOCUMENTATION) DONE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC011 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | SHAHBUDDIN |  | OQ (DOCUMENTATION) | 2024-12-13 11:52 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-13 11:53 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-13 11:54 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-14 16:05 | 2024-12-06 |  |  |  |  | CICU1938565 |  |  |  | Thermo king | +4.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/ 18 | 9.8/9.9/9.8 | 404/404/405 | Not done | IQ & OQ COMPLATED | NA | No | https://drive.google.com/open?id=1x34gfuVCS9-suvpT3YR82dxbTaNnI-sS, https://drive.google.com/open?id=1EUG7qXsymKZ-FPxqm47p1xpk_DqYhQ_g |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC012 | 2024-12-07 13:25 | rahul.gawade@crystalgroup.in | Qwik Supply | Amiyalochan Panda | 7024101572 | Operation Engineeriner | TRIU8850831 | Frequent power ON/OFF | Rahul Gawade | amiyalochan.panda@qwick.co.in |  | Running with issues |  |  |  | 2024-12-07 17:51 | service@crystalgroup.in | RELIANCE DC | TRIU8850831 | 40FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | Frequent power ON/OFF & AL27, 22, 63,15,52 TEMPERATURE NOT PULL DOWN | NEED REPLACED CONTROLLER L3i C/R 12-5501 , SUSPECTED Carrier Contactor 12A, Carrier supply sensor , Carrier Return Sensor, Carrier Contactor 30A Carrier Defrost Sensor TRANSFORMER, SERVICE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC012 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA622180048 | RAMIZ |  | Frequent power ON/OFF | 2024-12-13 12:03 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-13 12:04 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-13 12:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-07 18:17 | 2024-12-07 |  |  |  |  | TRIU8850831 |  |  |  | Carrier | -21C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | 404404403 | Not done | Frequent power ON/OFF & AL27, 22, 63,15,52 TEMPERATURE NOT PULL DOWN | "NEED REPLACED CONTROLLER L3i C/R 12-5501 , SUSPECTED Carrier Contactor 12A, Carrier supply sensor , Carrier Return Sensor, Carrier Contactor 30A Carrier Defrost Sensor TRANSFORMER, SERVICE " | NO | https://drive.google.com/open?id=1PoMuHqA2uiUwhOIS6E5_JK6Z8KxKp3cl |  |  | NO | Yes | Yes | Urgent | Frequent power ON/OFF & AL27, 22, 63,15,52 TEMPERATURE NOT PULL DOWN | Carrie Controller ML3i C/R 12-55012 Carrier Contactor 12A C/R 10-00431-06 Carrier supply sensor C/R 12-00395-01SV Carrier Return Sensor C/R 12-00500-01 Carrier Contactor 30A C/R 10-00431-07 Carrier Defrost Sensor C/R 24-00006-20 TRANSFORMER, SERVICE c/R 10-00332-21SV
DEC014 | 2024-12-09 15:11 | rahul.gawade@crystalgroup.in | Ola, Krishnagiri, Tamil Nadu | Martien Joseph |  | Senior Associate | TCLU1906493 | Compressor Rusted | Ramiz | martien.j@olaelectric.com |  | Running with issues |  |  |  | 2024-12-09 15:27 | service@crystalgroup.in | OLA | TCLU1906493 | 20 FT | DAIKIN | SERVICE-ON CALL | LEASE | FOC | COMPRESSOR RISTED & CONDENSER COIL NORMAL DIRTY | NEED TO PAINT COMPRESSOR BOTTOM | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC014 | Daikin | Daikin |  |  |  | Used | JSGA623040305 | RAMIZ | No | Compressor Rusted | 2024-12-13 18:25 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-18 15:23 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-18 15:23 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-05 16:59 | 2024-12-09 |  |  |  |  | TCLU1906493 |  |  |  | Daikin | + | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 05B/12B | 10.1/10/10.1 AMPS | 410/411/410 | Not done | Found condenser coil normal dirty & compressor bottom normal rusted | before visit need shout down permeation & the reefer unit working good condition | No | https://drive.google.com/open?id=1TlWDzAU0eeaAHf7qBNpNnzyWW9x4mYrl, https://drive.google.com/open?id=1HAO9UENBW8IZcmgPaoCGBsl_gT3QuKb2 |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
DEC016 | 2024-12-09 20:10 | service@crystalgroup.in | ZEPTO | Vikas Shidore |  | Operation executive | TITU9928040 | FLUCTUATIONS IN TEMEPRATURE | RAHUL | vikas.shidore@zeptonow.com |  | Running with issues |  |  |  | 2024-12-09 20:15 | service@crystalgroup.in | ZEPTO | TITU9928040 | 40 FT | THERMOKING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERSTURE NOT PULL DOWN | SUSPECTED TO LESS GAS OR COMPRESSOR CONTACTOR DEFECTIVE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC016 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | SHUBHAM |  | FLUCTUATIONS IN TEMEPRATURE | 2024-12-10 12:15 | operation@crystalgroup.in | YES | DEC009 | 2024-12-10 | FOC | ZEPTO | PUNE | TITU9928040 | SITE | FOC | TK-MP4000 | 2024-12-17 10:15 | mum.depot@crystalgroup.in | YES | DEC009 | YES |  |  | 2024-12-17 10:20 | mum.depot@crystalgroup.in | YES | DEC009 | TECHNICIAN |  |  | SHUBHAM |  |  | 2024-12-09 20:30 | 2024-12-08 |  |  |  |  | TITU9928040 |  |  |  | Thermo king | +4'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.0B & 12 B | 7.7/.7.5/7.7 | 404/403/404 | Not done | TEMPETARUTE NOT PULL DOWN | COMPRESSOR CONTACTOR OR LESS GAS R404A 0R LICKAGE | Yes | https://drive.google.com/file/d/1EqBZQ07WovBH1wzZwsvLhbOjMBTpeCcz/view?usp=drive_link |  |  | NA | Yes | Yes | Urgent | NA | NA
DEC017 | 2024-12-10 13:31 | rahul.gawade@crystalgroup.in | Softbox-Hyderabad | Satish Kondapalli |  | Site Manager | GRMU3707470 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Rahul | Skondapalli@csafeglobal.com |  | Running with issues |  |  |  | 2024-12-11 10:32 | service@crystalgroup.in | soft box | GRMU3707470 | 20 FT | DAIKIN OLD | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NEED TO REPLACED EXPANCTION VALVE & COIL | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC017 | Daikin |  |  |  |  | used |  | RAMIZ | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2024-12-12 17:04 | mum.depot@crystalgroup.in | YES | DEC010 | 2024-12-12 | Spares | SOFTBOX | HYDRABAD | GRMU3707470 | SITE | FOC | DAIKIN | 2024-12-12 17:08 | mum.depot@crystalgroup.in | YES | DEC010 | YES | https://drive.google.com/open?id=16eay2ACnzpu6KBJHVi7_F8Fl_SoPiu61 |  | 2024-12-18 10:57 | mum.depot@crystalgroup.in | YES | DEC010 | TECHNICIAN |  |  | RAMIZ |  |  | 2024-12-17 20:18 | 2024-12-17 |  |  |  |  | GRMU3707470 |  |  |  | Daikin | -25C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 2025-06-06 | 9.8/9.9/9.8 | 410/411/410 | Not done | found to expansion valve & coil defective & display sticker blurred | nee to fix new expansion valve & coil | Yes | https://drive.google.com/open?id=1zjSzTHTmKaZCjW6STgEu1JOKiAw8x3ec https://drive.google.com/open?id=1qYSOqJc61tEeNe9hLMPY1PMrP9PbmYIz |  |  | NA | Yes | Yes | Urgent | NA | NA | service@crystalgroup.in
DEC018 | 2024-12-10 16:53 | rahul.gawade@crystalgroup.in | RELIANCE | Bhushan | 9960964367 | Sr. Technician | TRIU6618663 | Possible defect in coil heater, dts sensor and Disply | Rahul | TO: Anbu.Ezhilan@ril.com CC: uday.kamati@ril.com | Jamnagar Gujarat | Running with issues |  |  |  | 2024-12-11 10:35 | service@crystalgroup.in | RELIANCE | TRIU6618663 | 20 FT | CARRIER | SERVICE-ON CALL | LEASE | AMC | UNIT TRIPPED DURING DEFROST PROCRESS | Possible defect in coil heater, dts sensor and Disply NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC018 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN | Yes | Possible defect in coil heater, dts sensor and Disply | 2024-12-10 17:41 | operation@crystalgroup.in | YES | DEC010 | 2024-12-10 | FOC | RELIANCE | JAMNAGAR-GUJARAT | TRIU6618663 | SITE | FOC | CARRIER-THINLINE | 2024-12-13 16:04 | mum.depot@crystalgroup.in | YES | NOV057 | YES | https://drive.google.com/open?id=10QFixFaPGA-jQoL-3LNHYmFERqNxUpRJ |  | 2025-02-01 10:40 | mum.depot@crystalgroup.in | YES | DEC010 | COURIER | 10683213887925 | DELHIVERY |  | https://drive.google.com/open?id=1qg90Wkc_xc4cu4Y7A2PefRDXvdMdPEoB |  | 2025-02-19 10:52 | 2025-02-15 |  |  |  |  | TRIU6618663 |  |  |  | Carrier | 0*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /12.6 | 14.5/14.5/14.2 | 421/420/420 | Not done | NA | NA | Yes | https://drive.google.com/open?id=105Bp28nEyrPnCOsxVuyB6t4i3Mjr1od2, https://drive.google.com/open?id=1iwGAQ6yJYTzOC7gKoN-kaXvf72zplu8g |  |  | TRIP073 | Yes | Yes | Urgent | installation Supply Sensor & Heater Coil | Supply Sensor Heater Coil | crm@crystalgroup.in | REEFER
DEC019 | 2024-12-10 16:55 | rahul.gawade@crystalgroup.in | RELIANCE | Bhushan | 9960964367 | Sr. Technician | CCLU1031918 | Defect in heater coil. | Rahul | TO: Anbu.Ezhilan@ril.com CC: uday.kamati@ril.com | Jamnagar Gujarat | Running with issues |  |  |  | 2024-12-11 10:38 | service@crystalgroup.in | RELIANCE | CCLU1031918 | 20 FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPPED DURING DEFROST OPRATION | Defect in heater coil. NEED TO REPLACED | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC019 | Carrier - Thinline | Thinline |  |  |  | brand New |  | SHAHBUDDIN | Yes | Defect in heater coil. | 2024-12-14 10:39 | mum.depot@crystalgroup.in | YES | NOV058 | 2024-11-11 | Spares | RELIANCE | JAMNAGAR | CCLU1031918 | SITE | FOC | CARRIER-THINLINE | 2024-12-17 10:27 | mum.depot@crystalgroup.in | YES | NOV058 | YES |  |  | 2025-02-01 10:49 | mum.depot@crystalgroup.in | YES | NOV058 | COURIER | 10683213887903 | DELHIVERY |  | https://drive.google.com/open?id=1OGHpy1P4enL7f2wd-dfxvIpoOUuWfWUB |  | 2025-02-19 11:25 | 2025-02-15 |  |  |  |  | CCLU1031918 |  |  |  | Carrier | +7*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /12.9 | 15.9/15.9/15.7 | 404/403/404 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1WiRHeCsnUNxMi_RvDgfTFIGfTqxqa1TH, https://drive.google.com/open?id=1llJzQnTjnJUnEYqAYpzerqSsbz74mSmS |  |  | TRIP073 | Yes | Yes | Urgent | NA | Keypad Condensor motor bearing | crm@crystalgroup.in | REEFER
DEC021 | 2024-12-12 12:39 | mum.depot@crystalgroup.in | Crystal | CRYSTAL YARD | NA | NA | GESU9440432 | COMPRESSOR MAKING NOISE | RAMIZ | NA |  | Running with issues |  |  |  | 2024-12-12 12:43 | service@crystalgroup.in | crystal yard | GESU9440432 | 40 FT | CARRIER THINE LINE | REPAIR | NA | NA | COMPRESSOR & CONTROLLER & DISPLY & ISOPLUG | COMPRESSOR & CONTROLLER & DISPLY & ISOPLUG NEED TO FIX FOR REPAIR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC021 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | RAMIZ | No | COMPRESSOR MAKING NOISE | 2024-12-12 13:16 | mum.depot@crystalgroup.in | YES | DEC009 | 2024-12-12 | Spares | CRYSTAL | YARD | GESU9440432 | DEPOT | FOC | CARRIER-ELITLINE | 2025-02-01 13:08 | operation@crystalgroup.in | YES | JAN047 | YES |  |  | 2025-02-01 19:03 | operation@crystalgroup.in | YES | JAN047 | YARD | [5 empty] | 2025-02-06 16:39 | 2025-01-05 |  |  |  |  | GESU9440432 |  |  |  | Carrier | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 05 / 13.8 BAR | 8.9/8.5/8.7 AMPS | 410/411/410 | Full | compressor, controller , display , compressor oill , gas 5 134a kgs , n2 test vacuum done | after working the reefer container has been running good & full pti pass | No | https://drive.google.com/open?id=1Qev3q3m8PwR7NdY1pk4yoKnCWR4GEGUA, https://drive.google.com/open?id=1jLHAG62H36oAKu0C5ikDEEH_6McPd385 |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
DEC022 | 2024-12-12 13:19 | mum.depot@crystalgroup.in | Crystal | CRYSTAL YARD | NA | NA | BMOU9782197 | COMPRESSOR REQUIRED | RAMIZ | NA |  | Running with issues |  |  |  | 2024-12-12 18:32 | service@crystalgroup.in | CRYSTAL YARD | CRYSTAL YARD | 40 FT | DAIKIN | REPAIR | STOCK | FOC | COMPRESSEO NO WORKING | COMPRESSOR DEFECTICE & EXPANCATION VALVE & STAINER & FILTER DRIER | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC022 | [7 empty] | UMESH | Yes | COMPRESSOR REQUIRED | 2024-12-14 14:46 | mum.depot@crystalgroup.in | YES | DEC017 | 2024-12-14 | Consumables, Spares | CRYSTAL | JNPT | BMOU9782197 | DEPOT | FOC | DAIKIN | 2024-12-18 15:03 | mum.depot@crystalgroup.in | YES | DECO17 | YES |  |  | 2024-12-24 15:24 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-27 18:43 | 2024-12-12 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | [23 empty] | Okay | Okay | Done | Clean | [5 empty] | na | container running good and ful pti passed but need to replace the sheet key | Yes | https://drive.google.com/open?id=1KWvmoP-ZXnH2Uh07L87MWwFM63YnF-c4 |  |  | 1 | No | No | Urgent | need to replace sheet key | Daikin Sheet key | mum.depot@crystalgroup.in
DEC023 | 2024-12-12 16:25 | rahul.gawade@crystalgroup.in | Devis Lab-Hyderabad | Surarchit | +91 96527 25368 | On Duty Officer | DCUNIT09 | Internal T Floor Ice Formation | Rahul | M.Ramakrishna@divislabs.com |  | Running with issues |  |  |  | 2024-12-12 16:53 | service@crystalgroup.in | Devis Lab-Hyderabad | DCUNIT09 | 40 FT | Carrier Thine | SERVICE-ON CALL | SALE | FOC | Internal T Floor Ice Formation | Internal T Floor Ice Formation & temperature issue | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC023 | [7 empty] | RAMIZ | Yes | Internal T Floor Ice Formation | 2024-12-16 16:22 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-16 16:23 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-27 15:45 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-17 00:22 | 2024-12-16 |  |  |  |  | SEZDC09 |  |  |  | Carrier | -23C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9/12.3 | 12.5/12.4/12.5 | 404/405/404 | Not done | Found evaporator drain has been clogged & condenser coil dirty & both door gasket hanging | removed ice from internal t floor & evp drain area by hot water & clean condenser coil with fresh water | No | https://drive.google.com/open?id=1BswDbEg1J4n9n7cCcMiihj08cF7V7SFs https://drive.google.com/open?id=17ql-Id57KLdxbi7VxWdMWcSVoC_WrUm0 |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in
DEC024 | 2024-12-13 18:47 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Executive | PRGU4958724 | Error AL 06 | Pushpalata Shetty | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues |  |  |  | 2024-12-14 14:24 | service@crystalgroup.in | Lauruslabs unit-2 | PRGU4958724 | 40 FT | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | AL 06 KEY PAD NOT WORKING | NEED TO CHANGE SET POINT | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC024 | Carrier - Thinline |  |  |  |  | Used |  | VIRENDRA | No | Error AL 06 | 2024-12-16 16:17 | mum.depot@crystalgroup.in | YES | DEC018 | 2024-12-16 | Spares | LAURUS SYNTHESIS UNIT 2 | VIZAG | PRGU4958724 | SITE | FOC | CARRIER-THINLINE | 2024-12-16 16:19 | mum.depot@crystalgroup.in | YES | DEC018 | YES |  |  | 2024-12-31 16:53 | mum.depot@crystalgroup.in | YES | NA | COURIER | 16453390531 | Patel courier | courier | https://drive.google.com/open?id=1mKzqXhPUdUT0xTcxGAirzSyuQMC9CFiP |  | 2025-02-05 17:49 | 2024-12-13 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | + | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2/12,3BAR | 12.1/12.0/12.1 | 404/405/404 | Not done | FOUND AL 06 | over phone the customer conform the key pad has been replaced & the unit working good | No | https://drive.google.com/open?id=1CeaFPehzKOPAxi2qHS4A5VCc3YxtkMfn, https://drive.google.com/open?id=1KPxFtEVC1crQ_RxfYlCR2j8WBCXx-C4o |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
DEC025 | 2024-12-14 17:05 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd, | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering, | CXRU1030387 | PREVENTIVE MAINTENANCE | Pushpalata Shetty | brahmaiah.g@hetero.com | Hyderabad | Preventive Maintenance |  |  |  | 2024-12-14 17:13 | service@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd, | CXRU1030387 | 40 FT | DAIKIN | SERVICE-ON CALL | LEASE | FOC | REVENTIVE MAINTENANCE Required | NA | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC025 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | RAMIZ |  | PREVENTIVE MAINTENANCE | 2024-12-16 15:59 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-16 16:07 | dhruvit.dedhia@crystalgroup.in | NO |  |  |  |  | 2024-12-27 15:41 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-20 07:20 | 2024-12-19 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -23;C & -20'C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/12.5 & 0.3/11.9 BAR | 9.1/9.2/9.1 & 8.9/9.0/8.9 | 410/411/410 | Not done | CONDENSER COIL DIRTY , CONDENSER AIR FLOW BLOCK FOR UNIT 2,ICE FOUNDATION ON T bar floor , UNIT 2 internal air circulation fully block by cargo . anti room door bottom ice foundation due to T bar fome packing removed . door heater connection open , full lode cargo . keep non freeze cargo (hot stuffing ) . both door open in running condition ( anti room & main door ) due to this moisture in al most daily 10 time every time 10 to 15 minutes. set point for both -25'C | For both unit clean condenser coil with fresh water & checked all parameter & set change unit one -23'C & unit 2 -20'C. future repaired work need to vacant the container . | No | https://drive.google.com/open?id=18BCAoYEntqjYSQ-zUcXrbtpPqhuRRzgc https://drive.google.com/open?id=11NdtUm0bwtr30KmC7TnUVfMi9cVgVbJd |  |  | NA | Yes | Yes | Urgent | na | na | service@crystalgroup.in
DEC026 | 2024-12-16 09:53 | crm@crystalgroup.in | Crystal | NA | NA | NA | CGMU2990461 | Problem in the evaporator motor | Sahil | NA | JNPT | Running with issues |  |  |  | 2024-12-18 18:26 | mum.depot@crystalgroup.in | CRYSTAL | CGMU2990461 | 20 FT | CARRIER | REPAIR | STOCK | FOC | CONDENSER LEAKED/ STS SENSOR FOUND FAULTY AND EVP MOTOR NOISY | UNDER REPAIR | EVP MOTOR BEARING, ISO PLUG, STS SENSOR, BRAZING ROD, R134a GAS, FILTER DRIER, N2, BRAZING SET, VACCUM PUMP |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC026 | Carrier - Thinline | Thinline | 4612UD6633 | LSM60197686 |  |  |  | RAMIZ | Yes | Problem in the evaporator motor | 2024-12-31 13:04 | mum.depot@crystalgroup.in | YES | DEC016 | 2024-12-14 | Consumables, Spares | CRYSTAL | JNPT | CGMU2990461 | DEPOT | FOC | CARRIER-THINLINE | 2025-02-01 13:12 | operation@crystalgroup.in | YES | JAN050 | YES |  |  | 2025-02-01 19:04 | operation@crystalgroup.in | YES | JAN050 | YARD | [5 empty] | 2024-12-19 11:44 | 2024-12-09 |  |  |  |  | CGMU2990461 |  |  |  | Carrier | - 18 c | Clean | Leakage |  | Okay | Clean | Noisy | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | 0 | 12.4/12.5/12.4 | 410/410/410 | Not done | Found condenser coil leak / Evaprator motor noisy/ supply sensor failure/ iso plug pin cut/ Gas & brazing rod with filter Drier etc ..... | As above | Yes | https://drive.google.com/open?id=111JBOAr5YCcZN6pWvJuwTLYu_ewupwCU |  |  | NA | Yes | Yes | Urgent | As above | As above | technician@crystalgroup.in
DEC027 | 2024-12-17 16:50 | crm@crystalgroup.in | DR Redddy Unit 6 | Smruti Ranjan Behera | 91602 77658 | Junior Manager | CXRU1033616 | Water stagnant inside container | Shahbuddin | smrutiranjanb@drreddys.com | Pydibhimavaram | Running with issues |  |  |  | 2024-12-19 13:05 | mum.depot@crystalgroup.in | Dr Reddy- CTO 6 | CXRU1033616 | 40 | Daikin | SERVICE-ON CALL | LEASE | FOC | water leaking | advice to client for house keeping/ need to clean with normal hot water inside and evaporator section | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC027 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | UMESH | Yes | Water stagnant inside container | 2024-12-20 10:12 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-20 10:13 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-20 10:14 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-19 12:44 | 2024-12-17 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | + 3.5 C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | NA | Not done | Water leaking issue. | Need to clean with hot water bottom & Evaprator section | No | https://drive.google.com/open?id=1VqLWgRvC4O761rDNQ30JmPm00CAffp2G, https://drive.google.com/open?id=1fzLAzXGpThlskVvL3COY-H6eEp6oZhJp |  |  | NA | Yes | Yes | Urgent | Not yet ckean | NA | technician@crystalgroup.in
DEC028 | 2024-12-17 16:54 | crm@crystalgroup.in | DR Redddy Unit 6 | Smruti Ranjan Behera | 91602 77658 | Junior Manager | KKFU6712802 | Water stagnant inside container | Shahbuddin | smrutiranjanb@drreddys.com | Pydibhimavaram | Running with issues |  |  |  | 2024-12-19 13:08 | mum.depot@crystalgroup.in | Dr Reddy- CTO6 | KKFU6712802 | 40 | CARRIER | SERVICE-ON CALL | LEASE | FOC | Water leaking issue | Advice for house keeping, need to clean inside and evaporator section with normal hot water | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC028 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | UMESH | No | Water stagnant inside container | 2024-12-20 10:12 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-20 10:13 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-20 10:15 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-19 12:52 | 2024-12-18 |  |  |  |  | KKFU6712802 |  |  |  | Carrier | + 5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | NA | Not done | Water leaking issue, need to clean Evaprator section and bottom space inside & Drain hole with hot normal water. | As above | No | https://drive.google.com/open?id=1y9qiYdeKBZzfqp9XBIhAQ4vDLKZy82jC , https://drive.google.com/open?id=1xIcS0K8WTNZYnBt5vNZNiOSsPi7-c-8E |  |  | NA | Yes | Yes | Urgent | Not yet clean by client's House keeping section | NA | technician@crystalgroup.in
DEC029 | 2024-12-18 16:52 | crm@crystalgroup.in | Crystal | NA | NA | NA | Site Cabin 79 | Modified Cargo Shipping Container | Sushma | NA | JNPT | Running with issues |  |  |  | 2024-12-18 17:29 | pravin.shinde@crystalgroup.in | Crystal Yard | Site Cabin 79 | Modified Cargo Shipping Container 20'X8'X12' | Porta Cabin | NA | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC029 | [7 empty] | RAMIZ | No | Modified Cargo Shipping Container | 2024-12-18 17:51 | mum.depot@crystalgroup.in | YES | DEC023 | 2024-12-18 | FOC | CRYSTAL | JNPT | PORTA CABIN | SITE | FOC | NA | 2024-12-18 18:00 | dhruvit.dedhia@crystalgroup.in | NO |  |  |  |  | 2024-12-27 15:40 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-05 17:54 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC030 | 2024-12-19 00:15 | service@crystalgroup.in | SoftBox | Satish Kondapalli | 918977711235 | "Site Manager" | GRMU3707470 | FLUCTUATIONS IN TEMEPRATURE | RAMIZ | NA | Hyderabad | Running with issues |  |  |  | 2024-12-19 00:18 | service@crystalgroup.in | SOFTBOX | GRMU3707470 | 20 FT | DAIKIN (DECOSE D III) | SERVICE-AT SITE | LEASE | FOC | TEMPERATURENOT PULL DOWN | EXP VALVE & COIL NEED TO REPLACE | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC030 | Daikin |  |  |  |  | used |  | RAMIZ |  | FLUCTUATIONS IN TEMEPRATURE | 2024-12-19 00:33 | service@crystalgroup.in | NO | [9 empty] | 2024-12-19 10:33 | dhruvit.dedhia@crystalgroup.in | NO |  |  |  |  | 2024-12-19 00:33 | service@crystalgroup.in | NO | [7 empty] | 2024-12-19 00:28 | 2024-12-18 |  |  |  |  | GRMU3707470 |  |  |  | Daikin | -20'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3 B/12.3 B | 8.9/8.9/8.9 | 411/410/411 | Not done | Lplate damaged & right side fome loose & temperature isssue | replaced expansion vale & coil & evp inlet & out let sensor , filter drier & N2 test & vacuum done gas charge R134a 5 kgs . L plate repaired . | No | https://drive.google.com/open?id=1NQZXR-it7a_1_cUoA04snKVyiFzF4hvC https://drive.google.com/open?id=1zlMIYgOtlnNihF4NDpfnIWG95LJx5zZW |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC031 | 2024-12-19 00:44 | service@crystalgroup.in | DIVIS LAB | Surarchit | +91 96527 25368 | On Duty Officer | SEZDC04 | MOTOR MAKING NOISE, ALARM CODE VISIBLE, AL 56 SUPPLY TEMPERATURE SENSOR | RAMIZ | NA | Hyderabad | Running with issues |  |  |  | 2024-12-19 00:47 | service@crystalgroup.in | DIVIS LAB | SEZDC04 | 40 FT | CARRER THINE LINE | SERVICE-AT SITE | SALE | CHARGEABLE | Both evaporator motor heavy noise & al 56 supply temperature sensor defective & condenser coil dirty | cleaned condenser coil with fresh water | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC031 | [7 empty] | RAMIZ |  | MOTOR MAKING NOISE, ALARM CODE VISIBLE, AL 56 SUPPLY TEMPERATURE SENSOR | 2024-12-19 00:48 | service@crystalgroup.in | NO | [9 empty] | 2024-12-19 00:50 | service@crystalgroup.in | NO |  |  |  |  | 2024-12-19 00:50 | service@crystalgroup.in | NO | [7 empty] | 2024-12-19 01:04 | 2024-12-16 |  |  |  |  | SEZDE04 |  |  |  | Carrier | +3'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.1b/10.9b | 12/12.1/12 amps | 404/404/403 | Not done | both evp motor need to replaced with new one & supply sensor | evp motor av with divis lab ( single phase ) | No | https://drive.google.com/open?id=1W0yFR0sLnBN3M2zTX18Ad3v66o9soboK, https://drive.google.com/open?id=17asY1iXNcVDB4ZrO4fHygQRvbQ-EXJOp |  |  | NA | Yes | Yes | Urgent | na | na | service@crystalgroup.in
DEC032 | 2024-12-19 01:07 | service@crystalgroup.in | DIVIS LAB | Surarchit | +91 96527 25368 | On Duty Officer | SEZDC06 | ICE FORMATION, IN T BAR FLOOR & DOOR SIDE | RAMIZ | NA | Hyderabad | Running with issues |  |  |  | 2024-12-19 01:10 | service@crystalgroup.in | DIVIS LAB | SEZDC06 | 40 FT | CSRRIER THINE LINE | SERVICE-AT SITE | SALE | CHARGEABLE | EVP DRAIN CLOGGED & DOOR GASKET HANGING (int) | Clean Evaporator drain & cut removed damaged gasket | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC032 | [7 empty] | RAMIZ |  | ICE FORMATION, IN T BAR FLOOR & DOOR SIDE | 2024-12-19 01:11 | service@crystalgroup.in | NO | [9 empty] | 2024-12-19 01:11 | service@crystalgroup.in | NO |  |  |  |  | 2024-12-19 01:12 | service@crystalgroup.in | NO | [7 empty] | 2024-12-19 01:18 | 2024-12-16 |  |  |  |  | SEZDC06 |  |  |  | Carrier | -21'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B/12.7B | 12.5/12.6/12.5 AMPS | 404/404/403 | Not done | CONDENSER COIL DIRTY & ICE FOUNDATIN NEER TO THR DOOR & EVP DRAIN CLOGGED | clean condenser coil with fresh water & FIX door gasket . under observation | No | https://drive.google.com/open?id=1IhOKEL4alCulqupLZbBNKdVzcf_sfIgX, https://drive.google.com/open?id=1DnaNIBHsT2xDd8YAHN2xbvYUgOzbL5qv |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in
DEC033 | 2024-12-19 10:57 | crm@crystalgroup.in | Crystal | NA | NA | NA | TRLU8727441 - Site Cabin 77 | Modified Cargo Shipping Container | Sushma | NA | JNPT | Running with issues |  |  |  | 2024-12-19 13:11 | rahul.gawade@crystalgroup.in | Crystal Yard | TRLU8727441 - Site Cabin 77 | 20ft | NA | NA | NA | NA | NA | NA | Crystal Logo 10'X3' |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC033 | [7 empty] | NA |  | Modified Cargo Shipping Container | 2024-12-20 09:22 | rahul.gawade@crystalgroup.in | YES | DEC027 | 2024-12-20 | Consumables | CRYSTAL YARD | JNPT | TRLU8727441 - Site Cabin 77 | DEPOT | FOC | NA | 2024-12-20 11:04 | dhruvit.dedhia@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:22 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-05 17:54 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC034 | 2024-12-20 16:27 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | CXRU1030854 | CONTAINER REPAIR WORK | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-20 16:35 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1030854 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC034 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | NA |  | CONTAINER REPAIR WORK | 2024-12-20 17:10 | rahul.gawade@crystalgroup.in | YES | DEC024 | 2024-12-20 | Consumables, FOC | CRYSTAL YARD | JNPT | CXRU1030854 | DEPOT | FOC | NA | 2024-12-24 15:21 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:22 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 16:55 | 2024-12-02 |  |  |  |  | CXRU1030854 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  | 10/9.9/9.7 | 415/413/411 | Full | NA | replaced Dry filter,N2 Test ,Vaccume and R134 refill 5KG,replaced Sheet key and Power Plug | No | https://drive.google.com/open?id=1-OANCodoTra9av7US5cL0XO7kGctLFPw, https://drive.google.com/open?id=1mmak_74lIxf5HWgCOuRLdafcyok-Qp_z |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC037 | 2024-12-21 11:51 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | CXRU1030854 | CONTAINER REPAIR WORK | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 11:55 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1030854 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC037 | Daikin | LXE10E147F2 | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used |  | NA |  | CONTAINER REPAIR WORK | 2024-12-21 12:50 | rahul.gawade@crystalgroup.in | YES | DEC026 | 2024-12-21 | Consumables | CRYSTAL YARD | JNPT | CXRU1030854 | DEPOT | FOC | NA | 2024-12-24 15:04 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:07 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 12:11 | 2024-12-02 |  |  |  |  | CXRU1030854 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  | .10/9.7/9.9 | 415/413/411 | Full | NA | Filter Drier replaced , N2 test Vaccume R134A 5Kg | No | https://drive.google.com/open?id=1uLfym6aAHP2fjRIIOzthKa-7mq6-MmKc, https://drive.google.com/open?id=1f1UJL2EPXlNkuExrqV1MZ-WK6n4ny04v |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC038 | 2024-12-21 11:58 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | ARCU4530736 | CONTAINER REPAIR WORK | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 12:07 | rahul.gawade@crystalgroup.in | Crystal Yard | ARCU4530736 | 40RF | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC038 | Carrier - Thinline | Thinline |  | JSL90656195 |  | used |  | NA |  | CONTAINER REPAIR WORK | 2024-12-21 13:01 | rahul.gawade@crystalgroup.in | YES | DEC027 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | ARCU4530736 | DEPOT | FOC | NA | 2024-12-24 15:05 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:08 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 12:36 | 2024-11-21 |  |  |  |  | ARCU4530736 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  | 9.9/9.5/9/7 | 415/413/411 | Full | NA | we have replaced complete reefer Unit and Filter Driyer | No | https://drive.google.com/open?id=127zdVrrt_fMl9YJa2vAz2OUun2aCIEmD, https://drive.google.com/open?id=1rNJjxbsnM_a0xipGKZ1StjZODRalu6K8 |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC039 | 2024-12-21 12:02 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | CXRU1036533 | CONTAINER REPAIR WORK | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 12:09 | rahul.gawade@crystalgroup.in | Crystal Yard | CXRU1036533 | 40RF | NA | REPAIR | STOCK | NA | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC039 | [7 empty] | NA |  | CONTAINER REPAIR WORK | 2024-12-21 13:05 | rahul.gawade@crystalgroup.in | YES | DEC028 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | CXRU1036533 | DEPOT | FOC | NA | 2024-12-24 15:05 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:08 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 13:03 | 2024-12-05 |  |  |  |  | CXRU1036533 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  | 8.7/9.0/9.1 | 410/407/409 | Full | NA | Touchup and cleaning | No | https://drive.google.com/open?id=1rZ8HSuIzcZrdJdukQ1Jqchwb6GZHG2i3, https://drive.google.com/open?id=1oou7VB6nouaAlz2ktBm9lJdEK_cFrM3z |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC040 | 2024-12-21 12:58 | crm@crystalgroup.in | Cipla | Anant Ravut | 7774089236 | Sr. Engineer | CRIU4024012 | Installation 2 Bay Super Store | Pushpalata Shetty | anant.ravut@cipla.com | Goa | Installation |  |  |  | 2024-12-30 16:14 | rahul.gawade@crystalgroup.in | Cipla | CRIU4024012, CRIU4024028 | 40FT Refer (Super Store 2 Bay) | Thermoking MP4000 | INSTALLATION | SALE | NA | Installation | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC040 | [7 empty] | SHAHBUDDIN, Harish , Akshay |  | Installation 2 Bay Super Store | 2024-12-31 14:50 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-31 15:01 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-31 15:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-31 17:12 | 2024-12-28 |  |  |  |  | CRIU4024012 |  |  |  | Thermo king | + 5 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/19 | 9.8/9.8/9.7 | 410/411/410 | Short | Two way Instalation | Two way Instalation complited | No | https://drive.google.com/open?id=1DsZ7UmEgsHHT46j_ReJ_ruRDgdQUlZ8t, https://drive.google.com/open?id=1iH9vh0oCWInNfg7k4aUoc6n-k7lJauwO |  |  | 61 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in
DEC041 | 2024-12-21 15:36 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | WHLU4283466 | Dry Container Repair | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 15:38 | rahul.gawade@crystalgroup.in | Crystal Yard | WHLU4283466 | 40ft Dry | NA | REPAIR | STOCK | FOC | NA | Na | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC041 | [7 empty] | NA |  | Dry Container Repair | 2024-12-21 16:03 | rahul.gawade@crystalgroup.in | YES | DEC029 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | WHLU4283466 | DEPOT | FOC | DRY | 2024-12-24 15:10 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:18 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 15:53 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC042 | 2024-12-21 16:20 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | JWWU5090354 | Repair | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 16:26 | rahul.gawade@crystalgroup.in | Crystal Yard | JWWU5090354 | 20ft Dry | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC042 | [7 empty] | NA |  | Repair | 2024-12-21 16:33 | rahul.gawade@crystalgroup.in | YES | DEC030 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | JWWU5090354 | DEPOT | FOC | DRY | 2024-12-24 15:10 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:19 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 15:56 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC043 | 2024-12-21 16:23 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | JWWU5090518 | Repair | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 16:37 | rahul.gawade@crystalgroup.in | Crystal Yard | JWWU5090518 | 20ft Dry | NA | REPAIR | STOCK | FOC | NA | Na | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC043 | [7 empty] | NA |  | Repair | 2024-12-21 16:53 | rahul.gawade@crystalgroup.in | YES | DEC031 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | JWWU5090518 | DEPOT | FOC | DRY | 2024-12-24 15:11 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:19 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 15:56 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC044 | 2024-12-21 17:11 | rahul.gawade@crystalgroup.in | Crystal | NA | NA | NA | MSCU5735843 | Repair Dry Container | NA | NA | JNPT | Running with issues |  |  |  | 2024-12-21 17:15 | rahul.gawade@crystalgroup.in | Crystal Yard | MSCU5735843 | 40ft Dry | NA | REPAIR | STOCK | FOC | NA | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC044 | [7 empty] | NA |  | Repair Dry Container | 2024-12-21 17:21 | rahul.gawade@crystalgroup.in | YES | DEC032 | 2024-12-21 | Consumables, FOC | CRYSTAL YARD | JNPT | MSCU5735843 | DEPOT | FOC | DRY | 2024-12-24 15:11 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-24 15:19 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 15:58 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC046 | 2024-12-21 20:55 | service@crystalgroup.in | DR REDDY CTO 06 | Tadikonda Kishore | 96767 55199 | NA | TRIU6632949 | PREVENTIVE MAINTENANCE | RAMIZ | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2024-12-21 21:13 | service@crystalgroup.in | Dr Reddy CTO 06 | TRIU6632949 | 20 FT | CARRIER THINE LINE | SERVICE-AT SITE | LEASE | FOC | found condenser coil normal dirty & evaporator Drin pipe clogged , less gas | cleaned condenser coil with fresh water & cleaned evp drin pipe with water presser | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC046 | Carrier - Thinline | Thinline | 1808L295 | MS60317785 |  | Used |  | RAMIZ | Yes | PREVENTIVE MAINTENANCE | 2024-12-23 12:54 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-23 12:56 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-23 12:57 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-21 21:18 | 2024-12-21 |  |  |  |  | TRIU6632949 |  |  |  | Carrier | +3'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1/10.5 bar | 11.8/11.9/11.8 amps | 404/404/403 | Not done | found condenser coil normal dirty & evaporator Drin pipe clogged , less gas | cleaned condenser coil with fresh water & cleaned evp drin pipe with water presser | No | https://drive.google.com/open?id=1uFDQ4t_FVTg4IiZiInxGZsBaF51kBTIF, https://drive.google.com/open?id=1nQqYB1sgiWOU1jXkuLDXcLHhmAqpUTjP |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in
DEC047 | 2024-12-21 22:22 | service@crystalgroup.in | DR REDDY CTO 06 | Tadikonda Kishore | 96767 55199 | na | CXRU1033616 | WATER STATEMENT IN SIDE | RAMIZ | na | Vishakapatnam | Running with issues |  |  |  | 2024-12-21 22:35 | service@crystalgroup.in | Dr Reddy CTO 06 | CXRU1033616 | 40 FT | DAIKIN | SERVICE-AT SITE | LEASE | AMC | WATER STATEMENT IN SIDE THE DUE TO DRAIN CLOGGED & CONDENSER COIL NORMAL DIETY | Cleaned condenser coil with fresh water & cleaned evp drain pipe with water presser | NO |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC047 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | RAMIZ | Yes | WATER STATEMENT IN SIDE | 2024-12-23 12:55 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-23 12:56 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-23 12:57 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-21 22:41 | 2024-12-21 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | +4'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3/10.5 BAR | 11,9/11,8/11.9 AMPS | 404/404/405 | Not done | found condenser coil normal dirty & evaporator Drin pipe clogged , less gas | cleaned condenser coil with fresh water & cleaned evp drain pipe with water presser& UNDER OBSERVATION | No | https://drive.google.com/open?id=1KNrxCCcMNHUKku0wCyq1qngWB27lC583 https://drive.google.com/open?id=19T5AEuH7oqgaz6jjxO9b_48De9Xz_jwA |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC048 | 2024-12-26 18:35 | crm@crystalgroup.in | Dr. Reddy's Labs -Biologics | Suresh Kasam | 99081 25456 | Plant Engineer | TITU9930074 | Display Issue | Ninad | sureshkasam@drredddys.com | Hyderabad | Running with issues |  |  |  | 2024-12-30 17:34 | rahul.gawade@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40FT Reefer - Dual Machine | Thermoking MP4000 | PREVENTIVE MAINTENANCE | SALE | FOC | Issue in Display, having damaged pixel. | Need to Replace | VGA display |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC048 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | VIRENDRA | Yes | Display Issue | 2024-12-31 17:50 | operation@crystalgroup.in | YES | DEC050 | 2024-12-31 | Consumables, FOC | Dr. Reddy's Labs -Biologics | HYDERABAD | TITU9930074 | SITE | FOC | TK-MP4000 | 2025-01-24 17:30 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-24 17:30 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-24 17:53 | 2025-01-21 |  |  |  |  | TITU9930074 |  |  |  | Daikin | -18*C | Clean | [22 empty] | Okay | [7 empty] | Attended unit over a phone call | Man trap required | Yes | https://drive.google.com/open?id=1yb8CqD2bu-ASMi_2ag9f6ADOodTLCpk9 |  |  | NA | Yes | Yes | Urgent | Mantrap installation | Mantrap 1 Cases 3 Wire 18 mt. Revit 20 Gangbox 1 on/off switch 1 Silicon 1 | crm@crystalgroup.in | REEFER
DEC049 | 2024-12-27 12:13 | crm@crystalgroup.in | Lupin Limited | Amit Sakpal | 9326179943 | System Operator | CCLU1036859 | Water Leakage | Sahil | depotcwhmumbai@lupin.com | Bhiwandi | Running with issues |  |  |  | 2024-12-27 15:52 | mum.depot@crystalgroup.in | LUPIN | CCLU1036859 | 20FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | NEED TO VISIT | SUPPLY SENSOR & DISPLAY |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC049 | Carrier |  |  |  |  | Used | JSGA623040314 | UMESH |  | Water Leakage | 2024-12-27 17:33 | mum.depot@crystalgroup.in | YES | DEC038 | 2024-12-27 | FOC | LUPIN LTD | BHIWANDI | CCLU1036859 | SITE | FOC | CARRIER-THINLINE | 2024-12-27 18:56 | crm@crystalgroup.in | YES | DEC038 | YES |  |  | 2024-12-27 18:57 | crm@crystalgroup.in | YES | DEC038 | TECHNICIAN |  |  | UMESH |  |  | 2024-12-30 12:14 | 2024-12-28 |  |  |  |  | CCLU1036859 |  |  |  | Carrier | +5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 126 | 2008-08-08 | 408/408/408 | Not done | Checked and found water leakage inside the container & drain hose choked cleaned it properly then issue was solved. | Container running in good condition | Yes | https://drive.google.com/open?id=1K14vKptgfR0quYqsgKwoc6b-1is9uztv |  |  | TRIP062 | No | No | Can be done on next PM | No | Carrier Supply Sensor *2, Carrier Display *1 | crm@crystalgroup.in
DEC050 | 2024-12-27 12:21 | crm@crystalgroup.in | Indian Navy | NA | NA | NA | HNKU6172760 | Porta Cabin Installation | Rahul | NA | Karwar | Installation |  |  |  | 2024-12-27 12:25 | rahul.gawade@crystalgroup.in | Indian Navy | HNKU6172760 | 40ft HQ DV | NA | REPAIR | STOCK | FOC | Site Installation | NA | Installtion Material and service |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC050 | [7 empty] | NA |  | Porta Cabin Installation | 2024-12-27 12:43 | operation@crystalgroup.in | YES | DEC036 | 2024-12-27 | Consumables, Spares, FOC | MASSK | KARWAR | HNKU6172760 | SITE | FOC | DRY | 2025-01-13 16:25 | operation@crystalgroup.in | YES | DEC036 | YES |  |  | 2025-01-14 15:25 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-05 17:55 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC051 | 2024-12-27 12:22 | crm@crystalgroup.in | Indian Navy | NA | NA | NA | LYGU4092923 | Porta Cabin Installation | Rahul | NA | Karwar | Installation |  |  |  | 2024-12-27 12:27 | rahul.gawade@crystalgroup.in | Indian Navy | LYGU4092923 | 40ft HQ DV | NA | REPAIR | STOCK | FOC | Site Installation | NA | Installtion Material and service |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC051 | [7 empty] | NA |  | Porta Cabin Installation | 2024-12-27 12:45 | operation@crystalgroup.in | YES | DEC037 | 2024-12-27 | Consumables, Spares, FOC | INDIAN NAVY | KARWAR | LYGU4092923 | SITE | FOC | DAIKIN LXE10E | 2025-01-13 16:26 | operation@crystalgroup.in | YES | DEC037 | YES |  |  | 2025-01-14 15:27 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-05 17:56 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC052 | 2024-12-27 13:00 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HARSTA | 8924660331 | Jr Executive | HDMU5537036 | PREVENTIVE MAINTENANCE | Pushpa | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2024-12-30 13:21 | mum.depot@crystalgroup.in | AJINOMOTO BIO | HDMU5537036 | 40FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | LOW GAS IN SYSTEM | NEED TO ADD GAS AND PM SERVICE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC052 | Carrier | Thineline |  |  |  | Used |  | RAMIZ | Yes | PREVENTIVE MAINTENANCE | 2024-12-31 17:42 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-15 17:41 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-16 11:07 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-31 11:57 | 2024-12-27 |  |  |  |  | HDMU5537036 |  |  |  | Carrier | +20'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3 B / 10.5 B | 11.9/11.8/11.9 | 410/411/410 | Not done | FOUND LESS GAS 1.5 KGS R134a | CHARGE R134a 2 KGS , AFTER WORKING THE REEFER UNIT RUN IN GOOG CONDITION NEED SOFT WARE UP DATE | No | https://drive.google.com/open?id=1qV1UnAmAxhvUNPo6RsyXiaOy-PuRyFYP, https://drive.google.com/open?id=1_Ce6wYwNUvIN_fo8-8HixiYByc0uS0iR |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC053 | 2024-12-27 13:05 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HARSTA | 8924660331 | Jr. Executive | KKFU6994964 | PREVENTIVE MAINTENANCE | Pushpa | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2024-12-30 13:24 | mum.depot@crystalgroup.in | AJNOMOTO BIO | KKFU6994964 | 40FT | CARRIER | SERVICE-AT SITE | LEASE | FOC | LOW GAS IN SYSTEM AND PM REQUIRED | NEED TO ADD GAS AND PM SERVICES AT SITE | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC053 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040298 | RAMIZ | Yes | PREVENTIVE MAINTENANCE | 2024-12-31 17:43 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-13 16:36 | operation@crystalgroup.in | NO |  |  |  |  | 2025-01-14 15:12 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-31 12:13 | 2024-12-27 |  |  |  |  | KKFU6994964 |  |  |  | Carrier | +20'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 03.B/12.1'B | 12/11.9/12 | 411/410/411 | Short | FOUND LESS GAS 1.5 KGS R134a | "CHARGE R134a 2 KGS , AFTER WORKING THE REEFER UNIT RUN IN GOOG CONDITION . | No | https://drive.google.com/open?id=1jV6NPqKA0ae06BkbcrElJOBamcF2HUmq, https://drive.google.com/open?id=1vCy2_vf4FXzdc8LPsmPJaeSv9QlNH5Mb |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
DEC054 | 2024-12-29 11:34 | operation@crystalgroup.in | Crystal | RAHUL | 7977769348 | Cold Chain Specialist | PORTA CABIN | FOR PORTA CABIN LOGO PURPOSE | RAHUL | rahul.gawade@crystalgroup.in | JNPT | Running with issues |  |  |  | 2024-12-29 11:35 | operation@crystalgroup.in | CRYSTAL YARD | PORTA CABIN | - | - | READINESS OF CONTAINER | NA | NA | FOR PORTA CABIN READINESS | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC054 | [7 empty] | RAMIZ | No | FOR PORTA CABIN LOGO PURPOSE | 2024-12-29 11:48 | operation@crystalgroup.in | YES | DEC039 | 2024-12-29 | Consumables, FOC | CRYSTAL YARD | JNPT | PORTA CABIN | DEPOT | FOC | DRY | 2025-02-01 13:20 | operation@crystalgroup.in | YES | DEC039 | YES |  |  | 2025-02-01 19:05 | operation@crystalgroup.in | YES | DEC039 | PORTA CABIN | [5 empty] | 2025-02-05 17:57 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC055 | 2024-12-29 12:25 | operation@crystalgroup.in | Crystal | RAHUL | NA | Crystal Logistics Cold Chian Ltd | CLHU8437426 | PANEL DENTING & PATCH WORK | RAHUL | rahul.gawade@crystalgroup.in | JNPT | Running with issues |  |  |  | 2024-12-29 12:27 | operation@crystalgroup.in | CRYSTAL YARD | CLHU8437426 | 40FT | DRY | READINESS OF CONTAINER | STOCK | FOC | DENTING AND PATCH WORK | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC055 | [7 empty] | RAMIZ | No | PANEL DENTING & PATCH WORK | 2024-12-29 12:31 | operation@crystalgroup.in | YES | DEC040 | 2024-12-29 | Consumables, FOC | CRYSTAL YARD | JNPT | CLHU8437426 | DEPOT | FOC | DRY | 2025-02-01 13:21 | operation@crystalgroup.in | YES | DEC040 | YES |  |  | 2025-02-01 19:06 | operation@crystalgroup.in | YES | DEC040 | FABRICATION WORK | [5 empty] | 2025-02-05 18:01 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC058 | 2024-12-30 11:11 | crm@crystalgroup.in | Lupin Limited | Amit Sakpal | 9326179943 | System Operator | TRIU6681082 | PREVENTIVE MAINTENANCE | Sahil | depotcwhmumbai@lupin.com | Bhiwandi | Preventive Maintenance |  |  |  | 2024-12-30 11:20 | crm@crystalgroup.in | Lupin Ltd | TRIU6681882 | 20 STD RF | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | None | Container is working well | No |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC058 | Carrier - Thinline | Thinline |  |  |  | Used | JSGA623040302 | UMESH |  | PREVENTIVE MAINTENANCE | 2024-12-30 11:21 | crm@crystalgroup.in | NO | [9 empty] | 2024-12-30 11:21 | crm@crystalgroup.in | NO |  |  |  |  | 2024-12-30 11:22 | crm@crystalgroup.in | NO | [7 empty] | 2024-12-30 11:57 | 2024-12-28 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | +5* C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 14 | 2010-10-10 | 411/411/412 | Not done | Checked and found container running in good condition. | Container running in good condition. | No | https://drive.google.com/open?id=1kGwbC-M09wSphu-bR0Xg9ol64YKdx0YY |  |  | TRIP062 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in
DEC059 | 2024-12-30 11:27 | operation@crystalgroup.in | Crystal | KSHIROD | NA | NA | HDMU5542110 | FLOOR REPAIR WORK | KSHIROD | NA | JNPT | Running with issues |  |  |  | 2024-12-30 11:53 | operation@crystalgroup.in | CRYSTAL YARD | HDMU5542110 | 40FT | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | FLOOR NEED TO REPAIR | 3RD PARTY VENDOR REPARI FLOOR | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC059 | [7 empty] | RAMIZ | No | FLOOR REPAIR WORK | 2024-12-30 12:09 | operation@crystalgroup.in | YES | DEC043 | 2024-12-30 | Consumables, FOC | CRYSTAL YARD | JNPT | HDMU5542110 | DEPOT | FOC | NA | 2025-02-01 13:25 | operation@crystalgroup.in | YES | DEC043 | YES |  |  | 2025-02-01 19:07 | operation@crystalgroup.in | YES | DEC043 | FABRICATION WORK | [5 empty] | 2025-02-06 17:31 | 2024-12-31 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | ok | ok | ok | Full | t bar floor need to repaired | repaired done | No | https://drive.google.com/open?id=13hEU5mwIrEUk5vUqLxvXRf4iQ2JE1hvs, https://drive.google.com/open?id=1IBIy3-IP3f6Nu_AHBLSYwGdUjAtC3nDU |  |  | na | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
DEC060 | 2024-12-30 11:50 | sushma.poojari@crystalgroup.in | Tan90 Thermal Solutions Private Limited | Shamboo | 89258 46277 | Site incharge | CICU3876523 | PCM pads blasting issue | Sushma | abhishek.sharma@tan90thermal.com | Pune | Running with issues |  |  |  | 2024-12-30 13:10 | mum.depot@crystalgroup.in | Tan90 Thermal Solutions Private Limited - PUNE | CICU3876523 | 10FT | TK MP-4000 | SERVICE-AT SITE | LEASE | FOC | UNIT TEMPERATURE NOT REACHED AT SET TEMPERATURE | UNDER PROCESS | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC060 | Thermoking | Magnum Plus | E0GM030291 | 0222GM030291 | ABC782800321480005 | Brand New |  | RAMIZ | No | PCM pads blasting issue | 2024-12-31 14:52 | operation@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:13 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2024-12-17 13:11 | mum.depot@crystalgroup.in | NO | [7 empty] | 2024-12-30 18:18 | 2024-12-30 |  |  |  |  | CICU3876523 |  |  |  | Thermo king | - 40 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/ 18 bar | 9.9/9.8/9,9 | 410/410/ 411 | Not done | Found container bottom side Icing and need Unit Defrost time time as manually, Already infom | Guide line has been provided on telephone | No | https://drive.google.com/open?id=1azA-BlNew30WeMFK1jbHtTNau0w0hF9v, https://drive.google.com/open?id=1JThzdOTQ-fzxRPBPyRVmWXOp01VxXjjg |  |  | NA | No | Yes | Can be done on next PM | NA | NA | technician@crystalgroup.in
DEC061 | 2024-12-30 13:30 | crm@crystalgroup.in | SOFTBOX | Satish Kondapalli |  | Site Manager | TITU8257288 | PREVENTIVE MAINTENANCE | Ramiz | Skondapalli@csafeglobal.com | Hyderabad | Preventive Maintenance |  |  |  | 2024-12-30 15:05 | mum.depot@crystalgroup.in | SOFTBOX | TITU8257288 | 20FT | TK MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | DISPLAY FOUND BLUR | NEED TO CHANGE DISPLAY | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC061 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | RAMIZ | Yes | PREVENTIVE MAINTENANCE | 2024-12-31 17:55 | operation@crystalgroup.in | YES | DEC051 | 2024-12-31 | Consumables, FOC | SOFTBOX | HYDERABAD | TITU8257288 | SITE | FOC | TK-MP4000 | 2025-02-10 14:58 | operation@crystalgroup.in | YES | DEC051 | YES | https://drive.google.com/open?id=1i-_iYiyBxNd4TYxi4uwA_pKvKyrMVfKX |  | 2024-11-26 14:44 | [9 empty] | 2025-01-17 18:15
DEC062 | 2024-12-30 15:20 | crm@crystalgroup.in | Crystal | NA | NA | NA | CGMU2989060 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:24 | service@crystalgroup.in | Crystal | CGMU2989060 | 20 ft | carrier thine line | REPAIR | STOCK | NA | Controller, Contactor, Key Pad, Power Plug, Curtains, EVP motor defectives | na | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC062 | Carrier - Thinline | Thinline | LSM 60197754 | LSM60197754 |  |  | JSGA622180043 | RAMIZ | No | Repair & Replacement | 2025-01-08 13:01 | operation@crystalgroup.in | YES | JAN069 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | CGMU2989060 | DEPOT | FOC | CARRIER-THINLINE | 2025-02-27 15:37 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-27 15:38 | service@crystalgroup.in | NO | [7 empty] | 2025-02-22 12:32 | 2025-02-20 |  |  |  |  | CGMU2989060 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5 Bar and Discharge 13.5 | 13.1/13.2/13.5 | 404/405/405 | Full | NA | Replaced Supply Sensor.Key Pad, Controller canalized from container TRIU6681671, Display replaced | No | https://drive.google.com/open?id=1GVoRkvOz2IT_ih2Wx6X4RABm_-YYFCMW, https://drive.google.com/open?id=1qxlGpwiGSKc42xzLD28i3rNXa8dZRals |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC063 | 2024-12-30 15:25 | crm@crystalgroup.in | Crystal | NA | NA | NA | TRIU6681671 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-08 13:28 | service@crystalgroup.in | Crystal | TRIU6681671 | 20 ft reefer | carrier thine line | REPAIR | STOCK | FOC | Power plug and curtain missing, N2 Gas, EVP Motor, SM Valve, Contactor, Filter drier, ISO Plug, R134 A gas. | For future process need to fix those spares. | Power plug , EVP Motor, SM Valve, Contactor, Filter drier, ISO Plug, R134 A gas 5KGS . | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC063 | Carrier - Transcold | Transcold | NSG 60383850 | KE 04959025 |  | Used |  | SHAHBUDDIN |  | Repair & Replacement | 2025-01-08 19:40 | operation@crystalgroup.in | YES | JAN082 | 2025-01-08 | Consumables, Spares, FOC | CRYSTAL YARD | JNPT | TRIU6681671 | DEPOT | FOC | CARRIER-THINLINE | 2024-11-19 18:30 | [6 empty] | 2024-11-19 18:31 | [9 empty] | 2025-01-17 18:12
DEC064 | 2024-12-30 15:29 | crm@crystalgroup.in | Crystal | NA | NA | NA | CCLU1030700 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-08 13:34 | service@crystalgroup.in | Crystal | CCLU1030700 | 20 ft | carrier thine line | REPAIR | STOCK | FOC | Power plug and curtain missing, EVP motor missing, controller damage, Condenser motor bearing need to replace. | For future process need to fix those spares. | ISO plug , EVP motor , controller ML 3, Condenser motor BEARING 2 NOS 6205 . | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC064 | Carrier - Thinline | Thinline |  |  |  | Refurbished |  | SHAHBUDDIN |  | Repair & Replacement | 2025-01-08 18:42 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-01 14:20 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 19:07 | operation@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
DEC065 | 2024-12-30 15:31 | crm@crystalgroup.in | Crystal | NA | NA | NA | CICU3876591 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:32 | service@crystalgroup.in | Crystal | CICU3876591 | 10 ft blast | thermoking mp 4000 | REPAIR | STOCK | FOC | ISO plug | need to fix iso plug | YES | yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC065 | Thermoking | Magnum + | E0GM030860 | ABC782800322010299 | ABC782900321510393 | Brand New |  | RAMIZ | No | Repair & Replacement | 2025-01-08 19:42 | operation@crystalgroup.in | YES | JAN070 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | CICU3876591 | DEPOT | FOC | TK-MP4000 | 2025-02-01 14:22 | operation@crystalgroup.in | YES | JAN070 | YES |  |  | 2025-02-01 19:08 | operation@crystalgroup.in | YES | JAN070 | YARD | [5 empty] | 2025-02-26 18:33 | 2024-12-30 |  |  |  |  | CICU3876591 |  |  |  | Thermo king | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 and 20 | 9.9/9.8/9.8 | 400/411/411 | Full | Power Plug Missing | Need to replace Power Plug | No | https://drive.google.com/open?id=1uPEKsEwRoDFpxCXrEO61_OEid51ufage |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC066 | 2024-12-30 15:34 | crm@crystalgroup.in | Crystal | NA | NA | NA | CICU1938924 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-04 15:39 | mum.depot@crystalgroup.in | Crystal | CICU1938924 | 20FT | THERMOKING MP4000 | REPAIR | STOCK | FOC | ISO PLUG MISSING | NEED TO FIX ISO PLUG | ISO PLUG | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC066 | Thermoking MP-4000 | MP 4000 |  |  |  | Brand New |  | RAMIZ | No | Repair & Replacement | 2025-01-08 19:45 | operation@crystalgroup.in | YES | JAN071 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | CICU1938924 | DEPOT | FOC | TK-MP4000 | 2025-02-01 14:24 | operation@crystalgroup.in | YES | JAN071 | YES |  |  | 2025-02-01 19:09 | operation@crystalgroup.in | YES | JAN071 | YARD | [5 empty] | 2025-02-26 12:28 | 2025-01-14 |  |  |  |  | CICU1938924 |  |  |  | Thermo king | -20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8 & 19 Bar | 9.9/9.8/9.9 | 410/410/410 | Full | Power Plug Missing | Replaced ISO Power Plug | No | https://drive.google.com/open?id=1hFqYOdBjCpMcBXWALDzd7lTDSOGopk5R |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC067 | 2024-12-30 15:36 | crm@crystalgroup.in | Crystal | NA | NA | NA | GRMU3707485 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:41 | service@crystalgroup.in | Crystal | GRMU3707485 | 20 ft blast | daikin | REPAIR | STOCK | FOC | Power plug required for unit 1 & unit 3 and curtain missing / ONE UNIT REMOVED & FIX NEPAL | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC067 | Daikin |  |  |  |  | used |  | RAMIZ | No | Repair & Replacement | 2025-01-08 19:47 | operation@crystalgroup.in | YES | JAN072 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | GRMU3707485 | DEPOT | FOC | DAIKIN | 2025-02-01 14:28 | operation@crystalgroup.in | YES | JAN072 | YES |  |  | 2025-02-01 19:10 | operation@crystalgroup.in | YES | JAN072 | YARD | [5 empty] | 2025-02-26 11:58 | 2025-02-26 |  |  |  |  | GRMU3707485 |  |  |  | Thermo king | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Full | NA | 2 Unit Fitment and additional work done from Supplier Massk ENterprices | No | https://drive.google.com/open?id=1WDNB6qIZqw8HD-AH0PD2DAkXWEkg-jdQ, https://drive.google.com/open?id=1Yzue4OsAKKE6EsKl46QiHCg4JYbnywEO |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC068 | 2024-12-30 15:37 | crm@crystalgroup.in | Crystal | NA | NA | NA | HDMU5221979 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-04 15:52 | mum.depot@crystalgroup.in | Crystal | HDMU5221979 | 20FT | DAIKIN | REPAIR | STOCK | FOC | CONTROLLER TAKEN FOR SITE BY VIRENDRA,ISO PLUG MISSING, CABLE SHORT | NEED TO FIX CONTROLLER, ISO PLUG REQUIRED AND NEED TO ADD 8 METER POWER CABLE | CONTOLLER DCOS III F, ISO PLUG AND powe cabe 4 CORE CARE 8meters | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC068 | Daikin |  |  |  |  | USed |  | RAMIZ | No | Repair & Replacement | 2025-01-08 19:50 | operation@crystalgroup.in | YES | JAN074 | 2025-08-01 | Spares, FOC | CRYSTAL YARD | JNPT | HDMU5221979 | DEPOT | FOC | DAIKIN | 2025-02-10 14:54 | operation@crystalgroup.in | YES | JAN074 | YES |  |  | 2025-02-11 11:03 | mum.depot@crystalgroup.in | YES | JAN074 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-02-13 21:46
DEC069 | 2024-12-30 15:43 | crm@crystalgroup.in | Crystal | NA | NA | NA | TCLU1911479 | Repair & Replacement | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-04 15:34 | mum.depot@crystalgroup.in | Crystal | TCLU1911479 | 20FT | DAIKIN | REPAIR | STOCK | FOC | SHEET KEY DAMAGE, ISO PLUG MISSING, | SHEET KEY AND ISO NEED TO CHANGE | SHEET KEY AND ISO PLUG | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC069 | DAIKIN LXE |  |  |  |  | USed |  | RAMIZ | No | Repair & Replacement | 2025-01-08 19:52 | operation@crystalgroup.in | YES | JAN075 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | TCLU1911479 | DEPOT | FOC | DAIKIN | 2025-02-01 14:32 | operation@crystalgroup.in | YES | JAN075 | YES |  |  | 2025-02-01 19:10 | operation@crystalgroup.in | YES | JAN075 | YARD | [5 empty] | 2025-02-22 12:58 | 2025-02-15 |  |  |  |  | TCLU1911479 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 181KPA and 1600 KPA | 9.5/9.2/9.3 | 415/411/413 | Full | NA | NA | No | https://drive.google.com/open?id=13DvOgvMM7MllJ10xvUjZiB7uMQwihi0S, https://drive.google.com/open?id=1_zSOSJTtVtSblZ5josNfhZw0O0FFQkmM |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC070 | 2024-12-30 15:55 | crm@crystalgroup.in | Crystal | NA | NA | NA | TITU7263521 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:44 | service@crystalgroup.in | Crystal | TITU7263521 | 10 ft | daikin | REPAIR | STOCK | FOC | battery missing, keypad damage, leakage found, cable missing, ISO plug is rusted, Complete unit need to be replace | need to replaced full unit | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC070 | Daikin |  |  |  |  | brand New | JSGA622180055 | RAMIZ | No | REPAIRS & REPLACEMENT | 2025-01-08 19:54 | operation@crystalgroup.in | YES | JAN076 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | TITU7263521 | DEPOT | FOC | DAIKIN | 2024-11-19 18:30 | [6 empty] | 2024-11-19 18:31 | [9 empty] | 2025-01-17 18:12
DEC071 | 2024-12-30 16:01 | crm@crystalgroup.in | Crystal | NA | NA | NA | HDMU5542114 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-04 15:21 | mum.depot@crystalgroup.in | Crystal | HDMU5542114 | 40FT | CARRIER THINLINE | REPAIR | STOCK | FOC | FLOOR REPAIRING DONE, PTI DONE BY RAMEZ, PAINTING BALANCE | NEED TO PAINT | NA | No |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC071 | Carrier | Thineline | [5 empty] | YARD TECHNICIAN | No | REPAIRS & REPLACEMENT | 2025-01-08 18:43 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-20 16:09 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-20 16:09 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-24 18:00 | 2025-01-09 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | need to repair flooring | Flooring repair done and Both Side INt CVP revitting and selicon work done | No | https://drive.google.com/open?id=1tAnPj0LCKVFK4dhQ0ITlU_-izF7zjZ2o, https://drive.google.com/open?id=1qzGI4mTVgd84fFgHckbup69lRfTDoanM |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC072 | 2024-12-30 16:02 | crm@crystalgroup.in | Crystal | NA | NA | NA | CRLU3181686 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-30 18:03 | rahul.gawade@crystalgroup.in | Crystal Yard | CRLU3181686 | 20FT Reefer | NA | READINESS OF CONTAINER | STOCK | NA | No Refer Machine | Refer Machine Required | Refer Machine Required |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC072 | Daikin | Daikin |  |  |  | Used |  | RAMIZ | No | REPAIRS & REPLACEMENT | 2024-12-31 17:47 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:48 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-10 16:27 | 2025-02-10 |  |  |  |  | CRLU3181686 |  |  |  | Daikin | -20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 181 KPA & 1658 | 9.5/9.3/9.1 | 415/411/413 | Full | NA | Fixed New complete Unit Daikin Baffle Plate Canalize from CCLU1030700 | No | https://drive.google.com/open?id=1XezyIZ7k8Ka2wHcmmbiWgGRP_2dFUpZ_, https://drive.google.com/open?id=1EAneLU0bdzgtkpe6Fz762TJiNY55CmhI |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC073 | 2024-12-30 16:07 | crm@crystalgroup.in | Crystal | NA | NA | NA | TRIU8836134 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-04 15:17 | mum.depot@crystalgroup.in | Crystal | TRIU8836134 | 40FT | NA | REPAIR | STOCK | FOC | MAIN UNIT MISSING, OUTSIDE L/R PANEL PUSHED OUT | UNIT REQUIRED, NEED TO REPAIR SIDE PANELS | UNIT | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC073 | Carrier |  |  |  |  | Used |  | RAMIZ | No | REPAIRS & REPLACEMENT | 2025-01-08 19:55 | operation@crystalgroup.in | YES | JAN077 | 2025-01-08 | Spares, FOC | CRYSTAL YARD | JNPT | TRIU8836134 | DEPOT | FOC | DAIKIN | 2025-02-12 16:29 | [6 empty] | 2025-02-12 16:30 | [9 empty] | 2025-02-13 21:46
DEC074 | 2024-12-30 16:10 | crm@crystalgroup.in | Crystal | NA | NA | NA | GLDU0894019 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 17:37 | service@crystalgroup.in | Crystal | GLDU0894019 | 40 ft | na | NA | NA | NA | Ready for dispatch | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC074 | [7 empty] | RAMIZ | No | REPAIRS & REPLACEMENT | 2024-12-31 17:48 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:49 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 11:18 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC075 | 2024-12-30 16:19 | operation@crystalgroup.in | CRYSTAL (AMEYA HYDRO ENGINEERING) | PUSHPA | - | - | QNLU1018110 | PORTA CABIN | PUSHPA | - | JNPT | Running with issues |  |  |  | 2024-12-30 16:26 | operation@crystalgroup.in | CRYSTAL | QNLU1018110 | 20GP | DRY | READINESS OF CONTAINER | STOCK | FOC | CUSTOMIZE CONTAINER | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC075 | [7 empty] | RAMIZ | No | PORTA CABIN | 2024-12-30 16:39 | operation@crystalgroup.in | YES | DEC044 | 2024-12-30 | Consumables, Spares, FOC | CRYSTAL (AMEYA HYDRO ENGINEERING) | JNPT | QNLU1018110 | DEPOT | FOC | DRY | 2025-01-08 12:30 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-14 11:05 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 16:01 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC076 | 2024-12-30 16:20 | crm@crystalgroup.in | Crystal | NA | NA | NA | TRLU8190780 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 17:33 | service@crystalgroup.in | Crystal | TRLU8190780 | na | na | NA | NA | NA | already dispatched | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC076 | [7 empty] | RAMIZ | No | REPAIRS & REPLACEMENT | 2024-12-31 17:49 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:50 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:01 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 16:05 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC077 | 2024-12-30 16:24 | operation@crystalgroup.in | CRYSTAL (AMEYA HYDRO ENGINEERING) | PUSHPA | - | - | GESU2720771 | PORTA CABIN | PUSHPA | - | JNPT | Running with issues |  |  |  | 2024-12-30 16:30 | operation@crystalgroup.in | CRYSTAL (AMEY HYDRO ENGINEERING) | GESU2720771 | 20GP | DRY | READINESS OF CONTAINER | STOCK | FOC | CUSTOMIZE CABIN | NA | YES |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC077 | [7 empty] | RAMIZ | No | PORTA CABIN | 2024-12-30 16:40 | operation@crystalgroup.in | YES | DEC045 | 2024-12-30 | Consumables, Spares, FOC | CRYSTAL 9 AMEYA HYDRO ENGINEERING ) | JNPT | GESU2720771 | DEPOT | FOC | DRY | 2025-01-08 12:30 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-14 11:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 16:06 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC078 | 2024-12-30 16:25 | crm@crystalgroup.in | Crystal | NA | NA | NA | GESU9440432 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:28 | service@crystalgroup.in | Crystal | GESU9440432 | 40 ft | carrier elight line | REPAIR | STOCK | FOC | ISO Plug,compressor elight line , controller ,disply , filter drier, gas r134a 5 kgs n2 | na | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC078 | Carrier-Eliteline | Elite line | LSP 60212379 | KE 04605256 |  | Used | JSGA622170282 | RAMIZ | No | REPAIRS & REPLACEMENT | 2025-01-08 19:58 | operation@crystalgroup.in | YES | JAN078 | 2025-08-01 | Consumables, Spares, FOC | CRYSTAL YARD | JNPT | GESU9440432 | DEPOT | FOC | CARRIER-THINLINE | 2025-01-29 15:44 | crm@crystalgroup.in | YES | JAN078 | YES |  |  | 2025-01-29 16:01 | crm@crystalgroup.in | YES | JAN078 | ARRENGING AT SITE | [5 empty] | 2025-02-24 18:14 | 2025-02-24 |  |  |  |  | GESU9440432 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Full | NA | Replaced Compressor,N2 Test Vaccume ,Compressor Oil 3 Ltr R134 A topup 5.21 Kg | No | https://drive.google.com/open?id=1_V4jLcLKbtOzSwot7fh7PlQsbg9XT3_u, https://drive.google.com/open?id=1doADWWUnQ1tvyv8DWs1TEnVcUKPB2FEh |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
DEC079 | 2024-12-30 16:26 | crm@crystalgroup.in | Crystal | NA | NA | NA | HNKU5111970 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 17:41 | service@crystalgroup.in | Crystal | HNKU5111970 | 40 ft | na | NA | NA | NA | panting & logo balance | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC079 | [7 empty] | RAMIZ | No | REPAIRS & REPLACEMENT | 2024-12-31 18:10 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:10 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 11:42 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 11:16 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC080 | 2024-12-30 16:28 | crm@crystalgroup.in | Crystal | NA | NA | NA | HNKU5113762 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 17:45 | service@crystalgroup.in | Crystal | HNKU5113762 | 40 FT | NA | NA | NA | NA | Already dispatched | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC080 | [7 empty] | RAMIZ | No | REPAIRS & REPLACEMENT | 2024-12-31 18:11 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 18:11 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 11:42 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-21 16:07 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC081 | 2024-12-30 16:30 | crm@crystalgroup.in | Crystal | NA | NA | NA | TITU8259655 | REPAIRS & REPLACEMENT | Rahul | NA | JNPT | Running with issues |  |  |  | 2024-12-31 18:37 | service@crystalgroup.in | Crystal | Painting touch up and cleaning | 20 FT | NA | REPAIR | STOCK | NA | Painting touch up and cleaning | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC081 | [7 empty] | RAMIZ | No | REPAIRS & REPLACEMENT | 2025-01-08 18:59 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-20 16:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-20 16:08 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-28 16:51 | [54 empty] | service@crystalgroup.in | DRY/Others
DEC082 | 2024-12-30 16:42 | crm@crystalgroup.in | Cipla | Anant Ravut | 7774089236 | Sr. Engineer | CRIU4024028 | Installation 2 Bay Super Store | Pushpalata Shetty | anant.ravut@cipla.com | Goa | Installation |  |  |  | 2024-12-31 15:55 | service@crystalgroup.in | Cipla | CRIU4024028 | 40 ft 2 bay | tk mp 4000 | INSTALLATION | SALE | CHARGEABLE | installation | na | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC082 | Thermoking | TK MP 4000 |  |  |  | New |  | SHAHBUDDIN, Harish , Akshay |  | Installation 2 Bay Super Store | 2024-12-31 17:50 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:50 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:02 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
DEC083 | 2024-12-30 16:52 | crm@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | Jitendra Malakar | 9630093361 / 7509699064 | Officer (Engineering) | GESU956813 | DOOR NOT CLOSING | Sahil | hvacsez@symbiotec.in | SEZ ,Pithampur | Running with issues |  |  |  | 2024-12-31 14:55 | service@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | GESU9568130 | 40 FT | NA | SERVICE-ON CALL | SALE | NA | UN ABALE TO CLOSE THE DOOR BOTH | NEED TO CHECK DOOR ALIMENT & GROUND LEVEL ISSUE | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC083 | [7 empty] | UMESH |  | DOOR NOT CLOSING | 2024-12-31 17:51 | mum.depot@crystalgroup.in | NO | [9 empty] | 2024-12-31 17:51 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-04 12:03 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-06 15:37 | 2024-12-31 |  |  |  |  | GESU9568130 |  |  |  | Carrier | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | SERVICE DOOR un able to close | need to check ground level | No | https://drive.google.com/open?id=18VbCcZJnheE7PaA5zyJDUgFCGP5Yf9EH, https://drive.google.com/open?id=1JDoIhfogUZCL2TeAaCDGBUUhDCZNJQAc |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
DEC084 | 2024-12-30 18:39 | operation@crystalgroup.in | RELIANCE | Mohit Rai | 9023419864 | SITE PERSON | CICU2779909 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NINAD | mohit2.rai@qwik.co.in | Ahmedabad | Running with issues |  |  |  | 2024-12-31 18:49 | service@crystalgroup.in | RELIANCE | CICU2779909 | 10 ft blast | thermoking mp 4000 | SERVICE-ON CALL | LEASE | FOC | PCM not freeze in expected time . | the reefer unit working sound & good condition . Need a heat lode calculation & explanation | no |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC084 | Thermoking | Magnum Plus | E0GM030263 | ABC782800322010201 |  | BrandNew |  | RAMIZ | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-02-07 10:14 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-07 10:14 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-11 11:00 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-24 18:39 | 2025-02-19 |  |  |  |  | CICU2779909 |  |  |  | Thermo king | -35*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 20.9A | 9.7/9.6/9.7 | 417/416/417 | Not done | NA | NA | No | https://drive.google.com/open?id=1AsL1nUmLlJ-y3_YdUoT6yAoGYnAQ44Xg, https://drive.google.com/open?id=1bGZuYgMscpIDVpxizykNLh780Mu5LjOx |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
DEC086 | 2024-12-31 13:04 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | +91 96527 25368 | On Duty Officer | DCUNIT09 | Evaporator coil motor making noise | Sahil | M.Ramakrishna@divislabs.com | Hyderabad | Running with issues |  |  |  | 2024-12-31 17:51 | service@crystalgroup.in | Divis Labs | DCUNIT09 | 40 ft | carrier thine line | SERVICE-ON CALL | SALE | CHARGEABLE | evaporator fan motor noise both | need to replace both evaporator fan motors . | na |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC086 | [7 empty] | RAMIZ | No | Evaporator coil motor making noise | 2025-01-08 20:01 | operation@crystalgroup.in | YES | JAN079 | 2025-08-01 | Spares, Paid | DIVIS LAB | HYDERABAD | DCUNIT09 | SITE | PAID | CARRIER-THINLINE | 2025-02-01 14:38 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 19:11 | operation@crystalgroup.in | NO | [7 empty] | 2025-01-17 18:15
DEC087 | 2024-12-31 16:37 | crm@crystalgroup.in | Qwik Supply | Ankit singh | 9780266737 | CPC Manager | APRU5066497 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpalata Shetty | ankit111.singh@qwik.co.in | Surat | Running with issues |  |  |  | 2024-12-31 17:00 | service@crystalgroup.in | Qwik Supply | APRU5066497 | 40 ft | carrier tine line | SERVICE-ON CALL | LEASE | FOC | condense coil heavy dirty,( suspected = filter drier & less gas & defrost sensor ) | clean condenser coil with fresh water , under observation nest 24 hrs | yes |  |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=DEC087 | Carrier - Thinline | Thinline |  |  |  |  | JSGA623040296 | RAMIZ |  | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-01-02 11:16 | operation@crystalgroup.in | YES | DEC052 | 2025-01-02 | Consumables, FOC | RELIANCE | SURAT | APRU5066497 | SITE | FOC | CARRIER-THINLINE | 2025-01-02 16:30 | crm@crystalgroup.in | YES | DEC052 | YES |  |  | 2025-01-02 16:35 | crm@crystalgroup.in | YES | DEC052 | TECHNICIAN |  |  | Ramiz |  |  | 2025-01-05 22:19 | 2025-01-03 |  |  |  |  | APRU5066497 |  |  |  | Carrier | - 21'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B / 12.3B | 12.1/12.3/12.2 AMPS | 410/411/410 | Not done | ICE FOUNDATION IN SUPPLY SIR FLOW AWAY (60% COOL AIR BLOCKED )& CONDENSER COIL DIRTY | removed all ice from t floor & supply air flow away & clean condenser coil fresh water | No | https://drive.google.com/open?id=1q_YlTvnzaZmNg5rBgtB9qJHp_5xo6Lr6, https://drive.google.com/open?id=1vwHJ9q4qR6REdaeZmkOfGEErlfXGMhub |  |  | NA | No | No | Can be done on next PM | na | NA | service@crystalgroup.in
JAN001/25 | 2025-01-02 14:33 | crm@crystalgroup.in | Reliance Wagholi | Mangesh Vannere | 7020374749 | NA | PCIU6015055 | MCB tripped when Compressor is ON | Ninad | Mangesh.Vannere@ril.com | Pune | Running with issues |  |  |  | 2025-01-09 11:54 | service@crystalgroup.in | Reliance Wagholi | PCIU6015055 | 40 ft | Daikin | SERVICE-ON CALL | LEASE | FOC | unit trapping during compressor operation. | as par the customer check all cable connection is ok power supply voltage stable still same condition . need a visit | suspected =1) discharge sensor,2) controller iiiD , 3 )temperature sensor & 4) pt & ct bord , 5)compressor contactor 30 amps | SUSPECTED | loose connection of incoming main power supply & old cable splicing after few hours getting heat then power supply or compressor motor winding over heat reduce & tripped . / suspected discharge sensor or controller or pcct & compressor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN001 | Daikin | Daikin | NA | NA | NA | used |  | RAMIZ | Yes | MCB tripped when Compressor is ON | 2025-01-13 16:52 | operation@crystalgroup.in | YES | JAN087 | 2025-01-13 | Spares, FOC | Reliance Wagholi | WAGHOLI | PCIU6015055 | SITE | FOC | DAIKIN | 2025-01-13 16:53 | operation@crystalgroup.in | YES | JAN087 | YES |  |  | 2025-01-17 12:06 | mum.depot@crystalgroup.in | YES | JAN087 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-01-20 18:01 | 2025-01-19 |  |  |  |  | PCIU6015055 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/170 | 9.8/9.9/9.8 | 415/415/4145 | Short | FOUND DISPLAY AND SHEETKEY/PTCT BOARD DEFECTIVE | REPLACED | No | https://drive.google.com/open?id=1OTr_ahpkXJfzPgR1-mK4pxFUJLQDAlvV |  |  | NA | No | No | Can be done on next PM | NA | NA | mum.depot@crystalgroup.in | REEFER
JAN002/25 | 2025-01-02 17:52 | crm@crystalgroup.in | DR REDDY CTO 06 | Tadikonda Kishore | 96767 55199 | NA | KKFU6712802 | PREVENTIVE MAINTENANCE | Sahil | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-01-04 18:02 | crm@crystalgroup.in | DR REDDY CTO 06 | KKFU6712802 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | Preventive Maintenance | Need to replace Condenser Coil | Carrier Thinline Condenser Coil 1 No Liquid Filter 1 No Refrigerant Gas - R134a 5.2 kgs Nitrogen 1 No Brazing Torch Heavy Duty 1 No Vaccum Pump RX-6D Double Stage (11.8CFM) 1 No | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN002 | Carrier - Thinline | Thinline |  | 69NT40541321 |  |  | JSGA623040171 | SHAHBUDDIN |  | PREVENTIVE MAINTENANCE | 2025-01-04 18:11 | crm@crystalgroup.in | YES | DEC034 | 2024-12-24 | Spares | DR REDDY CTO 6 | Vishakapatnam | KKFU6712802 | SITE | FOC | CARRIER-THINLINE | 2025-01-04 18:16 | crm@crystalgroup.in | YES | DEC034 | YES | https://drive.google.com/open?id=1sjXYFXYVC-Tgj4t4ePWq8reX_PJmihOo |  | 2025-01-04 18:28 | mum.depot@crystalgroup.in | YES | DEC034 | COURIER | 412531754 | Dr Reddy CTO 06 | SHAHBUDDIN | https://drive.google.com/open?id=1gULrypP2SxjWvcJ3u7PRp8Hb55GnGfIa |  | 2025-01-09 21:09 | 2025-01-09 |  |  |  |  | KKFU6712802 |  |  |  | Daikin | + 4.5 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/18 Bar | 9.9/9.9/.9.9 | 415/415/415 | Short | Replaced new condenser coil | Repaired & replaced new condenser coil | No | https://drive.google.com/open?id=1nUu5emUzHU4L5TcqsTX6hSxoIB0yLNCY, https://drive.google.com/open?id=1ML8UV8cxYmSw2qOPDAPWg_TyPSUCSGHu, https://drive.google.com/open?id=1zfFUF8KRI64qO3Bb56mjA9o5HKeE2JnW |  |  | NA | Yes | No | Can be done on next PM | NA | NA | technician@crystalgroup.in
JAN003/25 | 2025-01-04 16:33 | operation@crystalgroup.in | Crystal | SHABUDIN |  | TECHNICIAN | CXRU1031758 | MOTOR ISSUE | NINAD | service@crystalgroup.in | JNPT | Running with issues |  |  |  | 2025-01-07 12:12 | service@crystalgroup.in | Crystal | CXRU1031758 | 40 ft | 40 ft reefer | REPAIR | STOCK | FOC | R/side Evaporator motor noise | need to replaced bearing both bearing | 2 nos bearing | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN003 | Daikin LXE | Daikin LXE |  |  |  | Used |  | SHAHBUDDIN |  | MOTOR ISSUE | 2025-01-04 17:06 | operation@crystalgroup.in | YES | DEC055 | 2025-01-04 | Spares, FOC | CRYSTAL YARD | JNPT | CXRU1031758 | DEPOT | FOC | DAIKIN | 2025-01-08 12:31 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-14 11:09 | mum.depot@crystalgroup.in | YES | JAN067 | ARRANGED AT DEPOT | NA | NA | SHUBHAM |  |  | 2025-01-21 16:48 | 2025-01-07 |  |  |  |  | CXRU1031758 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  |  | 10/9.7/9.9 | 415/413/411 | Full | NA | PTI done | No | https://drive.google.com/open?id=1iAIQ1KvpXnht90-c7CU8kDoF0EChxkNR, https://drive.google.com/open?id=1W5E0_dTcdjKm4kDH2B9yn_rZSA1Y5NGy |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JAN004/25 | 2025-01-07 11:31 | operation@crystalgroup.in | AMUL GOREGAON MUMBAI | SUJIT | 8291259886 | CONTAINER MANAGER | CXRU1056669 | CONTAINER NOT WORKING | NINAD | sujit.sangle@amul.coop | GOREGAON | Running with issues |  |  |  | 2025-01-07 11:55 | service@crystalgroup.in | AMUL GOREGAON MUMBAI | CXRU1056669 | 40 | daikin zestia | SERVICE-AT SITE | LEASE | AMC | unit tripped during normal operation due to MCB defective (32 amps) main cable joint burnt & condenser coil dirty | replaced new 63 AMPS & cable splicing done & cleaned condenser coil with fresh water | EVP MOTOR BEARING | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN004 | Daikin | LX10F15A2 | M000515 | RC1107000961 | WILCO S4AA00095 | Used |  | RAMIZ |  | CONTAINER NOT WORKING | 2025-01-07 14:16 | mum.depot@crystalgroup.in | NO | [9 empty] | 2025-01-07 14:17 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-07 14:18 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-07 13:44 | 2025-01-06 |  |  |  |  | CXRU1056669 |  |  |  | Daikin | +4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5 B/12.1B | 8.1./8.2/8.1 AMPS | 411/411/410 | Not done | unit tripped during normal operation due to MCB defective (32 amps) main cable joint burnt & condenser coil dirty | replaced new 63 AMPS & cable splicing done & cleaned condenser coil with fresh water | No | https://drive.google.com/open?id=1BwVk0lECl8bAxJx-cGiKZDU3qcVGdbEH, https://drive.google.com/open?id=1DYecz_qaGHGMNyccPjgNXBVInyMSVX90 |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
JAN005/25 | 2025-01-07 12:44 | operation@crystalgroup.in | AMUL GOREGAON MUMBAI | SUJIT | 8291259886 | CONTAINER MANAGER | GESU9440129 | CONTAINER NOT WORKING | NINAD | sujit.sangle@amul.coop | GOREGAON | Running with issues |  |  |  | 2025-01-07 13:29 | service@crystalgroup.in | AMUL GOREGAON MUMBAI | GESU9440129 | 40 ft | carrier elight line | SERVICE-AT SITE | LEASE | AMC | unit tripped during normal operation due to MCB defective (32 amps)& condenser coil dirty | replaced new 63 AMPS & cleaned condenser coil with fresh water . | na | No |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN005 | Carrier - Eliteline | Elite line | 69NT40551509 |  |  | USED |  | RAMIZ |  | CONTAINER NOT WORKING | 2025-01-07 14:15 | mum.depot@crystalgroup.in | NO | [9 empty] | 2025-01-07 14:17 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-01-07 14:18 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-07 14:12 | 2025-01-06 |  |  |  |  | GESU9440129 |  |  |  | Carrier | +4.C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B/12.3B | 9.1/9.2/9.1 amps | 411/410/411 | Not done | unit tripped during normal operation due to MCB defective (32 amps)& condenser coil dirty | replaced new 63 AMPS & cleaned condenser coil with fresh water . | No | https://drive.google.com/open?id=1VDSpGNftMz9yUBm4L4pkHHAwk0DSuzHW, https://drive.google.com/open?id=1mYp7jKUiIuISvlv_yik8q5CYy7DqcszR |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in
JAN006/25 | 2025-01-07 14:31 | mum.depot@crystalgroup.in | Crystal | NA | NA | NA | CXRU1032775 | REPAIRS & REPLACEMENT | RAMIZ | NA | JNPT | Running with issues |  |  |  | 2025-01-07 14:34 | service@crystalgroup.in | Crystal | CXRU1032775 | 40 ft | Daikin | REPAIR | STOCK | FOC | leakage from compressor body bottom side | need to replaced a new compressor | scroll compressor Dakin | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN006 | [7 empty] | SHAHBUDDIN |  | REPAIRS & REPLACEMENT | 2025-01-08 19:29 | operation@crystalgroup.in | YES | JAN080 | 2025-01-08 | Consumables, Spares, FOC | CRYSTAL | JNPT | CXRU1032775 | DEPOT | FOC | DAIKIN
JAN007/25 | 2025-01-07 14:54 | operation@crystalgroup.in | RELIANCE | SANDEEP RATHOD | 7977704469 | MANAGER | TRIU6681440 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NINAD | sandeep3.rathod@ril.com | Taloja | Running with issues |  |  |  | 2025-01-09 18:53 | service@crystalgroup.in | RELIANCE | TRIU6681440 | 20 ft reefer dual machine | carrier thine line | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Removed ice with hot water . condenser coil clean with fresh water . currently the reefer unit working normal & temperature pulling down to the set point . The reefer unit still under observation . | NA | No | ice foundation on t bar floor , air circulation blockby pcm pad . | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN007 | Carrier - Transcold | Transcold |  |  |  | Used |  | SHUBHAM | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-01-22 17:12 | operation@crystalgroup.in | YES | JAN091 | 2025-01-22 | Consumables, Spares, FOC | RELIANCE | TALOJA | TRIU6681440 | SITE | FOC | CARRIER-THINLINE | 2025-01-27 15:05 | crm@crystalgroup.in | YES | JAN091 | YES |  |  | 2025-01-27 15:06 | crm@crystalgroup.in | YES | JAN091 | TECHNICIAN |  |  | SHUBHAM |  |  | 2025-01-27 16:27 | 2025-01-24 |  |  |  |  | TRIU6681440 |  |  |  | Carrier | -30*C | Clean | [22 empty] | Okay | [7 empty] | Display & keypad not working ,dry filter needed to be replaced ,gas top up required | Spares need to be arranged work will be completed on next PM visit | Yes | https://drive.google.com/open?id=1-cWxav-4Z4hwQkiJ0AFXt-Il8N5pYfZs, https://drive.google.com/open?id=1PHkqh3w9h2ZjEgk3KT5dgTnFIhP58lDJ, https://drive.google.com/open?id=1vXUwbdhOWZGHZczcc96gB_aWBHVM-Msr, https://drive.google.com/open?id=1kEpEKCBP5d6rZ8j8-r94MglyqODFxnk2 |  |  | TRIP068 | Yes | Yes | Urgent | Display & keypad not working ,dry filter needed to be replaced ,gas top up required | Display 1 Keypad 1 Dry Filter 1 Supply Sensor 2 R134 2 kg | crm@crystalgroup.in | REEFER
JAN008/25 | 2025-01-07 18:56 | mum.depot@crystalgroup.in | Crystal | NA | NA | NA | CICU2094068 | REPAIRS & REPLACEMENT | NA | NA | JNPT | Running with issues |  |  |  | 2025-01-07 19:00 | service@crystalgroup.in | Crystal | CICU2094068 | 10 FT | MP 4000 THERMOKING | REPAIR | STOCK | FOC | DISPLY DEFECTIVE & ISOPLUG MISSIN & MAN TRAP MISSING & STRIP CURTAN 13 NO DAMAGED , FLOOR NORMAL RISTED | FOR FOUTURE PROCRESS NEED TO FIX DISPLY & ISOPLUG | DISPLY IN UNDER WARRENTY | Yes |  | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN008 | Thermoking | Magnum Plus | E0GM029715 | ABC782800321410498 |  | BrandNew |  | RAMIZ |  | REPAIRS & REPLACEMENT | 2025-01-08 19:26 | operation@crystalgroup.in | YES | JAN081 | 2024-01-08 | Consumables, Spares, FOC | CRYSTAL | JNPT | CICU2094068 | DEPOT | FOC | TK-MP4000 | 2025-02-01 14:44 | operation@crystalgroup.in | YES | JAN081 | YES |  |  | 2025-02-01 19:12 | operation@crystalgroup.in | YES | JAN081 | AT YARD
JAN009/25 | 2025-01-09 14:36 | service@crystalgroup.in | Lupin Limited | Amit Sakpal | 9326179943 | System Operator | CCLU1036859 | MOTOR MAKING NOISE | SHUBHAM/RAMIZ | depotcwhmumbai@lupin.com | Bhiwandi | Running with issues |  |  |  | 2025-01-09 14:43 | service@crystalgroup.in | Lupin Ltd | CCLU1036859 | 20 FT | CARRIER THINE LINE | SERVICE-AT SITE | LEASE | FOC | Unit making noise | Need to replace both bearing | 2 nos bearing | Yes | Due to condenser fan motor bearing rusted. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN009 | Carrier |  |  |  |  | Used | JSGA623040314 | SHUBHAM | Yes | MOTOR MAKING NOISE | 2025-01-10 15:11 | operation@crystalgroup.in | YES | JAN083 | 2025-01-10 | Spares, FOC | LUPIN LTD | BHIVANDI | CCLU1036859 | SITE | FOC | CARRIER-THINLINE | 2025-01-29 15:59 | crm@crystalgroup.in | YES | JAN083 | YES |  |  | 2025-01-29 16:17 | crm@crystalgroup.in | YES | JAN083 | TECHNICIAN |  |  | SHUBHAM |  |  | 2025-02-07 17:31 | 2025-01-09 |  |  |  |  | CCLU1036859 |  |  |  | Carrier | +5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/12.5 bar | 12.1/12.0/12.1 amps | 410/411/410 | Not done | found condenser fan motor noise bearing | need to replace bearing or cfm motor | No | https://drive.google.com/open?id=1hMbDoRbMT4Xun2KHBWDOFzQEb2gCthDO, https://drive.google.com/open?id=1Vz9oOaOkLtKwxdFpIZdN8Nw6p3Xsy-uc |  |  | NA | No | No | Can be done on next PM | na | no | service@crystalgroup.in | REEFER
JAN010/25 | 2025-01-09 15:37 | crm@crystalgroup.in | DR REDDY CTO 06 | Tadikonda Kishore | 96767 55199 | NA | CXRU1033616 | PREVENTIVE MAINTENANCE | Ramiz | tadikondakishore@drreddys.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-01-09 16:10 | crm@crystalgroup.in | Dr Reddy Ct 06 | CXRU1033616 | 40 FT STD | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintenance | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN010 | DAikin | LXE10E147F2 | M001192 | K31508150460 | DECOS 3F 2557 / 1 | Used | JSGA622340481 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-01-09 16:16 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-13 12:33 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-09 16:17 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-20 18:33 | 2025-01-09 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | 3 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/180 psi | 9.8/9.9/9.8 | 414/415/414 | Short | PM Service | PM Service completed | No | https://drive.google.com/open?id=1exQcARdqZo34ScH-rhiifotGReyNWFTE, https://drive.google.com/open?id=1WcMX00Jw-iWFuN3c9VLWphuflnLCcPQf |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JAN011/25 | 2025-01-09 15:37 | crm@crystalgroup.in | Lupin Limited | Amit Sakpal | 9326179943 | System Operator | TRIU6681082 | MOTOR MAKING NOISE | SHUBHAM/RAMIZ | depotcwhmumbai@lupin.com | Bhiwandi | Running with issues |  |  |  | 2025-01-23 11:02 | crm@crystalgroup.in | Lupin Ltd | TRIU6681082 | 20 FT | Carrier | SERVICE-AT SITE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN011 | [7 empty] | SHUBHAM | Yes | MOTOR MAKING NOISE | 2025-01-23 11:04 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-23 11:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-23 11:11 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-23 12:28 | 2025-01-14 |  |  |  |  | TRIU6681082 |  |  |  | Carrier | -5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0/14 | 2010-10-10 | 410/410/415 | Not done | Condensor FAN motor heavy noise , condensor coil heavy dirty | Reefer unit running in good condition | No | https://drive.google.com/open?id=1ua8541cMfQccGOa9mXD_KLKUkoA5YiCg |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JAN012/25 | 2025-01-10 12:44 | crm@crystalgroup.in | Zepto | Vikas Shidore |  | Operation executive | TITU9928040 | Leakage issue | Ninad | vikas.shidore@zeptonow.com | Pune | Running with issues |  |  |  | 2025-01-10 13:10 | operation@crystalgroup.in | Zepto | TITU9928040 | 40-REEFER | THERMOKING MP4000 | REPAIR | LEASE | FOC | LEAKAGE FOUND NEAR COMRESSOR | N2 TEST & BRAZING NEED TO BE DONE | SILVER BRAZING ROD, NITROGEN ,OXYGEN, R404a, VACUUM PUMP,BRAZING SET | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN012 | Thermoking MP-4000 | MP 4000 |  |  |  | Used |  | RAMIZ & SHUBHAM | Yes | Leakage issue | 2025-01-10 16:07 | operation@crystalgroup.in | YES | JAN084 | 2025-01-10 | Consumables, Spares, FOC | Zepto | ZEPTO | TITU9928040 | SITE | FOC | TK-MP4000 | 2025-01-10 16:08 | operation@crystalgroup.in | YES | JAN084 | YES |  |  | 2025-01-10 16:24 | operation@crystalgroup.in | YES | JAN084 | TECHNICIAN |  |  | RAMIZ & SHUBHAM |  |  | 2025-01-20 18:07 | 2025-01-19 |  |  |  |  | TITU9928040 |  |  |  | Thermo king | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8BAR/19BAR | 9.9/9.8/9.9 | 412/413/412 | Short | EVP COIL FOUND LEAKED | REPLACED EVP COIL | No | https://drive.google.com/open?id=1sT3-Ok3j3T48Ek1vflECIzKKBlEPadpC |  |  | NA | No | No | Can be done on next PM | NA | NA | mum.depot@crystalgroup.in | REEFER
JAN013/25 | 2025-01-13 10:10 | crm@crystalgroup.in | Swadesh Milk | V.Singh | 7459091115 | GM-Plant | GESU9290991 | Controller issue | Rahul | v.nsingh@hotmail.com | Lucknow | Running with issues |  |  |  | 2025-01-13 10:25 | service@crystalgroup.in | Swadesh milk products pvt ltd | GESU9290991 | 40 ft | carrier thine line | SERVICE-ON CALL | SALE | CHARGEABLE | compressor contactor burnt & controller defective ml3 | replaced compressor contactor & found the controller not responding | yes | Yes | due to compressor contactor coil burnt controller got defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN013 | Carrier | Thineline |  |  |  | Used |  | SHAHBUDDIN | Yes | Controller issue | 2025-01-22 17:36 | operation@crystalgroup.in | YES | JAN093 | 2025-01-22 | Spares, Paid | Swadesh milk products pvt ltd | LUCKNOW | GESU9290991 | SITE | PAID | CARRIER-THINLINE
JAN014/25 | 2025-01-14 13:08 | crm@crystalgroup.in | Crystal | NA | NA | NA | CICU1442256 | REPAIRS & REPLACEMENT | Sushma | NA | JNPT | Running with issues |  |  |  | 2025-01-20 17:18 | service@crystalgroup.in | Crystal Yard | CICU1442256 | 40" | Thermo king MP 4000 | MACHINE INSPECTION | STOCK | FOC | 3 Nos Display Blur ,Power Plug Missing ,Logo sticker damaged ,Display door damaged | Need to replace Display assembly ,Power Plug Assembly and display door assembly | Display TK 4000 3 Nos ,Power Plug TK 4000 2 Nos ,Display Door TK 4000 1 Nos ,Logo Sticker TK 4000 1 Nos | Yes | Door Damaged Due to misused , Display issue need to study | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN014 | Thermoking | EOG5003933 | EOG5003933 | 220916, 3.29.00 |  | brand New |  | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-01-22 18:23 | operation@crystalgroup.in | YES | JAN094 | 2025-01-22 | Spares | CRYSTAL YARD | JNPT | CICU1442256 | DEPOT | FOC | TK-MP4000
JAN015/25 | 2025-01-14 17:08 | operation@crystalgroup.in | RELIANCE | PRAMOD RANE | 8865021446 | RELIANCE FM | CXRU1040322 | Electric current flowing issue | PUSHPA | Kuldeep18.Yadav@qwik.co.in | Hapur | Running with issues |  |  |  | 2025-01-27 17:12 | crm@crystalgroup.in | RELIANCE | CXRU1040322 | 40FT | Daikin | SERVICE-ON CALL | LEASE | FOC | Electric current flowing issue | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN015 | [7 empty] | THIRD PARTY LOCAL | Yes | Electric current flowing issue | 2025-01-27 17:20 | operation@crystalgroup.in | YES | JAN099 | 2025-01-18 | FOC | RELIANCE | HAPUR | CXRU1040322 | SITE | FOC | DAIKIN | 2025-01-27 17:47 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-27 17:47 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-21 15:10 | 2025-01-18 |  |  |  |  | CXRU1040322 |  |  |  | Daikin | -18.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 150Kpa 1400Kpa | 9.1A 8.9A 9.3A | 402V 397V 399av | Not done | We hv attand this unit and found container give electric shock to due to netrul line loose | We hv fix netrul wire properly now container not give any sock and working fine condition | No | https://drive.google.com/open?id=1HiZnAVmIm2MF4Ib2W-Pg_zaBOLkZHunm, https://drive.google.com/open?id=1M5HyUFaor8Cwx9URChK5ZYyYKu4YkULH |  |  | N/a | No | No | Can be done on next PM | N/a | N/a | viru0068@gmail.com | REEFER
JAN016/25 | 2025-01-15 18:17 | operation@crystalgroup.in | Crystal | KSHIROD | NA | NA | CRIU2151790 | TANK CONTAINER REPAIR | NINAD | NA | JNPT | Running with issues |  |  |  | 2025-01-15 18:18 | operation@crystalgroup.in | CRYSTAL YARD | CRIU2151790 | 20FT ISO TANK | NA | REPAIR | STOCK | FOC | TANK PATCH WORK | 3RD PART WORK | NA | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN016 | [7 empty] | MASSK | No | TANK CONTAINER REPAIR | 2025-01-15 18:23 | operation@crystalgroup.in | YES | JAN088 | 2024-01-15 | Consumables, FOC | CRYSTAL YARD | JNPT | CRIU2151790 | DEPOT | FOC | NA | 2025-02-01 14:48 | operation@crystalgroup.in | YES | JAN088 | YES |  |  | 2025-02-01 19:13 | operation@crystalgroup.in | YES | JAN088 | FABRICATION WORK | [5 empty] | 2025-02-13 14:58 | [54 empty] | service@crystalgroup.in | DRY/Others
JAN017/25 | 2025-01-17 18:21 | crm@crystalgroup.in | Reliance Wagholi | Mangesh Vannere | 7020374749 | NA | CICU1442240 | PREVENTIVE MAINTENANCE | Shahbuddin | Mangesh.Vannere@ril.com | Pune | Preventive Maintenance |  |  |  | 2025-01-20 14:51 | service@crystalgroup.in | Reliance Wagholi | CICU1442240 | 10'' | Thermo King MP 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | PM Service | PM Service Done |  | No | PM Service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN017 | Thermoking | MP-4000 |  |  |  | Brand New |  | SHAHBUDDIN | No | PREVENTIVE MAINTENANCE | 2025-01-20 14:56 | mum.depot@crystalgroup.in | NO | [9 empty] | 2025-02-01 14:49 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 19:13 | operation@crystalgroup.in | NO | [7 empty] | 2025-02-04 10:29 | 2025-01-17 |  |  |  |  | CICU1442240 |  |  |  | Thermo king | -40*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8 & 19 | 9.9/9.9/9.8 | 416/416/415 | Short | PM service | Unit working well, internal liquid need to be replaced | Yes | https://drive.google.com/open?id=1qwh4iliMQiBSQ2XrDwnlzJCk3b4jV2Hp, https://drive.google.com/open?id=1TDSd0WvNVirVPF2q9bgzz8irzNR13R3J |  |  | TRIP066 | No | Yes | Can be done on next PM | NA | Internal Iiquid | crm@crystalgroup.in | REEFER
JAN018/25 | 2025-01-20 16:27 | crm@crystalgroup.in | Shah TC | Jitendra Sharma | 9711734411 | Sr. Manager – Operations & Logistics | CXRU1186451 | CONTAINER TEMPRATURE ISSUE - Error : Alarm 101 | Sushma | jitenderk@shahtc.com | Ghansoli, Navi Mumbai | Running with issues |  |  |  | 2025-01-20 17:28 | service@crystalgroup.in | Shah TC | CXRU1186451 | 40" | Daikin | SERVICE-ON CALL | LEASE | FOC | Unit tripping off frequently with Alarm E101 | Temporarily reset | Daikin TXV coil old Model 1 Nos , Silicon 1 Nos | Yes | Suspected TXV coil | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN018 | Daikin | LXE10E136F2 | M002046 | K12102057718 | DECOS 3F 2557 / 1 | Used | JSGA622180066 | Rajkumar | Yes | CONTAINER TEMPRATURE ISSUE - Error : Alarm 101 | 2025-01-22 12:04 | operation@crystalgroup.in | YES | JAN089 | 2025-01-22 | Spares, Paid | Shah TC | GHANSOLI | CXRU1186451 | SITE | PAID | DAIKIN | 2025-02-10 14:42 | operation@crystalgroup.in | YES | JAN089 | YES | https://drive.google.com/open?id=1_SB8CrotgkCWkbq_H0GE0JVqkzFLZ5Ca |  | 2025-02-12 16:30 | [9 empty] | 2025-02-13 21:46
JAN019/25 | 2025-01-21 17:32 | crm@crystalgroup.in | Reliance Hapur | Pramod Rana | 8865021446 | RELIANCE FM | CXRU1043912 | ALARM CODE VISIBLE, Safety alarm issue | Sahil | Kuldeep18.Yadav@qwik.co.in | Hapur | Running with issues |  |  |  | 2025-01-21 18:15 | service@crystalgroup.in | Reliance Hapur | CXRU1043912 | 40' | Daikin | SERVICE-ON CALL | LEASE | FOC | Customer required Mantrap and Light | Na | Mantrap ,Light | Yes | New Requirement | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN019 | DAikin | LXE10E-147F2 | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | JSGA623040331 | RAMIZ | Yes | ALARM CODE VISIBLE, Safety alarm issue | 2025-02-10 14:44 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-10 14:44 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-10 14:45 | operation@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN020/25 | 2025-01-22 10:42 | crm@crystalgroup.in | Reliance Bhopal | Ram Babu | 7869533375 | NA | MYRU4515188 | COMPRESSOR MAKING NOISE | Pushpa | NA | Bhopal | Running with issues |  |  |  | 2025-01-22 11:05 | service@crystalgroup.in | Reliance Bhopal | MYRU4515188 | 40' | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Noisy and HPT pressure Low | Need to Inspect Compressor ,Expansion Valve, ISV and ESV valve ,Liquid Valve,N2 Test, Vacuum ,Brizing Rod,R134A | Compressor Expansion Valve ISV and ESV Valve Liquated Valve Brazing Rod R 134A | Yes | Due to compressor leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN020 | Daikin | Daikin |  |  |  | Used |  | THIRD PARTY LOCAL | Yes | COMPRESSOR MAKING NOISE | 2025-01-22 13:02 | operation@crystalgroup.in | YES | JAN090 | 2025-01-22 | Consumables, Spares, FOC | Reliance | BHOPAL | MYRU4515188 | SITE | FOC | DAIKIN | 2025-02-01 15:05 | operation@crystalgroup.in | YES | JAN090 | YES |  |  | 2025-02-01 16:42 | crm@crystalgroup.in | YES | JAN090 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-01-31 19:27 | 2025-01-31 |  |  |  |  | MYRU4515188 |  |  |  | Daikin | -22.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 122KPA 1600KPA | 7.4A 7.0A 7.1A | 395V 397V 399V | Not done | We hv found compressor take high amps due to faulty | We have replaced compressor N2 test Vacvum And R134-a refill 5.2kg | Yes | https://drive.google.com/open?id=13osQgAGZbNJOqg2l23vIZeu41WvtVjhb, https://drive.google.com/open?id=1saQ0synV1HMdFsCDGOp8umOdZYQNXLD1, https://drive.google.com/open?id=16RPzXYXFucY9mm06QtgmWOSIfT0PXF3z, https://drive.google.com/open?id=1AuG8wJxr4zFl163DcU0xmD7KYqCHxDgY |  |  | TRIP NO 070 | Yes | No | Can be done on next PM | Liquid valve miner leakage from brizing | Liquid valve Isv valve Esv valve Expension valve Brizing set N2 Vacvum pump Brizing rod 4nos R-134a 5.5kg | viru0068@gmail.com | REEFER
JAN021/25 | 2025-01-22 11:12 | crm@crystalgroup.in | Reliance Kamaspura | Veer Singh | 9813816264 | Supervisor | TRIU6618391 | Alarm 26 | Pushpa | deepak91.singh@ril,com | Kamaspura, Haryana | Running with issues |  |  |  | 2025-01-22 15:29 | service@crystalgroup.in | Reliance Kamaspura | TRIU6618391 | 20' | Carrier Tinline | SERVICE-ON CALL | LEASE | FOC | ,Container showing Alarm AASA,DA70 ,AA56 ,AA26 | Need to Replace Supply and Return Sensor ,Ambient Sensor | Supply Sensor 2 Nos Return Sensor 2 Nos Ambient Sensor Spare 1 Nos | Yes | Return and Supply Sensor Failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN021 | Carrier - Thinline | Thinline |  |  |  | Used |  | VIRENDRA | Yes | Alarm 26 | 2025-01-22 18:40 | operation@crystalgroup.in | YES | JAN095 | 2025-01-22 | Spares, FOC | Reliance Kamaspura | KAMASPUR | TRIU6618391 | SITE | FOC | CARRIER-THINLINE | 2025-02-01 15:07 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 19:14 | operation@crystalgroup.in | NO | [7 empty] | 2025-02-07 17:43 | 2025-01-22 |  |  |  |  | TRIU6618391 |  |  |  | Carrier | - 18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8 /12.7 bar | 12.2/12.1/12.2 amps | 411/410/411 | Not done | found supply & return & ambient sensor defective | need to replaced all temperature sensor | Yes | https://drive.google.com/open?id=1cD2sirN6kVqpq_l-2ctFcb_97PMKU39m, https://drive.google.com/open?id=192dGq9ztN9j2uG88ZULArFF9ntesxzY6 |  |  | na | Yes | Yes | Can be done on next PM | all those sensor need to replead | supply sensor 2 nos , return sensor 2 nos, ambient sensor 1 nos | service@crystalgroup.in | REEFER
JAN022/25 | 2025-01-22 12:48 | crm@crystalgroup.in | Shah TC | Jitendra Sharma | 9711734411 | Sr. Manager – Operations & Logistics | CXRU11864512 | PREVENTIVE MAINTENANCE | Sahil | jitenderk@shahtc.com | Panvel | Preventive Maintenance |  |  |  | 2025-01-23 10:30 | crm@crystalgroup.in | Shah TC | CXRU11864512 | 40 FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN022 | [7 empty] | Rajkumar | Yes | PREVENTIVE MAINTENANCE | 2025-01-23 11:04 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-23 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-23 11:09 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-23 11:30 | 2025-01-21 |  |  |  |  | CXRU11864512 |  |  |  | Daikin | + 5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 255 & 967 | 10.8/10.8/9.9 | 216/215/216 | Not done | Condensor coil heavy dirty | Container running in good condition | No | https://drive.google.com/open?id=1x6xMM5ix0F3_MGrUQ98tFdUlQ1N_Ultu |  |  | TRIP067 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JAN023/25 | 2025-01-22 12:55 | crm@crystalgroup.in | Shah TC | Jitendra Sharma | 9711734411 | Sr. Manager – Operations & Logistics | CAIU5404270 | PREVENTIVE MAINTENANCE | Sahil | jitenderk@shahtc.com | Panvel | Preventive Maintenance |  |  |  | 2025-01-23 10:35 | crm@crystalgroup.in | Shah TC | CAIU5404270 | 40 FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN023 | DAikin |  |  |  |  | Refurbished |  | Rajkumar | Yes | PREVENTIVE MAINTENANCE | 2025-01-23 11:04 | crm@crystalgroup.in | NO | [9 empty] | 2025-01-23 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-01-23 11:09 | crm@crystalgroup.in | NO | [7 empty] | 2025-01-23 11:23 | 2025-01-21 |  |  |  |  | CAIU5404270 |  |  |  | Daikin | +5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay |  | Okay | Done | Clean |  | 10 & 996 |  | 215/215/214 | Not done | Condensor Coil heavy dirty | Container running in good condition | No | https://drive.google.com/open?id=13mq4tw1sG7bSuZDhNdsGNI6AHk3fOGmH |  |  | TRIP067 | No | No | Urgent | NA | NA | crm@crystalgroup.in | REEFER
JAN024/25 | 2025-01-22 16:23 | operation@crystalgroup.in | Crystal | KSHIROD | . | . | CRLU3181686 | REPAIRS & REPLACEMENT | NINAD | . | JNPT | Running with issues |  |  |  | 2025-01-22 16:25 | operation@crystalgroup.in | CRYSTAL | CRLU3181686 | 20-REEFER | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | Fabrication of Internal Baffle Plate | MASSK VENDOR WORK |  | 3RD PARTY VENDOR | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN024 | Daikin | Daikin |  |  |  | Used |  | MASSK | No | REPAIRS & REPLACEMENT | 2025-01-22 16:29 | operation@crystalgroup.in | YES | JAN092 | 2025-01-22 | FOC | CRYSTAL | JNPT | CRLU3181686 | DEPOT | FOC | NA | 2025-02-01 15:08 | operation@crystalgroup.in | YES | JAN092 | YES |  |  | 2025-02-01 19:15 | operation@crystalgroup.in | YES | JAN092 | FABRICATION WORK | [5 empty] | 2025-02-10 13:08 | 2025-02-08 |  |  |  |  | CRLU3181686 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | OK | OK | OK | Not done | BUFFEL PLATE MISSING | replaced with good one | No | https://drive.google.com/open?id=1dv__6QHT_EGgrSGfAWWhPUKrOVSGNo8y |  |  | NA | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
JAN025/25 | 2025-01-22 18:12 | crm@crystalgroup.in | Siemens | NA | NA | NA | TRIU6617646 | Compressor Leakage issue | Ninad | NA |  | Running with issues |  |  |  | 2025-01-22 18:24 | service@crystalgroup.in | Siemens | TRIU6617646 | 20' | Carrier | SERVICE-AT SITE | SALE | AMC | condenser coil leakage to brazing | Need to carry out Brazing of condenser coil, ,N2 test ,Need to replace EVP motor | Brazing Set 1 Nos LPG 1 Nos O2 1 Nos N2 1 Nos R134A 5 KG EVP Motor 1 Nos Brazing Rod 2 Nos Vacuum Pump 1 Nos | Yes | Malfunctioning | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN025 | Carrier - Thinline | Thinline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | SHAHBUDDIN | Yes | Compressor Leakage issue | 2025-01-23 19:08 | operation@crystalgroup.in | YES | JAN097 | 2025-01-23 | Consumables, Spares, Paid | Siemens | AURANGABAD | TRIU6617646 | SITE | PAID | CARRIER-THINLINE | 2025-02-26 12:55 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-26 12:55 | service@crystalgroup.in | NO
JAN026/25 | 2025-01-24 13:00 | crm@crystalgroup.in | Crystal | NA | NA | NA | AKA0004025 | Battery required in Gen. Set | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-01-29 09:37 | service@crystalgroup.in | Crystal Yard | AKA0004025 | Genset Thermoking | Thermoking | SERVICE-AT SITE | STOCK | FOC | Battery Not Available | Need to Purchase new Battery 12V 180 AH | Battery 12V 180 AH | Yes | Battery Not Available | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN026 | [7 empty] | SHAHBUDDIN | No | Battery required in Gen. Set | 2025-03-10 11:38 | tender@crystalgroup.in | YES | MAR007 | 2025-03-10 | Spares | CRYSTAL YARD | JNPT | AKA0004025 | DEPOT | FOC | TK-MP3000 | 2025-01-31 18:18 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 10:51 | mum.depot@crystalgroup.in | NO
JAN027/25 | 2025-01-25 12:40 | service@crystalgroup.in | Dr Reddy CTO5 | Narendra | 7036305829 | SR ENGINEER | CXRU1045896 | Container getting Tripped | Pushpa | operation@crystalgroup.in | Hyderabad | Running with issues |  |  |  | 2025-01-25 12:48 | service@crystalgroup.in | Dr Reddy CTO 5 | CXRU1045896 | 40' | Daikin | SERVICE-AT SITE | LEASE | FOC | on Operation of compressor contactor ,electricity is getting tripped due to faulty compressor | Need to replace Compressor Compressor contactor (suspected) PCC1 and PCC2 contactor (suspected) N2 Test Vacuum | compressor 01 Nos compressor contactor 01 Nos PCC1 and PCC2 01 Nos Gauge set 0 Nos R134A 5KG | Yes | Compressor and contactor Faulty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN027 | DAikin | LXE10E147F2 | M001282 | K31411141398 | DECOS 3F 2606 / 1 | used | JSGA623040309 | VIRENDRA | Yes | Container getting Tripped | 2025-01-27 10:36 | operation@crystalgroup.in | YES | JAN098 | 2025-01-27 | Spares, FOC | Dr Reddy CTO 5 | HYDERABAD | CXRU1045896 | SITE | FOC | DAIKIN | 2025-02-01 15:12 | operation@crystalgroup.in | YES | JAN098 | YES | https://drive.google.com/open?id=1iaFZ4YkYVFTda1ZGTrrrbeF4s4KOeHwd |  | 2025-02-01 19:17 | operation@crystalgroup.in | YES | JAN098 | COURIER | VH-SP/6351 | GLOBAL PARCEL SERVICES |  |  |  | 2025-02-10 21:54 | 2025-02-10 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | + 4 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/200 | 10.2/10.3/10.2 | 408/409/408 | Short | Unit not working, found compressor terminalsblock burnt out & compressor got damaged same place and Gas leakage.found controller Fuse blown , wiring burnt. | Pulled out burnt compressor and replaced good one, leak test , used Nitrogen, replaced filter drier, vacum system, and Gas charge 4.6 kg R134a , unit run and kept for under observation.. | No | https://drive.google.com/open?id=16y4dVUyByaSf10oVaZbCZHTQUiW8RBSI |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN028/25 | 2025-01-27 12:08 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | GESU9454776 | Capacitor problem in FAN | Ninad | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues |  |  |  | 2025-01-27 15:48 | service@crystalgroup.in | Laurus unit 2 | GESU9454776 | 40' | Carrier | SERVICE-AT SITE | LEASE | FOC | Found Alarm code AA25 condenser motor capacitor defective | Need to Replace Motor Capacitor | Condenser motor Capacitor 20mfd/370 V | Yes | condenser motor Capacitor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN028 | Carrier | Thineline |  |  |  | Used |  | THIRD PARTY LOCAL | Yes | Capacitor problem in FAN | 2025-01-31 17:57 | operation@crystalgroup.in | YES | JAN102 | 2025-01-31 | Spares, FOC | LAURUS SYNTHESIS UNIT 2 | Vishakapatnam | GESU9454776 | SITE | FOC | CARRIER-THINLINE | 2025-01-31 18:16 | operation@crystalgroup.in | YES | JAN102 | YES | https://drive.google.com/open?id=13upzsarKLu7IVxPOQS0BOCJaFhbNMb71 |  | 2025-02-01 10:53 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN029/25 | 2025-01-27 12:11 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site In charge | PRGU4958724 | Filter issue | Ninad | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues |  |  |  | 2025-01-27 12:51 | service@crystalgroup.in | Laurus unit 2 | PRGU4958724 | 40' | Carrier Thinline | SERVICE-AT SITE | LEASE | FOC | Alarm AA19.AA15 | Need to Replace Filter Dryer | Filter Dryer | Yes | Filter Dryer Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN029 | Carrier - Thinline |  |  |  |  | Used |  | THIRD PARTY LOCAL | Yes | Filter issue | 2025-01-31 18:25 | operation@crystalgroup.in | YES | JAN103 | 2025-01-31 | Spares, FOC | LAURUS SYNTHESIS UNIT 2 | VISAKHAPATNAM | PRGU4958724 | SITE | FOC | CARRIER-THINLINE | 2025-01-31 18:35 | operation@crystalgroup.in | YES | JAN103 | YES | https://drive.google.com/open?id=1xvfv3O9DmpCPqCRCaSgRx8_qG3s-64th |  | 2025-02-01 11:02 | mum.depot@crystalgroup.in | YES | JAN103 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-02-11 18:44 | 2025-02-11 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | +2.C | Clean | Clean |  | Noisy | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /16 | 10.1/10.2/10.1 | 405/407/408 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1KZW-tmLMdOP3Aum07xi0TDa-DbLGBKL-, https://drive.google.com/open?id=1rsagxvEHd8ns5gnBbW1jIkGa5eeMMkNO |  |  | TRIP072 | Yes | Yes | Can be done on next PM | Na | Fan *1 Gas Kit *1 | crm@crystalgroup.in | REEFER
JAN030/25 | 2025-01-27 17:31 | crm@crystalgroup.in | Dr. Reddy's Labs -Biologics | Suresh Kasam | 99081 25456 | Plant Engineer | TITU9930074 | Anti Room temp. issue | Virendra | sureshkasam@drredddys.com | Hyderabad | Running with issues |  |  |  | 2025-01-28 11:26 | service@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40' | Blue Star | SERVICE-AT SITE | LEASE | FOC | Low cooling Issue | Need to Refill Gas | Required Gas R22 1kg | Yes | Gas is Low | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN030 | Thermoking | MP-4000 | 05G7619AG | E001051602 |  |  | JSGA622180047 ¦ JSGA622180052 | THIRD PARTY LOCAL | Yes | Anti Room temp. issue | 2025-02-05 14:23 | operation@crystalgroup.in | YES | FEB002 | 2025-02-05 | Consumables, FOC | Dr. Reddy's Labs -Biologics | HYDERABAD | TITU9930074 | SITE | FOC | TK-MP4000 | 2025-02-11 11:45 | operation@crystalgroup.in | YES | FEB002 | YES | [12 empty] | 2025-02-20 10:57 | 2025-02-14 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20 bar x 2 | 9.9/9.8/9.9 | 410/411/412 | Short | Found TK- MP -4000 DISPLAY FADED NOTCREADABLE | Need to replaced Display | Yes | https://drive.google.com/open?id=1lSDXfOsgtTWsvKizSd02OvG1YmPRovDc, https://drive.google.com/open?id=1x4v3ZgmFBPN49xcmPzgR5DBW5LKoUhAk |  |  | 71 | Yes | No | Can be done on next PM | MP 4000 DISPALY NEED TO REPLACED( WAITING FOR SPARE) | TK MP 4000 DISPLAY | technician@crystalgroup.in | REEFER
JAN031/25 | 2025-01-28 11:14 | operation@crystalgroup.in | Mochan Food Processors Pvt Ltd | DEELIP AGARWAL | 9836800040 | commercial head | GRMU3707525 | 1 unit working fine other 2 are faulty | NINAD | agarwal.dilip1@gmail.com | Kolkata | Running with issues |  |  |  | 2025-05-06 16:53 | crm@crystalgroup.in | MOCHAN food processors private limited | GRMU3707525 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN031%2F25 | NA | NA | NA | NA | NA | NA | NA | RAMIZ | No | 1 unit working fine other 2 are faulty | 2025-05-07 10:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-07 10:41 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-10 12:59 | crm@crystalgroup.in | NO
JAN032/25 | 2025-01-28 11:30 | operation@crystalgroup.in | RELIANCE | BIPLAB SARKAR |  | FM | CXRU1042578 | OIL LEAKAGE FOUND ON PIPE | NINAD | BIPLAB.KR.2218@GMAIL.COM | SILIGURI | Running with issues |  |  |  | 2025-02-06 14:44 | service@crystalgroup.in | REALIANCE | CXRU1042578 | 40 reefer | daikin | SERVICE-AT SITE | LEASE | FOC | found oil satin from DPR NRV | need to charge 4 can R134a & (1.8 kgs) | Gas R134a 1.8 kgs | Yes | leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN032 | main unit | daikin decose iiif | OK | OK | OK | Used | OK | THIRD PARTY LOCAL | Yes | OIL LEAKAGE FOUND ON PIPE | 2025-02-07 10:29 | operation@crystalgroup.in | YES | FEB003 | 2025-02-07 | Consumables, FOC | REALIANCE | SILIGURI | CXRU1042578 | SITE | FOC | DAIKIN | 2025-02-12 16:29 | operation@crystalgroup.in | YES | FEB003 | YES | https://drive.google.com/open?id=1ob-OD2T5XtXUIQuYWNT3WDZbOW_vWe-T |  | 2025-02-12 16:30 | operation@crystalgroup.in | YES | FEB003 | ARRENGING AT SITE | [5 empty] | 2025-02-12 10:50 | 2025-02-11 |  |  |  |  | CXRU1042578 |  |  |  | Daikin | +2C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/13.5B | 9.8/9.7/9.8 | 411/410/411 | Not done | found oil satin from DPR NRV/leakage | repaired the NRV valve & chare R134a 1.5 KGS | No | https://drive.google.com/open?id=1KsF_gBodfI0Am_4CbA5sUhPxgcAW3lfr, https://drive.google.com/open?id=1aXwlxsnPfiu9EgtGXccYryd264rE5kMP |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JAN033/25 | 2025-01-28 13:01 | mum.depot@crystalgroup.in | Aspiro pharma ltd | T. RAMESH REDDY | 9959404803 | TECHNICAL MANAGER | CGMU2991560 | MOTOR MAKING NOISE, EVP MOTOR AND ML3 CONTROLLER CARRIER THINLINE | SHAHBUDIN | NA | Hyderabad | Complete Breakdown |  |  |  | 2025-01-28 13:04 | service@crystalgroup.in | ASPIRO PHARMA | CGMU2991560 | 20' dual Unit | Carrier | SERVICE-AT SITE | LEASE | FOC | Evaporator Motor Over heat and Noisy and ML3 Controller | Need to Replace EVP Motor single phase(Carrier) | EVP Motor single phase(Carrier) 1 Nos Controller Ml3 Thinline | Yes | EVP motor Fail | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN033 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHAHBUDDIN | Yes | MOTOR MAKING NOISE, EVP MOTOR AND ML3 CONTROLLER CARRIER THINLINE | 2025-01-30 11:20 | operation@crystalgroup.in | YES | JAN101 | 2025-01-30 | Spares, FOC | ASPIRO PHARMA | HYDERABAD | CGMU2991560 | SITE | FOC | CARRIER-THINLINE | 2025-02-11 11:43 | operation@crystalgroup.in | YES | JAN101 | YES |  |  | 2025-02-28 12:52 | service@crystalgroup.in | YES | JAN101 | Gati | [5 empty] | 2025-03-02 00:09 | 2025-03-01 |  |  |  |  | CGMU2991560 |  |  |  | Carrier | +4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1/12.3 bar | 12.3/12.4/12.3 | 395/396/395 | Not done | unit one condenser coil dirty & evaporator fan motor R side defective | clean condenser coil with fresh & replace evaporator fan motor with good one | No | https://drive.google.com/open?id=15QTxNuJiITeKGY_KRlZ837Vaniev94SP, https://drive.google.com/open?id=1dddtwRByjNoCTjAYnQzO9Jd0IMNiGDdy |  |  | 76 | No | No | Can be done on next PM | na | for 2 nd machine controller | service@crystalgroup.in | REEFER
JAN034/25 | 2025-01-29 17:37 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | M.Subba Reddy | 8106009300 | Warehouse Manager | BMOU9787239 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Sushma | Subbareddy.Mandadi@apitoria.com> | Srikakulam | Running with issues |  |  |  | 2025-01-29 18:23 | mum.depot@crystalgroup.in | Apitoria Pharma | BMOU9787239 | 40FT | DAIKIN | SERVICE-AT SITE | LEASE | FOC | TEMPERATURE NOT REACHED AT SET POINT | NEED TO CHECK LEAKAGE AND ADD GAS.NEED TO CLEAN CONDENSER COIL. | NA |  | SUSPECTED GAS LEAK | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN034 | Daikin |  |  |  |  | Refurbished |  | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-02-01 14:54 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-01 14:55 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-01 14:56 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-01 15:33 | 2025-01-30 |  |  |  |  | BMOU9787239 |  |  |  | Daikin | 22*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | Condensor coil dirty | Condensor running in good condition, after washing with water | No | https://drive.google.com/open?id=1HMghUwlbm1EgATQUEWWxGCjDFIkdi4dY, https://drive.google.com/open?id=18dZYzgTUnHuAMX4ZRHk4xLeMcLpB3QLW |  |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JAN035/25 | 2025-01-30 16:17 | crm@crystalgroup.in | Laurus Synthesis Pvt Ltd Unit2 | Vinay Kumar | 9849316414 | Associate | TRIU6680994 | Alarm 52 | Ninad | lsv2.electrical@laurussynthesis.com | Vishakapatnam | Running with issues |  |  |  | 2025-02-06 12:18 | service@crystalgroup.in | Laurus Synthesis Pvt Ltd Unit2 | TRIU6680994 | 40 ft | carrier | SERVICE-AT SITE | LEASE | FOC | condenser fan motor capacitor defective | removed old capacitor & need to fix new one 15 uf | capacitor 15 UF (440 &50 to 60 HZ ,stating capacitor ) | Yes | getting old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN035 | man unit | thine line | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | Alarm 52 | 2025-02-07 12:46 | operation@crystalgroup.in | YES | FEB004 | 2025-02-07 | Consumables, FOC | LAURUS SYNTHESIS UNIT 2 | VISAKHAPATNAM | TRIU6680994 | SITE | FOC | CARRIER-THINLINE | 2025-02-07 12:47 | operation@crystalgroup.in | YES | FEB004 | YES |  |  | 2025-02-11 10:53 | mum.depot@crystalgroup.in | YES | FEB004 | TECHNICIAN |  |  | SHUBHAM |  |  | 2025-02-11 18:35 | 2025-02-10 |  |  |  |  | TRIU6680994 |  |  |  | Carrier | +3*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Rusty |  | 17.1 | 2011-11-11 | 410/411/410 | Not done | NA | NA | No | https://drive.google.com/open?id=1R15WwW1mio_qgGcWNQNFMxE8T6zEEpwP, https://drive.google.com/open?id=1LJNSjmsX61i9jzwYoVCWJ0W9jCx_EY29 |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JAN036/25 | 2025-01-31 10:53 | crm@crystalgroup.in | Reliance Bhopal | Ram Babu | 7869533375 | NA | CRLU6220410 | PREVENTIVE MAINTENANCE | Sahil | NA | Bhopal | Preventive Maintenance |  |  |  | 2025-01-31 14:21 | service@crystalgroup.in | Reliance Bhopal | CRLU6220410 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintenance | Technician to be arranged for Preventive Maintenance | NA | No | Preventive Maintainence | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN036 | Carrier - Thinline | Thinline |  |  |  | Refurbished | JSGA622170434 | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2025-01-31 18:47 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-31 18:49 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 11:03 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-31 19:39 | 2025-01-31 |  |  |  |  | CRLU6220410 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/a | 9.7A 9.3A 9.5A | 395V 392V 393V | Not done | We have found showing Alaram AL05 manual defrost switch failure | We have removed switch and repair and fix again | No | https://drive.google.com/open?id=1mBY92nYQEyo7_IadzYmljyNEJTE7vuEJ, https://drive.google.com/open?id=1zJ_Fg1B3seqNEtBHCqk9B5DuzI4JNZkT |  |  | TRIP NO 070 | No | No | Can be done on next PM | N/a | N/a | viru0068@gmail.com | REEFER
JAN037/25 | 2025-01-31 10:55 | crm@crystalgroup.in | Reliance Bhopal | Ram Babu | 7869533375 | NA | CICU3876544 | PREVENTIVE MAINTENANCE | Sahil | NA | Bhopal | Preventive Maintenance |  |  |  | 2025-01-31 14:24 | service@crystalgroup.in | Reliance Bhopal | CICU3876544 | 10FT | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | Preventive Maintainece | Schedule Engg Visit for M |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN037 | Thermoking | Magnum Plus | E0GM030963 | 0322GM030961 | ABC782900321510545 | Brand New |  | VIRENDRA | Yes | PREVENTIVE MAINTENANCE | 2025-01-31 18:47 | operation@crystalgroup.in | NO | [9 empty] | 2025-01-31 18:49 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-01 11:04 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-01-31 19:46 | 2025-01-31 |  |  |  |  | CICU3876544 |  |  |  | Thermo king | -40.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 18.6B | 7.0A 6.7A 6.9A | 409V 407V 405V | Not done | We have found container run in old software and condenser coil dirty | We have updated software and clean condenser coil with normal water | No | https://drive.google.com/open?id=1oeOO1TzAtNipMSw8DjBINgHIXprBWENQ, https://drive.google.com/open?id=1CammPHrM0B6A6QVrlXxaqCCqwtlML1ZN |  |  | TRIP NO 070 | No | No | Can be done on next PM | N/a | N/a | viru0068@gmail.com | REEFER
JAN038/25 | 2025-01-31 11:41 | crm@crystalgroup.in | Navin Fluorine | Ketan | 6357662623 | NA | CCLU1031878 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Ninad | NA | Dhej | Running with issues |  |  |  | 2025-02-06 12:30 | service@crystalgroup.in | Navin fluorine Dhej | CCLU1031878 | 20-REEFER | CARRIER THINELINE | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | CLEAN CONDENSER COIL WITH FRESH WATER | NA | No | CONDENSE COIL DIRTY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN038 | main unit | CARRIER THINELINE | NA | NA | NA | USED | NA | RAJESH | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-02-07 13:18 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-07 13:18 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:32 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-13 11:12 | 2025-01-31 |  |  |  |  | CCLU1031878 |  |  |  | Daikin | + | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3/9.8BAR | 8.8/8.8/8.7 | 404/405/405 | Not done | TEMPERATURE NO TACHIVE TO THE SET POINT | CONDENSER COIL DIRT | No | https://drive.google.com/open?id=1TP1_5YsKuXG-E2PfoezFCWldNI6FKdqi, https://drive.google.com/open?id=1A8SJLT4meg_NX1o-VCozxuF_27qECkXF |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JAN040/25 | 2025-01-31 17:54 | crm@crystalgroup.in | Aspiro pharma ltd | Gatturayudu | 9100980301 | NA | CAIU5422720 | PREVENTIVE MAINTENANCE | Ninad | RohanKumar.Y@aspiropharma.com | Karkapalta | Preventive Maintenance |  |  |  | 2025-02-03 12:34 | operation@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40-REEFER | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | FOC | REPAIR AND MAINTENANCE | - |  | No | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN040 | DAikin |  |  |  |  | Used | JSGA622340482 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-03 12:36 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-03 12:36 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-03 12:37 | operation@crystalgroup.in | NO | [7 empty] | 2025-02-02 22:06 | 2025-02-02 |  |  |  |  | CAIU5422720 |  |  |  | Daikin | + 4 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 5/200 | 9.9/9.8/9.9 | 400/398/399 | Short | Unit shut down due to contaminate refrigerant gas / with Al F802& Al E 107 | Release the contaminate refrigerant from system& replaced filter Drier , proper vacum system and New Gas charging to system. Need fixed low side suction valve cap asap. | Yes | https://drive.google.com/open?id=1o6EfHqJUt7CP0_nx2t2n02h8WsSeILFm, https://drive.google.com/open?id=1MRU46VpWnNuYzXjq7C7lAsbLZknio-W- |  |  | TRIP071 | No | No | Can be done on next PM | Need to fixed suction valve cap asap | EIS SENISR/ SUC. VALUE CAP | technician@crystalgroup.in | REEFER
JAN041/25 | 2025-01-31 18:02 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | +91 96527 25368 | On Duty Officer | CONT 1 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 10:48 | crm@crystalgroup.in | Divis Labs | CONT 1 | 40 FT | CARRIER-THINLINE | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN041 | [7 empty] | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:39 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 10:59 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:27 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-04 23:32 | 2025-02-04 |  |  |  |  | TDRU7152244 |  |  |  | Daikin | - 11 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/190 psig. | 9.9/9.8/9.8 | 410/411/412 | Short | Sale unit: break down due to compressor bottom. Base leak refrigerant gas | Work done: removed Defective leaking compressor,Fixed new one , compressor wiring rearrange and replaced filter drier, Nitrogen fill and leak test done , found no leak system.Gas /Refrigerant R134 a charge 5 kg. Again leak check and verified .system working is fine and handed over to duty Engineer | No | https://drive.google.com/open?id=1Izfu7uE7RMkoExgWqEmo5z5gc07YWZch, https://drive.google.com/open?id=1rxoyh6pfu2GvmJb_9RfB1beAG212-fE5 |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN042/25 | 2025-01-31 18:03 | crm@crystalgroup.in | Qwik Supply | Satish Battula | 91825 61332 | NA | CICU1799177 | PREVENTIVE MAINTENANCE | Ninad | Battula.Sateesh@ril.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 10:53 | crm@crystalgroup.in | Qwik Supply | CICU1799177 | 10FT | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN042 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 |  | BRand NEW | JSGA622180057 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:39 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:27 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN045/25 | 2025-01-31 18:28 | crm@crystalgroup.in | DSV Solutions Pvt Ltd | SAGAR | 9030909007 | NA | TITU8258978 | PREVENTIVE MAINTENANCE | Ninad | NA | Kompally | Preventive Maintenance |  |  |  | 2025-02-04 11:22 | crm@crystalgroup.in | DSV Solutions | TITU8258978 | 20FT | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN045 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 |  | Used |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:28 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-03 19:37 | 2025-02-03 |  |  |  |  | TITU8258978 |  |  |  | Thermo king | - 32 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace | https://drive.google.com/open?id=1-Jrt-0fzTAyGbBl7ila2ZGo0b6ze9nq7 | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20 bar | 9.8/9.9/9.9 | 405/406/404 | Short | Found unit Tk MP 4000 Display faded and key pad logo damaged & tear.( last visit also reported) | Need to replacedDisplay & key pad logo | Yes | https://drive.google.com/open?id=1q0Q_FmG8yAf18UtdcIGDgiuisW1D9C5q, https://drive.google.com/open?id=1Yw3Amgtiu_JzSMzOmXF3YI1M1DX9E-m9 |  |  | 71 | Yes | No | Can be done on next PM | As above | TK MP 4000 DISPLAY & TK KEY PAD LOGO | technician@crystalgroup.in | REEFER
JAN046/25 | 2025-01-31 18:30 | crm@crystalgroup.in | Softbox | Satish Kondapalli | 8977711235 | NA | GRMU3707470 | PREVENTIVE MAINTENANCE | Ninad | Skondapalli@csafeglobal.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 11:49 | crm@crystalgroup.in | Softbox | GRMU3707470 | 20FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN046 | Daikin |  |  |  |  | used |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:28 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN047/25 | 2025-01-31 18:31 | crm@crystalgroup.in | Softbox | Satish Kondapalli | 8977711235 | NA | TITU8257288 | PREVENTIVE MAINTENANCE | NA | Skondapalli@csafeglobal.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 11:51 | crm@crystalgroup.in | Softbox | TITU8257288 | 20FT | Thermoking MP4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN047 | Thermoking | Thermoking MP4000 |  |  |  | Used |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:29 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN049/25 | 2025-01-31 18:34 | crm@crystalgroup.in | DHL Supply Chain pvt Ltd | Ritesh Ingle ¦ Yogindar Singh ¦ Niranjan Kanthe | 9703874353 ¦ 9460975040 ¦ 70830 26116 ¦ 9885755890 | NA | DFOU6120281 | PREVENTIVE MAINTENANCE | Ninad | yogindar.singh@dhl.com ¦ niranjan.kanthe@dhl.com ¦ nikhil.adicherla@dhl.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 11:53 | crm@crystalgroup.in | DHL Supply Chain | DFOU6120281 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN049 | Daikin | Daikin | M004351 | LXEOE136A |  | Used | JSGA623040277 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 10:46 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 10:47 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-03 19:10 | 2025-02-03 |  |  |  |  | DFOU6120281 |  |  |  | Daikin | + 2 c | Clean | Clean | https://drive.google.com/open?id=1A1rbUBzpqDNplJh1avHu-562qsAlK5eh | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1C3keOaAEbzmmNp1nBs4rN6tX4Dc49nAW | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2/170 PSIG | 9.9/9.8/9.8 | 390/389/390 | Short | Unit found Abnormal pressure in system, | Need to removed old gas & need to replaced filter drier with need proper vacum system and need to charge fresh new gas R 134a 5.2 kg | Yes | https://drive.google.com/open?id=1cWJjnvqhxHK-V9DMBzyTc0bvIDjcAyde, https://drive.google.com/open?id=1c2TTEyWLxhbIw51z3U2dgrIPBvOmbT2j |  |  | 71 | No | No | Can be done on next PM | As above | Gas 134a/ Filter Drier/ vacuum pump. And Inlet sensor and suction gas sensor. | technician@crystalgroup.in | REEFER
JAN050/25 | 2025-01-31 18:36 | crm@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | PCIU6016370 | PREVENTIVE MAINTENANCE | Ninad | NA | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 11:55 | crm@crystalgroup.in | Hetero Unit 3 | PCIU6016370 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN050 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:33 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 19:25 | 2025-02-13 |  |  |  |  | PCIU6016370 |  |  |  | Daikin | +6c | Clean | Clean | https://drive.google.com/open?id=1905IAiPA6tSQAQyzQSkhFPb7UyN0iYsh | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1u5x-hp4HWR_Vpyme0oOd25eYPYPawTy4 | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/180 PSIG | 9.9/9.8/9.8 | 409/409/408 | Short | PM COMPLITED& UNIT WORKING AS NORMAL , RETURN SENSOR AND SUPPLY SENSOR READING ABNORMMAL READING . | PM COMPLITED WITH WASH UNIT & CONDENSER COIL, CHECKED UNIT OPERATION , MAIN VOLTAGE, ALL SENSOR READING & PARAMETER , GAS LEVEL PRESSURE, INSIDE HOUSE KEEPINGIN GOOD POSITION, CHECKED ALL ELECTRAL PANL WIRING . CHECKED SENSOR & CALIBRATION FOUND RETURN & SUPPLY SENSOR READING ABNIRMAL, NEED TO REPLACED NEXT SERVICE PM.( NO SPARE AVILABLE PM TIME. | Yes | https://drive.google.com/open?id=1V1gVHJO-CagYtxYfv0BFHbuoKV9bncZl, https://drive.google.com/open?id=1nvRs19bNpIZ4ELQmypWLA4zK71pkKrfS |  |  | 71 | No | No | Can be done on next PM | AS ABOVE | DAIKIN EIS SENSOR & SUPPLY TEMP.SENSOR | technician@crystalgroup.in | REEFER
JAN051/25 | 2025-01-31 18:38 | crm@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | APRU5091041 | PREVENTIVE MAINTENANCE | Ninad | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:03 | crm@crystalgroup.in | Hetero Unit 3 | APRU5091041 | 40FT | Carrier-Primeline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN051 | Carrier-Primeline | Thinline | KSU60094860 | 541308SN |  | Used | JSGA623040287 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:33 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN052/25 | 2025-01-31 18:39 | crm@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | CXRU1026520 | PREVENTIVE MAINTENANCE | Ninad | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:12 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1026520 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN052 | Daikin | LXE10E147F2 | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:33 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN053/25 | 2025-01-31 18:42 | crm@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | CXRU1030427 | PREVENTIVE MAINTENANCE | Ninad | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:13 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1030427 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN053 | Daikin | LXE10E147F2 | M001451 | K31508150299 | DECOS 3F 2551 / 1 | Used | JSGA623040186 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:05 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN054/25 | 2025-01-31 18:44 | crm@crystalgroup.in | Qwik Supply | avinash | 9281026402 | NA | CICU2779920 | PREVENTIVE MAINTENANCE | Ninad | Battula.Sateesh@ril.com | Shamshabad | Preventive Maintenance |  |  |  | 2025-02-03 12:47 | operation@crystalgroup.in | Qwik Supply | CICU2779920 | 10-REEFER | THERMOKING | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN054 | Thermoking | Magnum Plus | E0GM030270 | ABC782800322010477 |  | BrandNew |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-03 12:49 | operation@crystalgroup.in | NO | [9 empty] | 2025-02-03 12:50 | operation@crystalgroup.in | NO |  |  |  |  | 2025-02-03 12:50 | operation@crystalgroup.in | NO | [7 empty] | 2025-02-01 20:02 | 2025-02-01 |  |  |  |  | CICU2779920 |  |  |  | Thermo king | - 30 c | Clean | Clean | https://drive.google.com/open?id=1H8vy9PjhIOdkG1jA2pQMXAJJPivwM_N6 | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1ZrpEiKN0MgGi6CbnRnjs0UTdCYNq1L6b | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/ 19 bar | 9.7/9.8/9.7 | 401/402/400 | Short | Found unit some time under voltage/ Internal home keeping not good need to clen once a month. | Need to send email to clints/ orally advise to duty person | No | https://drive.google.com/open?id=12TpneDHpQQFoYfHnC-0gCn2C4x-bqqPW , https://drive.google.com/open?id=18rLZ4-xWA-tSCw_oFoWhEzHA_J128ahB |  |  | TRIP071 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN056/25 | 2025-01-31 18:50 | crm@crystalgroup.in | Dr Reddy CTO5 | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | NA | GSOU6384240 | PREVENTIVE MAINTENANCE | Ninad | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  |  |  | 2025-02-04 12:20 | crm@crystalgroup.in | Dr Reddy CTO 5 | GSOU6384240 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN056 | Carrier | Carrier Thinline | SSB60749120 |  | ML-3 | used | JSGA622340472 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:42 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 21:57 | 2025-02-12 |  |  |  |  | GSOU6384240 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4/210 PSIG | 12.3/12.4/12.3 | 406/407/406 | Short | Unit malfunction call receivedas temp.not reac to set temp. And PM SERVICE balance after Instalation first Pm | Checked carrier thin line unit and found compressor sight glass for oil leaking with minor and due to this reason Freon Gas level down. Secured the oil sight glass and leak stop with adding Freon gas to system .( R134a- 1kg) PM service complited with checked unit operation , main voltage all motor Amp with all sensor reading and parameter, reset inactive Alam, clean unit and condenser coil with fresh normal water with pressure pump. Found internal house keeping is not good blocking air flow, ON duty person same time rectifie after guidelines. Unit observation and maintaining set temp. And handed over to duty person / Engineer.with Mr. Ashok appointed. Job complited...... | No | https://drive.google.com/open?id=1-knWYV7pdF-nP6w0uZIH7Ap7rFnsPwhe, https://drive.google.com/open?id=14MG8hNxwenlvJPfbIse3ywxHtHDqXtlG |  |  | 71 | No | No | Can be done on next PM | Need to add gas again next service pm apx. 1kg R134a | NA | technician@crystalgroup.in | REEFER
JAN057/25 | 2025-01-31 18:51 | crm@crystalgroup.in | Dr Reddy CTO5 | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | NA | GSOU6384153 | PREVENTIVE MAINTENANCE | Ninad | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  |  |  | 2025-02-04 12:25 | crm@crystalgroup.in | Dr Reddy CTO 5 | GSOU6384153 | 40FT | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN057 | Carrier | Carrier Thinline | SSB60750588 |  | ML-3 | used | JSGA623040187 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:42 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 00:15 | 2025-02-11 |  |  |  |  | GSOU6384153 |  |  |  | Carrier | +20c | Clean | Clean | https://drive.google.com/open?id=1eYffDvG0xIB8eyfgeLNYQRrLoMi-wr1H | Okay | Clean | Okay | Okay | https://drive.google.com/open?id=18zbAHtf9lD_6ZA4JKWGuqBS6ahlfYbj5 | Okay |  | Okay | https://drive.google.com/open?id=1WjXlNZ0TQJ9GSY8ysbn07SoFBzsFFsX7 | Okay | https://drive.google.com/open?id=1cuO2ZK9l_IqHBtsIGmiWFpZYjvM9PjQp | Okay |  | Okay | Okay |  | Okay | https://drive.google.com/open?id=1NZShJ5-KeQBRSDWcxfMpZN2UooLSrxYz | Okay | Okay | Okay | Done | Clean |  | 6/190 PSIG | 12.2/12.1/12.1 | 405/406/405 | Short | UNIT FOR PM SHOUDULE | UNIT PM DONE & OPERATION CHECKED FOUND WORKING AS NORMAL | No | https://drive.google.com/open?id=11lXtYsoSYzAbOm4gSQZ0VdeiiUd-KPM1, https://drive.google.com/open?id=1ij_axdbjDTuY8DFINb2CtlKgvbIzV9lB |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN058/25 | 2025-01-31 18:52 | crm@crystalgroup.in | Dr Reddy CTO5 | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | NA | CXRU1032564 | PREVENTIVE MAINTENANCE | Ninad | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  |  |  | 2025-02-04 12:29 | crm@crystalgroup.in | Dr Reddy CTO 5 | CXRU1032564 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN058 | DAikin | LXE10E147F2 | M001540 | K31304076026 | DECOS 3F 2611 / 1 | Used | JSGA622340187 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:42 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:37 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 00:22 | 2025-02-11 |  |  |  |  | CXRU1032564 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1h6LcKqLW2yeP4jwD2_yxqvZRKQK9SGDd | Okay |  | Okay |  | Okay | Okay | https://drive.google.com/open?id=1ncwi5jOBz1cZTC8ZY1sSWLV_pDHvQA3- | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9/210 | 9.9/9.8/9.8 | 407/406/407 | Short | UNIT PM SHOUDULE | UNIT PM DONE AND WORKING AS SATISFACTORY, WITH PTI TEST PASS | No | https://drive.google.com/open?id=1sUCa2KTw2gjOEB_NJLw93lebJ3VwIoaO, https://drive.google.com/open?id=1grma9R-mE9nc6Rrj_aFedXwxZEUbWYj5 |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN059/25 | 2025-01-31 18:54 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Srinivas | 7981717737 | NA | CXRU1030387 | PREVENTIVE MAINTENANCE | Ninad | plasma.projects@hetero.com | Telangana | Preventive Maintenance |  |  |  | 2025-02-04 12:32 | crm@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN059 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:37 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-09 19:04 | 2025-02-08 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -23c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/8. 170/190 | 9.8/9.9 9.9/9.8. 9.8/9.9 | 407/408/409 | Short | Two way Dainikn reefer workingfine | PM SERVICE DONE FOR TWO WAY DAIKIN UNIT | No | https://drive.google.com/open?id=14Egjd16VOd1wb8URYc7jSjp9GZIt60A2, https://drive.google.com/open?id=1n8ZRSDXIx7fJlNqaXl0WansGotaYDdah |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JAN060/25 | 2025-01-31 18:55 | crm@crystalgroup.in | Hetero Unit 5 | Mr. Malyadri ¦ Mr. Prudhvi | 80964 40123/ 99897 18520 | NA | SUDU6218004 | PREVENTIVE MAINTENANCE | Ninad | malyadri.k@hetero.com ¦ prudhviraju.v@hetero.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:33 | crm@crystalgroup.in | Hetero Unit 5 | SUDU6218004 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN060 | Carrier-Primeline | Primeline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished |  | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:37 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN061/25 | 2025-01-31 18:58 | crm@crystalgroup.in | Hetero Unit 5 | Mr. Malyadri ¦ Mr. Prudhvi | 80964 40123/ 99897 18520 | NA | CXRU1186425 | PREVENTIVE MAINTENANCE | Ninad | malyadri.k@hetero.com ¦ prudhviraju.v@hetero.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:35 | crm@crystalgroup.in | Hetero Unit 5 | CXRU1186425 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN061 | DAikin | LXE10E136F2 | M002116 | K31511151600 | DECOS 3F 2557 / 1 | Used | JSGA621320194 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:38 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
JAN062/25 | 2025-01-31 18:59 | crm@crystalgroup.in | Hetero Unit 5 | Mr. Malyadri ¦ Mr. Prudhvi | 80964 40123/ 99897 18520 | NA | CXRU1186467 | PREVENTIVE MAINTENANCE | Ninad | malyadri.k@hetero.com ¦ prudhviraju.v@hetero.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-04 12:37 | crm@crystalgroup.in | Hetero Unit 5 | CXRU1186467 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JAN062 | Daikin | LXE10E136F2 | M002118 | K31503145677 | DECOS 3F 2557 / 12 | Used | JSGA622180060 | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:38 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46
FEB001/25 | 2025-02-03 10:35 | crm@crystalgroup.in | NSR Trader | KAMARAJU | 9903999266 | MANAGER | TCLU1112683 | PREVENTIVE MAINTENANCE | Ninad | NA | TUNI | Preventive Maintenance |  |  |  | 2025-02-04 12:39 | crm@crystalgroup.in | NSR Trader | TCLU1112683 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB001 | [7 empty] | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:38 | crm@crystalgroup.in | NO | [7 empty] | 2025-03-02 20:30 | 2025-03-02 |  |  |  |  | TCLU1112683 |  |  |  | Thermo king | -3.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/a 22.2B | 8.0A 7.7A 7.9A | 400V 397V 399V | Not done | Container run in sound condition without any Alaram | Relay board replace, display replace, keypad replace, fillter Drier replace, vaccum, R-404a refill 4.0kg and condenser coil wash with normal water | No | https://drive.google.com/open?id=1a4KanPnQrXwY2ZaX3SUqYT40joracv-V, https://drive.google.com/open?id=1pyHC_bll7IHkM4Wyqu2QIMbuvN1cbWaD |  |  | Trip no 077 | No | No | Can be done on next PM | N/a | N/a | viru0068@gmail.com | REEFER
FEB002/25 | 2025-02-03 10:47 | crm@crystalgroup.in | LAURUS UNIT -1 | Narasimha Rao | 89780 90939 | Manager | APRU5000210 | PREVENTIVE MAINTENANCE | Ninad | narasimharao.b@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-04 12:41 | crm@crystalgroup.in | LAURAS UNIT 1 | APRU5000210 | 40FT | DAikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB002 | Carrier - Thinline | Thinline | 2594J02559 | GGCR80067211 |  | Refurbished |  | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:44 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:39 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-10 13:09 | 2025-02-06 |  |  |  |  | APRU5000210 |  |  |  | Carrier | -27.7 | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 17.1 | 2011-11-11 | 407/405/407 | Not done | Need to replace display | Found display defective and and condenser coil normal dirty | Yes | https://drive.google.com/open?id=1HMbL2I4RqoOSXg2tMz89DNUSkFWjIilF, https://drive.google.com/open?id=1KJ6YAdwIMTt5Mfb_26Y-k3rlzibK7gza |  |  | TRIP072 | Yes | Yes | Can be done on next PM | Carrier Display need to replaces | Carrier Display | crm@crystalgroup.in | REEFER
FEB003/25 | 2025-02-03 10:51 | crm@crystalgroup.in | LAURUS UNIT -1 | Narasimha Rao | 89780 90939 | Manager | PCIU6006639 | PREVENTIVE MAINTENANCE | NInad | narasimharao.b@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-04 12:44 | crm@crystalgroup.in | LAURAS UNIT 1 | PCIU6006639 | 40FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB003 | Daikin |  |  |  |  | used |  | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-03-26 11:08 | tender@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:40 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-10 15:41 | 2025-02-06 |  |  |  |  | PCIU6006639 |  |  |  | Daikin | 0.8*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1800KPM | 10.2/10.1/10.1 | 406/405/409 | Not done | NEED TO REPLACE DISPLAY & SHEET KEY | DISPLAY & SHEET KEY NOT WORKING | No | https://drive.google.com/open?id=1p8FjwUKf2b6KBp2RECA05oNcBrfCKXyb, https://drive.google.com/open?id=1iZuY3bb08CVmuVObkTHFo3sYH3BSJKMc |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB004/25 | 2025-02-03 10:53 | crm@crystalgroup.in | Laurus Unit 3 | 99631 98979 | 99631 98979 | NA | KKFU6711724 | PREVENTIVE MAINTENANCE | Ninad | somireddy.k@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-04 12:47 | crm@crystalgroup.in | Lauras Unit 3 | KKFU6711724 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB004 | Carrier - Thinline | Thinline | 4515UD3741 | LSX60253415 |  | used |  | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:44 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:40 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 10:15 | 2025-02-05 |  |  |  |  | KKFU6711724 |  |  |  | Carrier | +20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /17.0 | 2011-11-11 | 410/409/410 | Not done | NA | NA | No | https://drive.google.com/open?id=1fK_C0aYQJSIZrg05rtX9pcnVINaBYAw_, https://drive.google.com/open?id=1Qyawc5ynVQiez9hN5SDhZdvAtQYoSV0X |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB005/25 | 2025-02-03 10:54 | crm@crystalgroup.in | Laurus Unit 3 | Somi Reddy | 99631 98979 | NA | MYRU4519115 | PREVENTIVE MAINTENANCE | Ninad | somireddy.k@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-04 12:49 | crm@crystalgroup.in | Lauras Unit 3 | MYRU4519115 | 40FT | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB005 | Carrier - Thinline | Thinline |  |  |  | Used |  | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-04 14:44 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-05 11:09 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-05 11:40 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 12:03 | 2025-02-05 |  |  |  |  | MYRU4519115 |  |  |  | Daikin | + 20*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /1800KPA | 10.1/10.2/10 | 405/406/407 | Not done | NA | NA | No | https://drive.google.com/open?id=1hqnaGBhTvvQX96qG16oDOSn2xJd_QhcX, https://drive.google.com/open?id=1C9QZeRJPmzcuJat6eZigB6kKHRPr15Rj |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB006/25 | 2025-02-03 11:50 | operation@crystalgroup.in | Jubliant Consumer Pvt Ltd | ATUL TYAGI | 7827984943 | MANAGER | TRIU6687350 | ICE FORMATION | NINAD | NA | Noida | Running with issues |  |  |  | 2025-02-06 14:55 | service@crystalgroup.in | JUBILIENT | TRIU6687350 | 20 ft reefer | carrier | SERVICE-ON CALL | LEASE | FOC | temperature not pull down to the set point - 25C | clean condenser coil with fresh water | no | No | condenser coil to much dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB006 | main unit | carrier prime line | ok | ok | ok | USED | NA | RAMIZ | No | ICE FORMATION | 2025-02-07 12:43 | mum.depot@crystalgroup.in | NO | [9 empty] | 2025-02-07 12:43 | mum.depot@crystalgroup.in | NO |  |  |  |  | 2025-02-07 12:44 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-10 12:49 | 2025-02-06 |  |  |  |  | TRIU6687350 |  |  |  | Carrier | -25'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | O.5 & 13.5 BAR | 9.8/9.7/98 | 410/411/410 | Not done | FOUND CONDENSER COIL VERY MUCH DIRTY | CLEAN CONDENSER COIL WITH FRESH WATER & THE UNIT WORING GOOD CONDITION | No | https://drive.google.com/open?id=1l9qKCS3Im0vnp-i2Osdyas_WXkYli0kx, https://drive.google.com/open?id=1mb0SIrV4XjixmoKDasZT1SU8MkWN3cnM |  |  | na | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB008/25 | 2025-02-05 14:18 | crm@crystalgroup.in | Dr. Reddy's Labs -Biologics | Suresh Kasam | 99081 25456 | Plant Engineer | TITU9930114 | PREVENTIVE MAINTENANCE | Ninad | sureshkasam@drredddys.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-05 14:45 | technician@crystalgroup.in | DR. REDDY BIOLOGICS BACHUPALLY | TITU9930114 | 40 | TK MP 4000 | SERVICE-ON CALL | LEASE | FOC | FOUND COMPRESSOR OVER HEAT & NOISY. | NEED TO REPLACED COMPRESSOR / FILTER DRIER & VACUM WITH GAS R404 | THERMOKING COMPRESSOR/ FILTER DRIER/ GASKET DIS WITH O- RING SUC & GAS R 404 5 KG/ VACUM PUMP AND NITOGEN FOR LEAK TEST | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB008 | TK MP 4009 | TK MP 4009 | NA | NA | NA | USED | NA | SHAHBUDDIN | No | PREVENTIVE MAINTENANCE | 2025-02-11 12:16 | operation@crystalgroup.in | YES | FEB011 | 2025-02-11 | Consumables, Spares, FOC | SHAHBUDDIN | HYDERABAD | TITU9930114 | SITE | FOC | TK-MP4000 | 2025-02-28 12:57 | service@crystalgroup.in | YES | FEB011 | YES | [12 empty] | 2025-02-05 19:59 | 2025-02-05 |  |  |  |  | TITU9930114 |  |  |  | Thermo king | - 28 c | Clean | Clean | https://drive.google.com/open?id=1Dg4h_DqboJNb6jrOimhVepVU1fmNgZvY | Okay | Clean | Okay | Okay |  | Okay | https://drive.google.com/open?id=14bWff2AkhLJmJNrpYwwBu1JnLshvgwwc | Okay | https://drive.google.com/open?id=1CgYEAHsfu0WdFQo3XqG-gxAJEenUIrnZ | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/21 bar | 11.2/11.3/11.4 | 407/408/409 | Short | Two way thermoking main unit found compressor over heat with Noisy and leak back. | Need to replaced compressor scroll Tk asap. | Yes | https://drive.google.com/open?id=1XD1CQjm9cDh9icOw5KVGmP3y6C8LFda3, https://drive.google.com/open?id=1jvnl4ebYgRwSPWrvtz36BvQN0OMStHgW |  |  | 71 | Yes | No | Can be done on next PM | As above | Scroll TK compressor, Filter Drier, Gas ket Discharge Flame, O- Ring for suction Flange value.GasR 404 ( 6kg) Nitogen for flushout & for leak test, vacum pump.... | technician@crystalgroup.in | REEFER
FEB009/25 | 2025-02-06 12:31 | crm@crystalgroup.in | Crystal Dhulagarh | NA | NA | NA | TRLU5253890 | Painting | Pushpa | NA | Dhulagarh, Kolkata | Refurbishment |  |  |  | 2025-02-07 10:01 | service@crystalgroup.in | Crystal Dhulagarh | TRLU5253890 | 40' | NA | SERVICE-AT SITE | LEASE | FOC | Need to Carry Out Painting | NA | Blue Paint 5002 SR Thinner and Primer | Yes | Need to deploy on new Site | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB009 | NA | NA | NA | NA | NA | Used | NA | THIRD PARTY LOCAL | No | Painting | 2025-02-27 10:34 | service@crystalgroup.in | NO | [9 empty] | 2025-02-27 10:36 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-27 10:36 | service@crystalgroup.in | NO | [7 empty] | 2025-02-27 10:37 | [54 empty] | service@crystalgroup.in | DRY/Others
FEB010/25 | 2025-02-06 12:32 | crm@crystalgroup.in | Crystal Dhulagarh | NA | NA | NA | CRLU3179858 | Painting | Pushpa | NA | Dhulagarh, Kolkata | Refurbishment |  |  |  | 2025-02-07 09:59 | service@crystalgroup.in | Crystal Dhulagarh | CRLU3179858 | 40' | NA | SERVICE-AT SITE | LEASE | FOC | Need to Carry out Painting | NA | Blue Paint 5002 SR Thinner | Yes | Need to deploy at New Site | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB010 | NA | NA | NA | NA | NA | Used | NA | THIRD PARTY LOCAL | No | Painting | 2025-02-27 10:32 | service@crystalgroup.in | NO | [9 empty] | 2025-02-27 10:32 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-27 10:33 | service@crystalgroup.in | NO | [7 empty] | 2025-02-27 10:33 | [54 empty] | service@crystalgroup.in | DRY/Others
FEB011/25 | 2025-02-06 18:13 | crm@crystalgroup.in | DIVIS LAB | NA | NA | NA | CONT 2 | PREVENTIVE MAINTENANCE | Ninad | NA | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:27 | crm@crystalgroup.in | Divis Labs | CONT 2 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB011 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:23 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:26 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 12:34 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-06 21:39 | 2025-02-06 |  |  |  |  | DEVIS CONTR. DC SEZ A/C CONTR.NO#02 |  |  |  | Carrier | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/190 PSIG | 12.4/12.3/12.3 | 407/407/409 | Full | Unit pm done & observation unit found working as fine | NA | No | https://drive.google.com/open?id=1zit7uuiIjiI4qejOJMBYq9watvdlDS4-, https://drive.google.com/open?id=1r6OIellpxCc_Q3M7Qs7pViir7vOkV_7k |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB012/25 | 2025-02-06 18:15 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | On Duty Officer | CONT 3 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:25 | crm@crystalgroup.in | Divis Labs | CONT 3 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB012 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:23 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:26 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:27 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-06 21:27 | 2025-02-06 |  |  |  |  | TRIU8387141/ DEVIS UNIT NO: DC SEZ A/C NO# 03 |  |  |  | Carrier | + 22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/180 PSIG | 12.9/12.8/12.8 | 407//406/405 | Short | Unit pm done and working as fine with no alaram | No | No | https://drive.google.com/open?id=1M1KPlQhVn64mo8JaQp1Q5cVm36zWK585, https://drive.google.com/open?id=1OLyP9UM_Td9zZobx0YXYmEQkAeEUnNoO |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB013/25 | 2025-02-06 18:18 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CONT 4 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:18 | crm@crystalgroup.in | Divis Labs | CONT 4 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB013 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:23 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:28 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-06 21:16 | 2025-02-06 |  |  |  |  | TRIU8363258/ DEVIS NO: DC SEZ- A/C CONTR. # 04 |  |  |  | Carrier | +2.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/180 PSIG | 12.9/12.8/12.8 | 406/407/406 | Short | Found unit Evaprator motor number 1 Noisy & over heating. | Replaced Evaprator motor. Secure motor wiring run unit checked unit operation , unit working as fine | No | https://drive.google.com/open?id=1hCoO7bqsS5z9ccrZEDUsqUuqv_9S-GcY, https://drive.google.com/open?id=1AvrgQc8dtG_fhj1XQ3jM84G0SIiyfsLA |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB014/25 | 2025-02-06 18:20 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CONT 5 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:15 | crm@crystalgroup.in | Divis Labs | CONT 5 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB014 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:22 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:28 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-07 21:53 | 2025-02-07 |  |  |  |  | DC SEZ A/C CONTR. # 05 ( ORIGINAL NO NOT AVILABLE) |  |  |  | Carrier | -12.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/170 | 12.7/12.8/12./ | 406/407/406 | Full | CARRIER THIN LINE REEFER UNIT WORKING AS SATISFACTORY. | PM Complited | No | https://drive.google.com/open?id=1IN1uJSZl5iFDPGaU50nRpSxqjl0wmawQ, https://drive.google.com/open?id=1mNgisHEzZVinOebFfBVIBrpiaJ8o-QR3 |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB015/25 | 2025-02-06 18:21 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | On Duty Officer | CONT 6 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:13 | crm@crystalgroup.in | Divis Labs | CONT 6 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB015 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:22 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:24 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:29 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-07 22:02 | 2025-02-07 |  |  |  |  | APRU5090955/ DEVIS NO: DC SEZ A/C #06 |  |  |  | Carrier | - 21 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/190 PSIG | 12. 1/12.2/12.2 | 407/408/407 | Short | CARRIER REEFER THIN LINE UNIT WORKING AS FINE | PM SERVICE COMPLAINTS | Yes | https://drive.google.com/open?id=1RFqGxoFuUkf2PuK6Q9BNld4sN_7i5Fab, https://drive.google.com/open?id=1uzEmTyV59M_4NkmuzUFjGxYAQJstYn8f |  |  | 71 | No | No | Can be done on next PM | NA | DOOR GASKET & TWO STS SENSOR | technician@crystalgroup.in | REEFER
FEB016/25 | 2025-02-06 18:23 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CONT 7 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:10 | crm@crystalgroup.in | Divis Labs | CONT 7 | 40 FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB016 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:21 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:24 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:29 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-07 22:09 | 2025-02-07 |  |  |  |  | TDRU7152244 DEVIS NO: DC SEZ A/C CONTR# 07 |  |  |  | Daikin | -11.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/190 PSIG | 9.9/9.8/9.9 | 406/407/406 | Short | DAIKIN REEFER UNIT WORKING AS SATISFACTORY | PM SERVICE DONE | No | https://drive.google.com/open?id=1YrEs7o0ft0TAx6s62LaQsj1uVfu7huV3, https://drive.google.com/open?id=1lWbcJU_e6rVFnCQsN1CqfhIwLZKzbiY1 |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB017/25 | 2025-02-06 18:24 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CONT 8 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:07 | crm@crystalgroup.in | Divis Labs | CONT 8 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB017 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:22 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:30 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-07 21:44 | 2025-02-07 |  |  |  |  | TCLU10032229/ DC SEZ A/C CONTR. 08 |  |  |  | Thermo king | -10c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/20 bar | 9.9/10/10 | 407/406/407 | Full | TK MP 3000 UNIT WORKING AS SATISFACTORY WITH NO ALRAM.PM SERVICE DONE | PM SERVICE DONE | No | https://drive.google.com/open?id=1Y24XCSKExGe5jsLWA4XrYDMNRmjTOATQ, https://drive.google.com/open?id=1mV4No8rVo0fclFR4SWWniu-uA3aqLj-D |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB018/25 | 2025-02-06 18:25 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CONT 9 | PREVENTIVE MAINTENANCE | Ninad | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-02-07 16:06 | crm@crystalgroup.in | Divis Labs | CONT 9 | 40FT | NA | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB018 | NA | NA | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | PREVENTIVE MAINTENANCE | 2025-02-07 17:21 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-07 17:24 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-08 16:31 | mum.depot@crystalgroup.in | NO | [7 empty] | 2025-02-07 22:18 | 2025-02-07 |  |  |  |  | TRIU8431985 DEVIS : DC SEZ A/C CONTR# 09 |  |  |  | Carrier | - 23c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/190 PSIG | 13/12.9/13.1 | 407/408/409 | Short | CARRIER THIN LINE REEFER WORKING AS SATISFACTORY | PM SERVICE DONE | No | https://drive.google.com/open?id=1c5Kh4Bnan5nrm-3vsQwcphwG0KZunuD_, https://drive.google.com/open?id=1HkVmdCg1OcMWxZ9fFgHbKNvJB1-W2NtR |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB019/25 | 2025-02-07 14:48 | operation@crystalgroup.in | Qwik Supply | Nabajit Talukdar | +91 9817976354 | DC Operations | TRIU8850831 | ALARM CODE VISIBLE | NINAD | nabajit.talukdar@qwik.co.in | Guwahati | Complete Breakdown |  |  |  | 2025-02-07 16:00 | service@crystalgroup.in | Qwik Supply | TRIU8850831 | 40FT STD RF | carrier thine line | SERVICE-ON CALL | LEASE | FOC | suspected less gas , compressor heavy noise . | check on VC / need technician visit | gas R134a 4 kgs , filter drier | Yes | After find leakage we can explant | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB019 | Carrier - Thinline | Thinline | ok | ok | ok | Used | JSGA622180048 | VIRENDRA | Yes | ALARM CODE VISIBLE | 2025-02-10 15:39 | operation@crystalgroup.in | YES | FEB009 | 2025-02-10 | Consumables, Spares | QWIK SUPPLY | Guwahati | TRIU8850831 | SITE | FOC | CARRIER-THINLINE | 2025-02-27 10:30 | service@crystalgroup.in | NO |  |  |  |  | 2025-03-06 15:29 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-07 19:03 | 2025-05-07 |  |  |  |  | TRIU8850831 |  |  |  | Daikin | -18'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5 bar | 9.8/9.7/9.8 | 404/403/404 | Not done | Need to replace unit | Fix new daikin unit | No | https://drive.google.com/open?id=1kDZwXw-ni1LCayjgZHQEfRao41a5etDG | https://drive.google.com/open?id=1bz0vkZVKFs-CukwCO9aJY2rLCWaxF3fZ |  | 85 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
FEB020/25 | 2025-02-07 14:59 | crm@crystalgroup.in | Crystal | NA | NA | NA | CXRU1034382 | Modification(additional reefer machine, cut out) for QAS-5047/24-25 | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-02-07 15:42 | service@crystalgroup.in | Crystal Yard | CXRU1034382 | 40FT STD RF | Thermoking | SERVICE-AT SITE | LEASE | FOC | Modification in container | Need to Cut Container body and need to reinstall same | NA | No | Need to Install In New Order with 2 Unit | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB020 | Daikin LXE | Daikin LXE | NA | DECOSIII/2551/1 | ABC782900321510023 | Used | NA | THIRD PARTY LOCAL | No | Modification(additional reefer machine, cut out) for QAS-5047/24-25 | 2025-02-11 15:34 | operation@crystalgroup.in | YES | FEB012 | 2025-02-11 | Consumables, Spares, FOC | CRYSTAL YARD | JNPT ( GODREJ ) | CXRU1034382 | DEPOT | FOC | TK-MP4000 | 2025-02-11 15:47 | operation@crystalgroup.in | YES | FEB012 | YES | https://drive.google.com/open?id=1jjMmR-vwqAOyaG-U6itUwS3msOES31rW |  | 2025-02-26 10:57 | service@crystalgroup.in | NO | [7 empty] | 2025-02-26 12:46 | 2025-02-14 |  |  |  |  | CXRU1034382 |  |  |  | Thermo king | 3 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/0.7 and 20/21 bar | 9.9/9.8,9.8/9.9,9.8/9.9 | 409/410/410 | Short | NA | Cutting done and 2 Nos TK unit swapped for making it 2 Way | No | https://drive.google.com/open?id=1g8kJbTUH7zS5tNrn8okILj28RuXtfBUJ |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB021/25 | 2025-02-07 15:06 | crm@crystalgroup.in | Crystal | NA | NA | NA | SEGU9511192 | Additional reefer machine , Ante room for QAS-5449A/24-25 | Rahul | NA | JNPT | Running with issues |  |  |  | 2025-02-08 14:40 | service@crystalgroup.in | Crystal Yard | SEGU9511192 | 40FT STD RF | CARRIER THINELINE | SERVICE-AT SITE | LEASE | FOC | Additional reefer machine , Ante room for QAS-5449A/24-25 | Need to Cut Container body and need to reinstall same | NA | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB021 | Carrier | Thinline | Na | NA | NA | Used | NA | Rajkumar | Yes | Additional reefer machine , Ante room for QAS-5449A/24-25 | 2025-02-11 15:40 | operation@crystalgroup.in | YES | FEB013 | 2025-02-11 | Consumables, FOC | Crystal Yard ( DR REDDY ) | JNPT | SEGU9511192 | DEPOT | FOC | CARRIER-THINLINE | 2025-02-11 15:48 | operation@crystalgroup.in | YES | FEB013 | YES | https://drive.google.com/open?id=1UuO1_TZ8DMNWcQ_ZgmZtuk-5Ow2B8Xac |  | 2025-03-15 15:03 | kshirod.khatua@crystalgroup.in | NO
FEB022/25 | 2025-02-07 15:22 | crm@crystalgroup.in | Navin Fluorine | Ketan | 6357662623 | NA | CCLU1031878 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Ninad | NA | Dhej | Running with issues |  |  |  | 2025-02-12 16:13 | crm@crystalgroup.in | Navin Fluorine | CCLU1031878 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | Gas top up | Required Gas top up R134 | Gas top up R134 | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB022 | Carrier - Thinline | Thinline | NA | NA | NA | Used | NA | Rajkumar | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-02-12 16:35 | operation@crystalgroup.in | YES | FEB015 | 2025-02-12 | Consumables, FOC | Navin Fluorine | DHEJ | CCLU1031878 | SITE | FOC | CARRIER-THINLINE | 2025-02-24 12:18 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-24 12:19 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-24 12:24 | 2025-02-22 |  |  |  |  | CCLU1031878 |  |  |  | Carrier | +5*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /14.1 | 14.8/14.9/15 | 440/439/440 | Not done | NA | Unit running in good condition | No | https://drive.google.com/open?id=1eOPA1z9ras00otR2AdMuWIjQ_umEPXJO, https://drive.google.com/open?id=1g-90l8DOaQ5M1bUJne0VFKo7eeH0PnWN |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB023/25 | 2025-02-09 17:16 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | GAURAV GULHANE | 9145242830 | EXECUTIVE | MYRU4500887 | COMPRESSOR INTERNALLY DAMAGED | NINAD | NA | Hyderabad | Running with issues |  |  |  | 2025-02-09 17:21 | operation@crystalgroup.in | HETERO PLASMA | MYRU4500887 | 40FT STD RF | DAIKIN | MACHINE INSPECTION | LEASE | FOC | NO GAS IN SYSTEM ,COMMPRESSOR NOT PERFORMING THE DISCHARGE PRESSURE SUSPECTED DAMAGED INTERNALLY | REPLACE COMPRESSOR |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB023 | Daikin | Daikin | NOT AVAILABLE | LXE10E136A | DECOS 3E | Refurbished | NOT AVAABLE | SHAHBUDDIN | Yes | COMPRESSOR INTERNALLY DAMAGED | 2025-02-09 17:37 | operation@crystalgroup.in | YES | FEB006 | 2025-02-09 | Consumables, Spares, FOC | HETERO PLASMA | Hyderabad | MYRU4500887 | SITE | FOC | DAIKIN | 2025-02-11 15:51 | operation@crystalgroup.in | YES | FEB006 | YES | https://drive.google.com/open?id=10yDswuqWlyTZcg8_jdLw_CqYXF2yafDv |  | 2025-02-24 18:46 | crm@crystalgroup.in | YES | FEB006 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-02-08 23:33 | 2025-02-08 |  |  |  |  | MYRU5400887 |  |  |  | Daikin | - 25c | Clean | Clean | https://drive.google.com/open?id=1CgWxSJJDjd9lX2Cq6BKbJ1MxQg0fOE8F | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1-k5mygJD_lJ7P7EjPHAoz3R2oKyD3-AP | Okay |  | Okay |  | Okay | Okay | https://drive.google.com/open?id=14L121FQZ19oVzmeShBUbw_WbUheq92He | Okay | https://drive.google.com/open?id=1gl75R-m_ooawGVQq5FTdW7-tppPRFGR8 | Okay | Okay | Okay | Done | Need to replace |  | 8/0& 190/00 | 9.8/9.7/9.7 | 407/409/408 | Short | Two way daikin unit , Main unit working as fine Side unit compressor having problems not function due to internal mechanical isdue | Need to replaced side compressor with filter drier/ solonied value and Gas R134a | Yes | https://drive.google.com/open?id=1OuzfXcNWBz6fFJr6hqjR9tHGrngpo4PU, https://drive.google.com/open?id=1xib29CAlcc6GR_7c58Ehq0ANywu7fJR3 |  |  | 71 | No | Yes | Urgent | Side unit only | Job order | technician@crystalgroup.in | REEFER
FEB024/25 | 2025-02-10 16:48 | crm@crystalgroup.in | RELIANCE | Mark / Anbu | 77188 81734 ¦ 90040 43704 | NA | CGMU2991679 | PREVENTIVE MAINTENANCE | Ninad | mark.Silveira@ril.com / anbu.EZHILAN@ril.com | Jamnagar Gujarat | Preventive Maintenance |  |  |  | 2025-02-10 16:57 | crm@crystalgroup.in | Reliance - Jamnagar | CGMU2991679 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB024 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | Raj Kumar | Yes | PREVENTIVE MAINTENANCE | 2025-04-19 10:56 | tender@crystalgroup.in | NO | [9 empty] | 2025-04-19 10:57 | tender@crystalgroup.in | NO | [14 empty] | 2025-02-19 10:33 | 2025-02-13 |  |  |  |  | CGMU2991679 |  |  |  | Carrier | -6*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | NA | NA | Yes | https://drive.google.com/open?id=1o6MJdDmpFUh5IpA6hCPQNGYUbkKZ-d0z, https://drive.google.com/open?id=1PQZ6HaHSdaAj2xyyMAv6IjTBy2PYala4 |  |  | TRIP073 | Yes | Yes | Urgent | Keypad installation | Heater Keypad | crm@crystalgroup.in | REEFER
FEB025/25 | 2025-02-10 17:00 | crm@crystalgroup.in | Kirloskar Corrocoat | Shailendra Patil/Jawed | 9881230615/9386362186 | NA | ARCU4530799 | PREVENTIVE MAINTENANCE | Ninad | shailendra.patil@kicopl.com | Jamnagar Gujarat | Preventive Maintenance |  |  |  | 2025-02-18 15:01 | crm@crystalgroup.in | Kirloskar Corrocoat | ARCU4530799 | 20FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB025 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-18 15:02 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-18 15:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-18 15:05 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-18 15:24 | 2025-02-12 |  |  |  |  | ARCU4530799 |  |  |  | Carrier | +13*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /15.1 | 15/15/14.8 | 405/404/405 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1LfjCnZmRRHh-NVtuH7u-39TGlodzakcN, https://drive.google.com/open?id=1y3jKEVuoNksrmf6VN1kiJ4iaMTavF7qE |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB026/25 | 2025-02-10 17:03 | crm@crystalgroup.in | DHL Supply Chain pvt Ltd | Shailesh Patil ¦ Yogindar Singh ¦ Niranjan Kanthe | 99099 86653 ¦ 9460975040 ¦ 70830 26116 | NA | TCLU1912270 | PREVENTIVE MAINTENANCE | Ninad | yogindar.singh@dhl.com ¦ niranjan.kanthe@dhl.com | Ahmedabad | Preventive Maintenance |  |  |  | 2025-02-24 16:46 | crm@crystalgroup.in | DHL Supply Chain | TCLU1912270 | 20FT | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=%20FEB026 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | Yes | PREVENTIVE MAINTENANCE | 2025-02-24 16:46 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-24 16:46 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-24 16:47 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-24 16:41 | 2025-02-18 |  |  |  |  | TCLU1912270 |  |  |  | Daikin | +3*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 178/1532 | 9.5/9.5/9.4 | 402/401/402 | Short | NA | NA | No | https://drive.google.com/open?id=1Z3YED_WhDQ4p1vVyqEXvUZAETP5adAJw, https://drive.google.com/open?id=1qtLMH8rpRbCtr91X-MC3vOO6XJ6jOyrZ |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB027/25 | 2025-02-10 17:12 | crm@crystalgroup.in | Qwik Supply -Ahmedabad | Mohit Rai | 9023419864 | ASSISTANT MANAGER | TDRU5815332 | PREVENTIVE MAINTENANCE | Ninad | mohit2.rai@qwik.co.in | Ahmedabad | Preventive Maintenance |  |  |  | 2025-02-21 18:17 | crm@crystalgroup.in | Qwik Supply -Ahmedabad | TDRU5815332 | 40FT STD RF | Carrier Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB027 | Carrier - Thinline | Thinline | NA | NA | NA | NA | NA | RAJ KUMAR | Yes | PREVENTIVE MAINTENANCE | 2025-02-21 18:18 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-21 18:18 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-21 18:18 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-21 18:26 | 2025-02-19 |  |  |  |  | TDRU5815332 |  |  |  | Carrier | -21*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /14.9 | 12.6/12.6/12.5 | 419/418/419 | Not done | NA | NA | No | https://drive.google.com/open?id=1yzz1TXqdHzLOAvBEBJvE2THCRHcEUQCD, https://drive.google.com/open?id=1FirzhucTC-EhYYlNXi0PAjHDlicwpkLV |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB028/25 | 2025-02-10 17:32 | crm@crystalgroup.in | PI Industries Limited unit 6 | Dinesh Jaiswal | 92272 04408 | NA | MYRU4502299 | PREVENTIVE MAINTENANCE | Ninad | dinesh.jaiswal@piind.com | Panoli, Gujarat | Preventive Maintenance |  |  |  | 2025-03-12 10:39 | technician@crystalgroup.in | PI Industries Limited unit 6 | MYRU4502299 | 40' | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | PM Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB028%2F25 | DAIKIN | LXE 10-E | NA | NA | NA | Used | NA | Pm Done by Rajkumar | No | PREVENTIVE MAINTENANCE | 2025-05-06 17:22 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:39 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-10 14:56 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-24 11:24 | 2025-02-21 |  |  |  |  | MYRU4502299 |  |  |  | Daikin | -4*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Rusty |  | 128 KPA & 1263 KPA | 9A/9A/8.9A | 398/397/398 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1ihds0rTcTHiXJbhpnURwbhO1-GL1ejOU, https://drive.google.com/open?id=1NXJqOYXJ--MpgWRlK99TNR6IYe-rkx0j |  |  | TRIP073 | Yes | Yes | Can be done on next PM | Filter drier to be Replaced | Filter drier | crm@crystalgroup.in | REEFER
FEB029/25 | 2025-02-10 17:35 | crm@crystalgroup.in | PI Industries Limited | Dinesh Jaiswal | 92272 04408 | NA | CXRU1035856 | PREVENTIVE MAINTENANCE | Ninad | dinesh.jaiswal@piind.com | Panoli, Gujarat | Preventive Maintenance |  |  |  | 2025-02-26 11:00 | crm@crystalgroup.in | PI Industries | CXRU1035856 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB029 | DAikin | LXE10E147F2 | M000552 | K31412143316 | DECOS 3F 2553 / 1 | used | NA | RAJ KUMAR | Yes | PREVENTIVE MAINTENANCE | 2025-02-26 11:14 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-26 11:15 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-26 11:16 | crm@crystalgroup.in | NO
FEB030/25 | 2025-02-10 17:37 | crm@crystalgroup.in | Navin Fluorine | Alpesh Patel | 8347404111 | NA | HJCU6013796 | PREVENTIVE MAINTENANCE | Ninad | alpesh.patel@nfil.in | Surat | Preventive Maintenance |  |  |  | 2025-02-25 17:17 | crm@crystalgroup.in | Navin Fluorine | HJCU6013796 | 40FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB030 | Carrier - Thinline | Thinline | NA | NA | NA | Refurbished | NA | RAJ KUMAR | Yes | PREVENTIVE MAINTENANCE | 2025-02-25 17:20 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-25 17:20 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-25 17:21 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-25 17:43 | 2025-02-25 |  |  |  |  | HJCU6013796 |  |  |  | Carrier | NA | Dirty | Rusty |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Rusty |  | 15.3 | 16.7/16.6/16.9 | 418/417/418 | Not done | NA | NA | Yes | https://drive.google.com/open?id=1dYkQVVIV0SeyCxXTyCY4bCVnOdfFDT_J, https://drive.google.com/open?id=1Y_UbEuy5vBPNXGkD_rYYiORoVJy3hfqM |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB031/25 | 2025-02-10 17:39 | crm@crystalgroup.in | Switz International | Vilas/ Nitin Y Pagar | 98194 73839 ¦ 8511131793 | NA | TITU8259465 | PREVENTIVE MAINTENANCE | Ninad | vilasp@india.switzgroup.com ¦ nitinp@india.switzgroup.com | Daman | Preventive Maintenance |  |  |  | 2025-02-26 11:03 | crm@crystalgroup.in | Switz International | TITU8259465 | 20FT Spl RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB031 | Thermoking MP-4000 | MP 4000 | NA | NA | NA | Brand New | NA | RAJ KUMAR | Yes | PREVENTIVE MAINTENANCE | 2025-02-26 11:14 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-26 11:15 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-26 11:16 | crm@crystalgroup.in | NO | [7 empty] | 2025-03-04 18:19 | 2025-02-27 |  |  |  |  | TITU8259465 |  |  |  | Carrier | -21c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 21 bar | 10.8-R. 10.7-B, 10.6-Y | L1-409, L2-408, L3-409 | Not done | We have attende container found Condenser coil havy dirty condition | We have washed the condenser coil with normal water | No | https://drive.google.com/open?id=1AZThMPbouT8inqqE7p6zOxJha8Pjeg3B, https://drive.google.com/open?id=1vQYVtzLNVQmqTTIy2hu5aRj48jA63FXb |  |  | TRIP073 | No | No | Can be done on next PM | N/a | N/a | rajreefertech@gmail.com | REEFER
FEB032/25 | 2025-02-10 18:23 | crm@crystalgroup.in | Earl Corvus Habitat | Rajeev Gupta | NA | NA | CICU1938143 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Rahul | Rajeev@emcure.co.in | Jammu | Running with issues |  |  |  | 2025-03-07 16:35 | rahul.gawade@crystalgroup.in | EmCure | CICU1938143 | 20ft | Thermoking | REPAIR | SALE | CHARGEABLE | Controller issue (Required 2C, automatecally changes to -69 | Need to replace contoller with our existing Reefer unit's controller. Existing Reefer unit's controller need to modify and test for 3 days before dispatch. | Modified software installed and tested Controller from Existing unit. | Yes | Suspected Controller software issue. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB032%2F25 | Thermoking Superfreezer | Thermoking MP4000 Superfreezer | Missing | Missing | MP4000 | Brandnew | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-04-15 15:19 | tender@crystalgroup.in | YES | FEB074 | 2025-02-15 | Spares | EMCURE | Jammu & Kashmir | CICU1938143 | SITE | FOC | TK-MP4000 | 2025-04-15 15:21 | tender@crystalgroup.in | YES | FEB074 | YES |  |  | 2025-07-07 17:55 | crm@crystalgroup.in | YES | FEB074 | COURIER | 31210305396 | Indigo Cargo |  | https://drive.google.com/open?id=1jOloqAcyAdpIMokLfmG0F2TYZV6hFZ0v |  | 2025-07-09 12:26 | 2025-07-07 |  |  |  |  | CICU1938143 |  |  |  | Thermo king | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | Controller was Replaced on call | Installation of controller was done on call | No | https://drive.google.com/open?id=1kykAnwS5Uc50MuYXeuZJBFTUYA3q7FZH | https://drive.google.com/open?id=1q5xrFTDliNQZuKDIHF-Bvh9O19xQJot3 |  | NA | No | No | Can be done on next PM | NA | Controller Replacement- Under warrenty till 2027 | crm@crystalgroup.in | REEFER
FEB033/25 | 2025-02-11 17:44 | crm@crystalgroup.in | Shah TC | Jitendra Sharma | 9711734411 | Sr. Manager – Operations & Logistics | CXRU1186451 | Power connector Cable burned | Sushma | jitenderk@shahtc.com | Panvel | Running with issues |  |  |  | 2025-02-13 10:34 | service@crystalgroup.in | Shah TC | CXRU1186451 | 40 reefer | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | ISO PLUG BURNT | replaced ISO plug with new one | na | No | POWER Fluctional | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB033 | DK | DAIKIN LXE10 E | OK | OK | OK | USED | OK | RAMIZ | No | Power connector Cable burned | 2025-02-15 11:33 | service@crystalgroup.in | YES | FEB066 | 2025-02-11 | Paid | Shah TC | Uran Navi Mumbai | CXRU1186451 | SITE | PAID | DAIKIN | 2025-02-15 11:34 | service@crystalgroup.in | YES | FEB066 | YES |  |  | 2025-02-15 11:35 | service@crystalgroup.in | YES | FEB066 | TECHNICIAN |  |  | RAMIZ |  |  | 2025-02-15 11:41 | 2025-02-11 |  |  |  |  | CXRU1186451 |  |  |  | Daikin | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8 AND 14,3 bAR | 9.8/9.8/9.6 | 411/411/410 | Not done | NA | Replaced ISO Plug | No | https://drive.google.com/open?id=1ZHn9MxopxML5bNmt6ZceTYh7sd4Ffu4h, https://drive.google.com/open?id=1rHr3j5O3eYSf2bDnaZkeQ_mCMax1atRY |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB034/25 | 2025-02-12 10:20 | crm@crystalgroup.in | Laurus Unit 3 | Somi Reddy | 99631 98979 | NA | DFOU6120384 | PREVENTIVE MAINTENANCE | Ninad | somireddy.k@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-18 12:14 | crm@crystalgroup.in | Laurus Unit 3 | DFOU6120384 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB034 | Daikin | Daikin | MOO4338 | NA | NA | Used | NA | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-18 12:20 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-18 12:24 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-18 12:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 10:34 | 2025-02-05 |  |  |  |  | DFOU6120384 |  |  |  | Daikin | +22*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1700KPA | 10.0/10.1/10.2 | 407/407/406 | Not done | NA | NA | No | https://drive.google.com/open?id=1lObjDKH1wDnKmpyEKxGKgeQ2WWWhuzs7, https://drive.google.com/open?id=1WdOgua27gB-noyti4d4u7wroJBUpwhXf |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB035/25 | 2025-02-12 12:19 | crm@crystalgroup.in | Reliance Taloja | SANDEEP RATHOD | 7977704469 | MANAGER | TRIU6681440 | PCM pads not freezing | Ninad | sandeep3.rathod@ril.com | Taloja | Running with issues |  |  |  | 2025-02-12 12:55 | operation@crystalgroup.in | Reliance Taloja | TRIU6681440 | 20FT STD RF - Dual Machine Carrier | Carrier Thinline | REPAIR | LEASE | FOC | filter drier chock, heater failure, alarm aa60, aa61 | . |  | Yes | . | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB035 | Carrier - Transcold | Transcold | . | . | . | Used | . | VIRENDRA | Yes | PCM pads not freezing | 2025-02-12 13:02 | operation@crystalgroup.in | YES | FEB014 | 2025-02-12 | Consumables, Spares, FOC | Reliance | TALOJA | TRIU6681440 | SITE | FOC | CARRIER-THINLINE | 2025-02-15 10:24 | service@crystalgroup.in | YES | FEB014 | YES |  |  | 2025-02-15 10:27 | service@crystalgroup.in | YES | FEB014 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-02-15 10:55 | 2025-02-14 |  |  |  |  | TRIU6681440 |  |  |  | Carrier | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 17.06 | 10/10.7/10.5 | 408/403/405 | Not done | container running condition | Replaced Heater Coil 6 Nos ,Filter dryer,and 4 Kg R134A Gas reefilled | No | https://drive.google.com/open?id=1su5Saexq6ySE1GfjZqobpdSPx3VTyuUY |  |  | TRIP074 | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB036/25 | 2025-02-12 12:23 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 99631 98979 | NA | BMOU9784137 | PREVENTIVE MAINTENANCE | Ninad | somireddy.k@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-02-18 12:16 | crm@crystalgroup.in | LAURUS UNIT 3 | BMOU9784137 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB036 | Daikin | NA | NA | NA | NA | used | NA | SHUBHAM | Yes | PREVENTIVE MAINTENANCE | 2025-02-18 12:20 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-18 12:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-18 12:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-12 12:39 | 2025-02-05 |  |  |  |  | BMOU9784137 |  |  |  | Daikin | -10*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1800KPA | 10.1/10.2/10.1 | 405/406/406 | Not done | NA | NA | No | https://drive.google.com/open?id=1RWPqJ3F2O4cWxE4xnCpbTWpWYZa8Z8AT, https://drive.google.com/open?id=1bklzDW_W6yy0jS2Oe6unwXSNpU582fgE |  |  | TRIP072 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB037/25 | 2025-02-12 17:35 | service@crystalgroup.in | Reliance Kerala | Azif FM | 9048807412 | Technician | CICU2094089 | Compressor Contactor Burn | Chaitanya Mankar | NA | Kerala | Running with issues |  |  |  | 2025-02-12 17:47 | service@crystalgroup.in | Reliance Kerala | CICU2094089 | 10 ft reefer | TK MP 4000 | SERVICE-AT SITE | LEASE | FOC | Compressor Contactor Burn | Need to Replace Compressor Contactor 25 A | 1) TK Compressor Contactor 25 A 1 Nos 2)Mantrap Hooter 1 Nos 3)Transformer 1 Nos | Yes | Compressor contactor Burn | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB037 | Thermoking | Magnum Plus | E0GM029804 | ABC782800321480241 | NA | BrandNew | NA | VIRENDRA | Yes | Compressor Contactor Burn | 2025-02-20 10:50 | service@crystalgroup.in | NO | [9 empty] | 2025-02-22 12:13 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-26 11:06 | service@crystalgroup.in | NO | [7 empty] | 2025-03-10 16:17 | 2025-03-10 |  |  |  |  | CICU2094089 |  |  |  | Thermo king | -25 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19 bar | 9.9/9.8/9.9 | 407/406/407 | Full | Compressor faulty | Replaced compressor in Waranty by vandor Mr. Sharad | No | https://drive.google.com/open?id=10hSbeknTDzparLpwHbhvFxoJJhbZXMHh, https://drive.google.com/open?id=1TLEzSeFl342PS1zgraofIR8HMSsedjM- |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB038/25 | 2025-02-13 15:04 | service@crystalgroup.in | HETERO UNIT 3 | Mahindra Jedimetla | ‎+91 63096 52982 | Manager | CXRU1326276 | Installation and Handover | Chaitanya | NA | Hyderabad | Installation |  |  |  | 2025-02-15 14:35 | crm@crystalgroup.in | Hetro Unit 3 | CXRU1326276 | 40FT STD RF | Carrier Primeline | INSTALLATION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB038 | Carrier | Primeline | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | Installation and Handover | 2025-02-15 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-18 12:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-18 12:03 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 19:45 | 2025-02-13 |  |  |  |  | CXRU1326276 |  |  |  | Carrier | +5 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/200 psig | 10.8/10.9/10.8 | 408/407/408v | Short | ATTENDED FOR : IQ TEST - INSTALATION QUALIFICATION TEST & BASIC TRANING FOR USER & IQ OFFICER. | IQ TEST - COMPLITED , WITH BASIC TRANNINGDONE AND SHOW TO STAGF OOERANAL FUNCTION AND REEFER PARTS ACKNOWLEDGE FOR IQ TEST. SHORT PTI DONE & UNIT MAIN TEMP. IQ COMPLITED AND HANDED OVER FOR NEXT TEST. | No | https://drive.google.com/open?id=1sfHdHeNQAN5r0bAloA2O6fa1L_MhPI5k, https://drive.google.com/open?id=1SJSGT4hzugYZbmIhiAOy6mP0y34Ui33f, https://drive.google.com/open?id=19xrkdGxMekvUzpV38VZMgC85u6X-wfJp, https://drive.google.com/open?id=1-oBmEtWs84_VZpSGiPRCmDc7CqXsGLbN |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB039/25 | 2025-02-13 15:05 | service@crystalgroup.in | HETERO UNIT 3 | Mahindra Jedimetla | ‎+91 63096 52982 | Manager | CXRU1550769 | Installation and Handover | Chaitanya | NA | Hyderabad | Installation |  |  |  | 2025-02-15 14:37 | crm@crystalgroup.in | Hetro Unit 3 | CXRU1550769 | 40FT STD RF | Carrier - Primeline | INSTALLATION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB039 | Carrier | Primeline | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | Installation and Handover | 2025-02-15 14:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-18 12:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-18 12:03 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-13 21:46 | 2025-02-13 |  |  |  |  | CXRU1550769 |  |  |  | Carrier | +5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/250 | 10.2/10.1/10.2 | 407/408/407 V | Short | HETRO UNIT -III , CONTAINER ATTENDED FOR IQ- TEST / INSTALATION QUALIFICATION TEST AND BASIC TRANNING FOR STAFF WITH IQ OFFICER | IQ TEST COMPLITED. WITH BASIC TRANNING, CHECKED UNIT OPERATION , ALL PARTS VOMPENTS WITH IQ OFFICER, UNIT MAINTANING SET TEMP. AND HANDED OVER FOR NEXT QUALIFICATION. | No | https://drive.google.com/open?id=1uooidllukQyRiQPPPdK_odQzWogFzWAc, https://drive.google.com/open?id=1-ag9MxTIiuZ4OnVj5Hw5Bt_MLefHmMaM, https://drive.google.com/open?id=1luk937cZHUY8A71uoZeN2oYuCcpTRIiL, https://drive.google.com/open?id=1XdEpSpgqh1JD7CWj1fR6Ob3lbGpJArQS |  |  | 71 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
FEB040/25 | 2025-02-14 10:37 | crm@crystalgroup.in | Ajinomoto Bio Pharma | S.HARSTA | 8924660331 | NA | BMOU9766180 | Compressor not working | Chaitanya | ramesh.v@in.ajibio-pharma.com | Vishakapatnam | Running with issues |  |  |  | 2025-02-15 17:31 | service@crystalgroup.in | Ajinomoto Bio | BMOU9766180 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Supply return ,Ambient ,Inlet ,Outlet sensor issue, Decos 3iF controller suspectead | Need to replace all sensors .if issue not resolved need to replace controller also. | Temp Sensor 6 Nos Decos 3iF controller | Yes | Sensor Failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB040 | Daikin | NA | NA | NA | Decos 3iF | used | NA | VIRENDRA | Yes | Compressor not working | 2025-02-18 18:11 | service@crystalgroup.in | YES | FEB067 | 2025-02-18 | Spares | AJINOMOTO BIO | Vishakhapatnam | BMOU9766180 | SITE | FOC | DAIKIN | 2025-02-18 18:12 | service@crystalgroup.in | YES | FEB067 | YES | https://drive.google.com/open?id=1OGaPHCdRx0SYwvgl63CeIk-ApAeivPDL |  | 2025-02-28 12:49 | service@crystalgroup.in | YES | 1967-02-01 | Virendra
FEB042/25 | 2025-02-17 10:59 | service@crystalgroup.in | RELIANCE kamaspura | VEER SHING | 9813816264 | Supervisor | TRIU6618391 | LEAKAGE FROM FILTER DRIER , SUPLLY & RETURN SENSOR & DEFROST SENSOR FOR SPEARE | VIRENDER | deepak91.singh@ril,com | Kamaspura, Haryana | Complete Breakdown |  |  |  | 2025-02-17 11:36 | service@crystalgroup.in | RELIANCE kamaspura | TRIU6618391 | 20 ' FT REEFER | CARRIER THINE LINE | SERVICE-ON CALL | LEASE | FOC | LEAKAGE FROM FILTER DRIER , SUPLLY & RETURN SENSOR & DEFROST SENSOR FOR SUSPECTED | need to replaced filter drier & gas charged 5 KGS | SUPPLY SENSOR 2NOS,RETURN SENSOR 1, DEFROST SENSOR 1 , FILTER DRIER 1 & GAS R134a 5 KGS .. | Yes | A filter drier leakage problem can occur due to a clogged filter drier, which happens when contaminants like moisture, dirt, or debris accumulate within the desiccant material, restricting refrigerant flow and potentially causing leaks at the seals or casing due to increased pressure build-up. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB042 | DUAL | CARRIER THINE LINE | NA | NA | NA | USED | NA | VIRENDRA | Yes | LEAKAGE FROM FILTER DRIER , SUPLLY & RETURN SENSOR & DEFROST SENSOR FOR SPEARE | 2025-02-20 11:00 | service@crystalgroup.in | YES | Feb070 | 2025-02-20 | Spares, FOC | RELIANCE kamaspura | Kamaspura | TRIU6618391 | SITE | FOC | CARRIER-THINLINE | 2025-02-22 11:50 | service@crystalgroup.in | YES | FEB071 | NO |  |  | 2025-02-22 11:52 | service@crystalgroup.in | YES | FEB071 | Service Taken By Local Supplier Om Sai Refrigeration | [5 empty] | 2025-02-22 12:03 | 2025-02-21 |  |  |  |  | TRIU6618391 |  |  |  | Carrier | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Discharge 18 Bar | 9.5/9/10 | 408/410/410 | Not done | Alarm Al 52 coming ,need to replace Supply Sensor ,Compressor Running in Bypass Mode |  |  | https://drive.google.com/open?id=1JrlVllSNoqOLOuENEaZOaFc3fxeD5Otp, https://drive.google.com/open?id=1cEw4tCocJ-Hui0h1twTtgRz4v-PTTZLg, https://drive.google.com/open?id=1COjXRpb89gQFLk4u_gmiGhBncAWVDQ5Y, https://drive.google.com/open?id=197ITKilbVCS5ZYcmJ0WxZE57fM1Qq1-m |  |  | NA | Yes | Yes | Urgent | Need to Replace Supply Sensor and Compressor | Supply Sensor 2 Nos Compressor 1 Nos Suction and Discharge Gasket 2 Nos Compressor Oil 3 Ltr | service@crystalgroup.in | REEFER
FEB043/25 | 2025-02-18 18:35 | service@crystalgroup.in | Transy Global | Venkat | 9703736718Manager | Manager | TITU8259378 | ALARM CODE VISIBLE | Shahabuddin | NA | Hyderabad | Running with issues |  |  |  | 2025-02-18 18:39 | service@crystalgroup.in | Transy Global | TITU8259378 | 20FT Spl RF with Wheels | Thermoking MP-4000 | SERVICE-ON CALL | LEASE | FOC | Supply Sensor Alarm on display | Need to Replace 1 Nos Supply Sensor | Supply Sensor 1 Nos | Yes | Supply sensor failure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB043 | Thermo King MP-4000 | MP 4000 | NA | NA | MP4000 3.5 | Used | NA | SHAHBUDDIN | Yes | ALARM CODE VISIBLE | 2025-02-19 11:54 | service@crystalgroup.in | YES | Feb068 | 2025-02-19 | Spares, FOC | Transy Global | Hyderabad | TITU8259378 | SITE | FOC | TK-MP4000 | 2025-02-19 11:55 | service@crystalgroup.in | YES | Feb068 | NO |  |  | 2025-02-24 13:07 | crm@crystalgroup.in | YES | Feb068 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-02-19 12:05 | 2025-02-19 |  |  |  |  | TITU825938 |  |  |  | Thermo king | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 bar and 19 bar | 9.9/9.8/9.9 | 413V/410V/412V | Not done | Unit Temp Issue Supply sensor alarm | On Call Suggested To clean formed ICE on floor .After cleaning Issue resoled and container working properly. | Yes | https://drive.google.com/open?id=1nzAUbCJZ0xt_9JUgpSHD_2OEgMZEx03y, https://drive.google.com/open?id=12J6YJkZNSmT3wG7q08iUjUEUpsy-fIGq |  |  | NA | No | Yes | Can be done on next PM | NA | MP TK-MP4000 Supply Sensor 1 Nos | service@crystalgroup.in | REEFER
FEB044/25 | 2025-02-20 11:28 | crm@crystalgroup.in | ARAI & Chennai | Pranab D | 9284545994 | Deputy manager | CCLU1036545 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa | Pranab.vel@araiindia.com | Chennai | Running with issues |  |  |  | 2025-02-25 17:26 | service@crystalgroup.in | ARAI & Chennai | CCLU1036545 | NA | Carrier Thenline | SERVICE-AT SITE | LEASE | CHARGEABLE | Condensor Coil Leakage Issue | Need to Carriy N2 Test ,Braising Set,O2,LPG,Brazing Rod,Vaccum Pump | N2 Brazing Set O2 LPG N2 Brazing Rod Vaccume Pump | Yes | Leakage from Container | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB044 | NA | Thinline | NA | NA | NA | Used | NA | LOcal Supplier | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-03-10 11:00 | tender@crystalgroup.in | YES | MAR005 | 2025-03-10 | Spares | ARAI & Chennai | Chennai | CCLU1036545 | SITE | FOC | CARRIER-THINLINE | 2025-09-30 16:49 | crm@crystalgroup.in | YES | MAR005 | NA |  | Stock | 2025-09-30 16:51 | crm@crystalgroup.in | NO
FEB045/25 | 2025-02-20 13:10 | crm@crystalgroup.in | Aspiro pharma ltd | Gatturayudu | 9100980301 | Purchase | CAIU5422720 | SPARES required | Pushpa | RohanKumar.Y@aspiropharma.com | Hyderabad | Running with issues |  |  |  | 2025-03-05 12:04 | crm@crystalgroup.in | Aspiro Pharma | CAIU5422720 | 40FT STD RF | 2008 | REPAIR | LEASE | FOC | NA | Filter Drier to be replaced Gas top up required | Filter Drier | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB045%2F25 | DAikin | DAikin | NA | NA | NA | Used | JSGA622340482 | RAMIZ | Yes | SPARES required | 2025-03-05 12:08 | crm@crystalgroup.in | YES | MAR002 | 2025-03-05 | FOC | Aspiro Pharma | Hyderabad | CAIU5422720 | SITE | FOC | DAIKIN | 2025-03-05 12:20 | crm@crystalgroup.in | YES | MAR002 | YES |  |  | 2025-03-05 12:20 | crm@crystalgroup.in | YES | MAR002 | TECHNICIAN |  |  | RAMIZ |  |  | 2025-02-27 21:01 | 2025-02-27 |  |  |  |  | CAIU5422720 |  |  |  | Daikin | +4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1/12.1bar | 10.1/10.2/10.1 | 386/387/386 | Not done | filter drier pipe flir damaged & contaminated gas r134a. al f803 & f809 | cut the old flir & created a new & replaced filter drier with new one & vacuum done & gas charge R134a 5 kgs . still under observation 24 hrs | No | https://drive.google.com/open?id=1W38HnyRopN35JKZIcAAzeKwz3JKYOMoM, https://drive.google.com/open?id=1t2-YjQFqr8FT-OFXNNeJCoCfDqXjGjcn |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
FEB046/25 | 2025-02-20 16:54 | crm@crystalgroup.in | Cliantha Research Ltd | Sunil Prajapati | 9870010619 | NA | CICU1938267 | Preventive Maintenance | Chaitanya | NA | Ahmedabad | Preventive Maintenance |  |  |  | 2025-02-21 09:59 | crm@crystalgroup.in | Cliantha Research Ltd | CICU1938267 | 20FT Super RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | SALE | AMC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB046 | Thermoking MP-4000 | MP 4000 | NA | NA | NA | Brand New | NA | RAJ KUMAR | Yes | Preventive Maintenance | 2025-02-21 10:00 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-21 10:00 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-21 10:01 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-21 10:05 | 2025-02-20 |  |  |  |  | CICU1938267 |  |  |  | Carrier | -21*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -0.003125 | 11.2/11.2/11.9 | 411/411/411 | Not done | NA | NA | No | https://drive.google.com/open?id=1RYz6Vh-sHAdJcGVAyc_gyLi3qrLUM369, https://drive.google.com/open?id=1vpKqLDDgboNNLjiGM8cPkQMJEoJNZ9vv |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB047/25 | 2025-02-24 12:31 | crm@crystalgroup.in | Navin Fluorine | Ketan | 6357662623 | NA | CCLU1031878 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Raj Kumar | vatsal.rajani@nfil.in | Dhej | Running with issues |  |  |  | 2025-02-24 12:40 | crm@crystalgroup.in | Navin Fluorine | CCLU1031878 | 20FT | Carrier - Thinline | SERVICE-AT SITE | LEASE | FOC | Container not cooling down | Filter drier needs to replaced | Filter drier | Yes | Filter drier needs to replaced | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB047 | NA | Thinline | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-02-24 12:43 | crm@crystalgroup.in | YES | FEB072 | 2025-02-24 | Spares | Navin Fluorine | Dhej, Bharuch | CCLU1031878 | SITE | FOC | CARRIER-THINLINE | 2025-02-24 13:01 | crm@crystalgroup.in | YES | FEB072 | YES | https://drive.google.com/open?id=1TBYZddfoqdeiyD0JZI2nv47m8UTEBHt5 |  | 2025-02-24 13:02 | crm@crystalgroup.in | YES | FEB072 | ARRENGING AT SITE | [5 empty] | 2025-03-10 16:04 | 2025-03-09 |  |  |  |  | CCLU1031878 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/200 PSIG | 13.1/13.2/13.1 | 430/429/228 | Short | Staper motor stakup mot working | Replaced staper motor .vaucm system . Gas charging run unit obs | No | https://drive.google.com/open?id=1fmxlFRUw0-u2SVwNLqDnya2S91oWKEED, https://drive.google.com/open?id=1ze6RWRkfWRFsu21dcaRCjwKzc0CR6g6v |  |  | 77 | No | No | Can be done on next PM | Container wromg Instalation need to keep way drm wall 2/3 meter | NA | technician@crystalgroup.in | REEFER
FEB048/25 | 2025-02-24 18:56 | crm@crystalgroup.in | Transys Global Forwarding Private Limited | SriRangamadh | 9703736718 | Asst. Manager | TITU825937 | REPAIRS & REPLACEMENT | Pushpa | venkata.sriranganath@tgfworld.com | Shamshabad | Running with issues |  |  |  | 2025-03-08 10:43 | technician@crystalgroup.in | Transys Global Forwarding Private Limited | TITU8259378 | 20" | TK MP 4000 | SERVICE-ON CALL | LEASE | FOC | Temp. Issue with Display faded | Advise to clean ice from bottam | TK MP 4000 DISPLAY & DOOR ONLY | Yes | Frosting inside bottam area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB048%2F25 | THERMOKING | Tk MP 4000 | EOG1000179 | NA | NA | Used | NA | SHAHBUDDIN | No | REPAIRS & REPLACEMENT | 2025-03-19 15:58 | tender@crystalgroup.in | YES | MAR014 | 2025-03-19 | Spares | Transys Global Forwarding Private Limited | Hyderabad | TITU8259378 | SITE | FOC | TK-MP4000 | 2025-03-29 12:04 | tender@crystalgroup.in | NO |  |  |  |  | 2025-04-02 11:49 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-19 09:55 | 2025-03-18 |  |  |  |  | TITU8259378 |  |  |  | Thermo king | -22.C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1,7 / 16.5 bar | 8.6/8.6/8.6 | 407/408/407 | Not done | Display defective , key pad defective ,key pad logo defective , supply & return temperature sensor defective | need to replaced all the spares asap | Yes | https://drive.google.com/open?id=1qBQNv5tgHXLqYIDFvA7iPjOr1SMOTTiG, https://drive.google.com/open?id=1w9Qt-C-C5GwAtaysT4vikpDa3o-fdzGd |  |  | 76 | Yes | Yes | Urgent | all spares need to replace | 1)display , 2)key pad , 3)key pad logo , 4)temperature sensor 2 nos | service@crystalgroup.in | REEFER
FEB049/25 | 2025-02-25 12:43 | crm@crystalgroup.in | Qwik Supply | NA | NA | NA | HDMU5499131 |  |  | NA | Nagpur | Preventive Maintenance |  |  |  | 2025-02-26 12:08 | service@crystalgroup.in | Qwik Supply | HDMU5499131 | 40FT STD RF | Daikin 3D | SERVICE-AT SITE | LEASE | FOC | NA | NA | NA | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB049 | Daikin | Daikin | NA | NA | 3D | Used | NA | VIRENDRA | No |  | 2025-02-26 12:10 | service@crystalgroup.in | NO | [9 empty] | 2025-02-26 12:11 | service@crystalgroup.in | NO |  |  |  |  | 2025-02-26 12:11 | service@crystalgroup.in | NO | [7 empty] | 2025-02-26 12:16 | 2025-02-24 |  |  |  |  | HDMU5499131 |  |  |  | Daikin | NA | Dirty | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | Container is OK checked physically | Inspected container and and found Physically OK | No | https://drive.google.com/open?id=1ViQgZJJ9ps24WU_R4fBiTWDMRg0JkdiV |  |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB050/25 | 2025-02-25 12:45 | crm@crystalgroup.in | Qwik Supply | NA | NA | NA | MYRU4518166 |  |  | NA | Nagpur | Preventive Maintenance |  |  |  | 2025-02-26 16:34 | crm@crystalgroup.in | Qwik Supply | MYRU4518166 | 40FT STD RF | Carrier - Thinline | MACHINE INSPECTION | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB050 | Carrier - Thinline | Thinline | NA | NA | NA | Used | NA | VIRENDRA | Yes |  | 2025-02-27 10:45 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-27 10:46 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-27 10:58 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-27 11:09 | 2025-02-24 |  |  |  |  | MYRU4518166 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | NA | Not done | Container inspection completed and found power plug missing, T floor net to wash, hole inside RIS door ,condesor coil dirty | Compressor rusted to be painted | Yes | https://drive.google.com/open?id=1ERO1XdC3v4EVF5u4J-Rz-CageWV-sLA9 |  |  | TRIP075 | No | No | Can be done on next PM | NA | Power Plug *1 Expansion Valve *1 N2 Test Vaccum Brazing Set 1 R134a gas 5.2kg | crm@crystalgroup.in | REEFER
FEB051/25 | 2025-02-26 10:20 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site In charge | PRGU4958724 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Sahil | murthy.ss@lauruslabs.com | Vishakapatnam | Complete Breakdown |  |  |  | 2025-03-08 22:43 | service@crystalgroup.in | Laurus unit 2 | PRGU4958724 | 40 reefer | carrier thne line | SERVICE-AT SITE | LEASE | FOC | condenser fan defective & htt defective & fues burn 7.5 amps 1 nos condenser fan motor noise | replaed condenser fan motor new. | EVP MOTOR CONDENSOR FAN BLADE ML 3 CONTROLLER | Yes | HTT SHORT circuit & motor bearing risted | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB051%2F25 | reefer carrier | thine line | na | na | ok | used | na | VIRENDRA | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-03-25 15:31 | tender@crystalgroup.in | YES | MAR016 | 2025-03-25 | Spares | LAURUS SYNTHESIS UNIT 2 | Vishakapatnam | PRGU4958724 | SITE | FOC | CARRIER-THINLINE | [17 empty] | 2025-03-05 21:14 | 2025-03-05 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Noisy | Clean | Need to replace | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/a 13.8B | 10.0A 9.7A 9.9A | 386V 385V 387V | Not done | We have attend this unit and found condenser capecatior df, condenser motor create heavy noise, r/S EVP motor low speed fail and burn, HTT df to replace, fuse burn 7.5A2nos and gas less 2kg | Replace condenser motor capecatior | Yes | https://drive.google.com/open?id=1h7ds2ODWB6-CuyOzmOwgpx3nSPI52Ilc, https://drive.google.com/open?id=1Nse38g6jExB26bjcUPxdmdmLuHQd_5Bk |  |  | Trip no 077 | Yes | No | Urgent | Evp motor 1nos HTT 1NOS CONDENSER MOTOR 1NOS FUSE 7.5A 2 NOS GAS 2KG R-134a | Evp motor 1nos HTT 1NOS CONDENSER MOTOR 1NOS FUSE 7.5A 2 NOS GAS 2KG R-134a | viru0068@gmail.com | REEFER
FEB052/25 | 2025-02-26 10:33 | crm@crystalgroup.in | DSV Solutions Pvt Ltd | SAGAR | 9030909007 | NA | TITU8258978 |  |  | somnath.shewale@dsv.com | Kompally | Preventive Maintenance |  |  |  | 2025-02-26 10:58 | crm@crystalgroup.in | DSV Solutions | TITU8258978 | 20FT Spl RF | Thermoking MP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB052 | Thermoking MP-4000 | MP 4000 | 13E7843FT | EOG1000178 | NA | Used | NA | RAMIZ | No |  | 2025-03-18 17:21 | tender@crystalgroup.in | YES | MAR013 | 2025-03-18 | Spares | DSV Air & Sea Pvt. Ltd. | HYDERABAD | TITU8258978 | SITE | FOC | TK-MP4000 | 2025-02-26 11:14 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-26 11:15 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-26 21:02 | 2025-02-26 |  |  |  |  | TITU8258978 |  |  |  | Thermo king | -32C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5 /16 BAR | 8.6/8.7/8.6 AMPS | 411/412/411 | Not done | CONDENSER COIL DIRTY & DISPLY DEFECTIVE & KEYPAD LOGO DAMAGED | CLEAN CONDENSER COIL WITH FRESH WARER . REPLACED DIAPLY WITH GOOD ONE & KEY PAD LOGO REPLACED WITH NEW ONE , | No | https://drive.google.com/open?id=15sjgPA_hCT8dRnc8PsyRkmERNW0Y8Sxr, https://drive.google.com/open?id=1cSgq07YU-__7Zy7fX2KPDUgqBMzakwLE |  |  | 76 | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
FEB053/25 | 2025-02-27 13:07 | crm@crystalgroup.in | Reliance Surat | Sandip Parmar | 7984081490 | NA | APRU5066497 |  |  | NA | Surat | Preventive Maintenance |  |  |  | 2025-02-27 15:01 | crm@crystalgroup.in | Reliance Surat | APRU5066497 | 40FT STD RF | Carrier - Thinline | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB053 | Carrier - Thinline | Thinline | NA | NA | NA | NA | JSGA623040296 | RAJ KUMAR | Yes |  | 2025-02-27 15:04 | crm@crystalgroup.in | NO | [9 empty] | 2025-02-27 15:10 | crm@crystalgroup.in | NO |  |  |  |  | 2025-02-27 15:10 | crm@crystalgroup.in | NO | [7 empty] | 2025-02-27 15:30 | 2025-02-26 |  |  |  |  | APRU5066497 |  |  |  | Carrier | -21*C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | /12.2 | 14.8/14.8/14.6 | 406/405/406 | Not done | Condensor coil normal dirty | Condensor coil cleaned, LIS Door gas kit refix 8ft | No | https://drive.google.com/open?id=1KMjG9F1Wssnwv09-g2fdrbu-rShayBkr, https://drive.google.com/open?id=1UKk2xcogCkPs_uo318IuQVgLOVsDTyFP |  |  | TRIP073 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
FEB054/25 | 2025-02-28 16:26 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Srinivas | 7981717737 | NA | CXRU1030387 | Compressor defective | Pushpa | plasma.projects@hetero.com | Hyderabad | Running with issues |  |  |  | 2025-02-28 17:17 | service@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Winding Grounded | Need to Replace Compressor ,Clean Floor and need to keep Material in Pelletized way. | 1)Compressor 2)N2 Test 3)R134A Gas 4 KG 4)Compressor Oil | Yes | Suspected Insufficient Air Flow due to Ice Formation on T Bar and Material is Not pelletised | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB054%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | Na | RAMIZ | Yes | Compressor defective | 2025-05-06 17:22 | crm@crystalgroup.in | NO | [26 empty] | 2025-02-28 22:46 | 2025-02-28 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -25'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | 401/402/401 | Not done | FOUND COMPRESSER GROUNDED & ICE FOUNDATION ON T BAR FLOOR DUE TO THIS IN SUFFICENT AIR FLOW IN SYSTEM & CARGO AREA | NEED TO REPLACE COMPRESSOR & NEED TO CLEAN TBAR FLOOR & NEED TO KEEP PALLATS FPR BETTER AIR CIRCULATION BOTH MACHINE . | Yes | https://drive.google.com/open?id=1Nz_b1QHYg3DiCRq8T-KyxRSG7QWT4vtK, https://drive.google.com/open?id=1G4EDxNONK8OpgNLA41WGDUV0tONsy-VT |  |  | 76 | Yes | Yes | Urgent | NEED TO FIX COMPRESSOR | 1)COMPRESSSOR 2)R134a 6 KGS 3)FILTER DRIER 4)FUSE 10 AMPS 1 NOS 5)N2 6)SUCATION GAS KET 7)DISCHARGE GAS KET 8)VACUUM PUMP 1 HP FOR VACUUM | service@crystalgroup.in | REEFER
FEB055/25 | 2025-02-28 16:28 | crm@crystalgroup.in | Reliance Bhopal | Ram Babu | 7869533375 | NA | MYRU4515188 | Compressor issue | Psuhpa | dipak.verma@qwik.co.in | Bhopal | Complete Breakdown |  |  |  | 2025-02-28 17:25 | service@crystalgroup.in | Reliance Bhopal | MYRU4515188 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp Fluctuation observed | Need to Replace Evaporator Motor ,PT/CT Board, Compressor Contactor and if required compressor also need to be replaced (Suspected) | 1)Evaporator Motor 2)PT/CT Board 3)Compressor Contactor 4)Compressor (Suspected) 5)Brazing set 6)R134A Gas | Yes | Suspectead Evaporator Motor and PT/CT board Failure .Also Compressor Is Heavy Noicy | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=FEB055%2F25 | Daikin | Daikin | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | Compressor issue | 2025-03-03 18:46 | crm@crystalgroup.in | YES | FEB005 | 2025-03-03 | Spares | Reliance Bhopal | Bhopal | MYRU4515188 | SITE | FOC | DAIKIN | 2025-03-10 16:45 | crm@crystalgroup.in | YES | FEB005 | YES |  |  | 2025-03-15 15:02 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-05 17:15 | 2025-03-05 |  |  |  |  | MYRU4515188 |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Need to replace | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Need to replace |  | Need to replace | Okay | Need to replace | Not done | Clean |  | NOt working | 416 /405/406))) | NOT WORKING | Not done | Found compressor internal damaged & Noisy and both Evaprator motor stkup& oil trace on liquid value. | Need to replaced complit carrier unit for good working at this location | No | https://drive.google.com/open?id=1T-3-npQKg7lPztwBovGPrEcCTcCIAIgc, https://drive.google.com/open?id=1tCAvp8CxEtQkigm5sE57WrVn-FgZTFs3 |  |  | NA | Yes | Yes | Urgent | Need to replaced complit unit | NA | technician@crystalgroup.in | REEFER
MAR001/25 | 2025-03-01 17:42 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Srinivas | 7981717737 | NA | CXRU1030387 | REPAIRS & REPLACEMENT, Need to replace Compressor | Sahil | plasma.projects@hetero.com | Hyderabad | Complete Breakdown |  |  |  | 2025-03-03 14:48 | crm@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | DAikin | Breakdown | LEASE | FOC | Compressor winding grounded, insufficient gas , Ice formation | Need to replace Compressor, top up gas | Compressor 1 Filter Drier 1 Suction Gas Kit 1 Discharge Gas Kit 1 R134a gas 6kg Nitrogen 1 Vaccum Pump 1 HP 1 | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR001%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | NA | RAMIZ | Yes | REPAIRS & REPLACEMENT, Need to replace Compressor | 2025-03-03 14:52 | crm@crystalgroup.in | YES | MAR001 | 2025-03-03 | Spares | HETERO PLASMA | Hyderabad | CXRU1030387 | SITE | FOC | DAIKIN LXE10E | 2025-03-18 16:23 | tender@crystalgroup.in | YES | MAR001 | YES | https://drive.google.com/open?id=1e5NDp9r-rgEIp-oRTnXVAIMjL53a7l_P |  | 2025-04-02 11:45 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-04-07 13:42 | 2025-04-03 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -25.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 149KPA 88KPA 1685KPA 1321KPA | 9.6A 10.0A 9.3A 9.7A 9.5A 9.9A | 387V 385V 389V | Not done | We have found compressor df due to ground | Compressor replaced, fillter Drier replace, compressor oil 3ltr, N2 test vacuum and gas charge R-134a 5kg container run in sound condition without any Alaram and maintain required temperature | No | https://drive.google.com/open?id=1g1UoaVeMswd0r1lvhORoIH1LGipC7Cdp, https://drive.google.com/open?id=1VQGG2JaVBEcMKq4sCegFv_U8nAW2ivmJ |  |  | Trip no 080 | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
MAR002/25 | 2025-03-04 12:33 | crm@crystalgroup.in | RELIANCE | Mark / Anbu | 77188 81734 ¦ 90040 43704 | NA | CGMU2991679 | ALARM CODE VISIBLE | Pushpa | mark.Silveira@ril.com / anbu.EZHILAN@ril.com | Jamnagar Gujarat | Running with issues |  |  |  | 2025-03-11 03:43 | service@crystalgroup.in | Reliance - Jamnagar | CGMU2991679 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | condenser fan contactor 12 defectives ,al 58 & al 72 & al 74 | need to replaced contactor 12 amps | contactor 12 amps HP switch suspected | Yes | electrical overload, arcing, overvoltage, high surge voltages, frequent cycling, poor wiring, and environmental factors like dirt, dust, or moisture. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR002%2F25 | Carrier - Thinline | Thinline | ok | ok | ok | Refurbished | a | RAJ KUMAR | Yes | ALARM CODE VISIBLE | 2025-03-31 16:30 | tender@crystalgroup.in | YES | MAR026 | 2025-03-31 | Spares | Reliance-Jamnagar | Jamnagar | CGMU2991679 | SITE | FOC | CARRIER-THINLINE | 2025-04-01 12:52 | tender@crystalgroup.in | YES | MAR026 | YES |  |  | 2025-04-02 11:52 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-28 17:01 | 2025-03-27 |  |  |  |  | CGMU2991679 |  |  |  | Carrier | -16'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-1.2bar, dis-14.6bar | R11.8, B-11.9. Y-11.8 | L1-414. L2-415. L3-414 | Short | We have attende tha unit found condenser coil havy durty and keypad not working and supply sensor failure | We have work condenser coil wash with normal water and supply sensor replace and keypad replace after unit running sound condition | No | https://drive.google.com/open?id=1nxDIia5TLxJd_hSNiCVRHvjrW1xk5id8, https://drive.google.com/open?id=1OnbgrrgtAVGIG9wpcCIi3g4oyz914Ri4 |  |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAR003/25 | 2025-03-04 17:16 | crm@crystalgroup.in | Eugia Steriles Private Limited | Harikrishna | 9000478929/7981991169 | NA | CICU2093987 | FLUCTUATIONS IN TEMEPRATURE, supply temp too high compared to return | Pushpa | Harikrishna.gunda@eugiapharma.com /deepakraju.Kolukuluri@eugiapharma.Com | Vishakapatnam | Running with issues |  |  |  | 2025-03-05 16:50 | technician@crystalgroup.in | Eugia Steriles Private Limited | CICU2093987 | 40FT STD RF | THERMOKING | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Unit need to manual Defrost with duty person advise producers | On duty Engineer advance for manual Defrost pro | NA | No | Defrosting issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR003%2F25 | Thermoking | Magnum Plus | E0GM029791 | ABC782800321460084 | NA | BrandNew | NA | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE, supply temp too high compared to return | 2025-03-27 10:34 | tender@crystalgroup.in | NO | [9 empty] | 2025-03-27 10:35 | tender@crystalgroup.in | NO |  |  |  |  | 2025-04-25 16:41 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-25 16:41 | 2025-04-23 |  |  |  |  | CICU2093987 |  |  |  | Thermo king | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .2/18 bar | 9.8/9.9/9.8 | 405/406/406 | Short | Unit temp. Issue . Check & found gas leakage from filter Drier. | Leakage stop. And adding Freon Gas R 404a to system & observation .unit working as satisfactory & maintain set temp. | No | https://drive.google.com/open?id=1hX5IGkSy0sf9ai0UZscrcuPdTBlAlFQq, https://drive.google.com/open?id=11ebRy8cvL8yDJfQF2O93qaOQUeWvZdhO |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR004/25 | 2025-03-04 17:50 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | GESU9460634 | KEYPAD NOT WORKING | Pushpa | tharunkishore.r@sailife.com | Bidar | Running with issues |  |  |  | 2025-03-07 17:41 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | GESU9460634 | 40" | Carrier | SERVICE-ON CALL | LEASE | FOC | INSTALATION DONE ✔️ WITH AL 06 KEY PAD HANGUP | Need to send through courier key pad | Carrier key pad | Yes | Carrier key pad hangup | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR004%2F25 | Carrier | Carrier | NA | NA | NA | Used | NA | SHAHBUDDIN | No | KEYPAD NOT WORKING | 2025-03-28 12:44 | tender@crystalgroup.in | YES | MAR021 | 2025-03-28 | Spares | Sai Life Science Pvt Ltd | Bidar | GESU9460634 | SITE | FOC | CARRIER-ELITLINE | 2025-04-25 11:03 | tender@crystalgroup.in | YES | MAR021 | YES | [12 empty] | 2025-04-11 12:40 | 2025-03-04 |  |  |  |  | GESU9460634 |  |  |  | Carrier | - 18 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | NA | NA | NA | Not done | AL 06. Key pad not function | Need to replaced key pad | Yes | https://drive.google.com/open?id=1HFjkmg6Wb8pnOtFwfZsiTaYduPwOKqd4, https://drive.google.com/open?id=1FSQJ_a-kaqG7yIXJPJ5zcbBFnJ-RyqXk |  |  | NA | No | No | Can be done on next PM | NA | Carrier key pad | technician@crystalgroup.in | REEFER
MAR005/25 | 2025-03-04 18:58 | crm@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | PCIU6016370 | SERVICING | Pushpa | yugandhar.s@hetro.com | Hyderabad | Running with issues |  |  |  | 2025-03-10 17:27 | service@crystalgroup.in | Hetero Unit 3 | PCIU6016370 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | found fungus on cargo dram label sticker . | need to clean evaporator coil & container internal | na | No | evaporator coil oxidized or fungus occurred | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR005%2F25 | Daikin | Daikin | A000897 | LXE10EA36A | NA | used | JSGA623040188 | RAMIZ | Yes | SERVICING | 2025-03-17 14:41 | tender@crystalgroup.in | NO | [9 empty] | 2025-03-17 14:41 | tender@crystalgroup.in | NO |  |  |  |  | 2025-07-08 16:12 | crm@crystalgroup.in | NO | [7 empty] | 2025-03-10 21:07 | 2025-03-10 |  |  |  |  | PCIU6016370 |  |  |  | Carrier | +5C | Dirty | Clean |  | Okay | Rusty | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5 & 13.1 BAR | 8.9/9.O/8.9 | 410 VPLTAGE | Not done | found fungus on cargo dram label sticker . | need to clean evaporator coil & container internal | No | https://drive.google.com/open?id=17LdzPtyaxA6naOnBOOrOdPK1lWETjMix, https://drive.google.com/open?id=1DzapBb8WgIghSabw-0WwaWhezzwxxdGY |  |  | 76 | Yes | Yes | Urgent | NEED TO REMOVE ALL CARGO FOR FUTURE PROCRESS | NA | service@crystalgroup.in | REEFER
MAR006/25 | 2025-03-06 00:59 | service@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | GAURAV GULHANE | 9145242830 | executive | MYRU4500887 | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa mam | na | Hyderabad | standby unit shout down found compressor defective |  |  |  | 2025-03-06 01:10 | service@crystalgroup.in | Hetero plasma | MYRU4500887 | 40FT | Daikin dual | SERVICE-ON CALL | LEASE | AMC | compressor noise & pumping fail | need to replaced compressor & filter drier & gas R34a & n2 & vacuumpump 1 hp | compressor , gas R134a 6 kgs & filter drier &suctions & discharge gas ket & vacuum pump | Yes | insufficient lubrication, overheating, electrical issues, contamination, restricted airflow, excessive refrigerant pressures, inadequate oil return, voltage fluctuations, | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR006%2F25 | standby | daikin | na | ok | ok | used | na | RAMIZ | Yes | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-03-10 12:23 | tender@crystalgroup.in | YES | MAR008 | 2025-03-10 | Consumables, Spares | Hetero Plasma | Hyderabad | MYRU4500887 | SITE | FOC | DAIKIN | 2025-03-12 15:31 | tender@crystalgroup.in | YES | MAR008 | YES | https://drive.google.com/open?id=1NOQQio_uZ5PJhZmkJHtw6Ky-iAH51wgD |  | 2025-04-02 11:45 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-06 01:35 | 2025-03-05 |  |  |  |  | MYRU4500887 |  |  |  | Daikin | -25C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5 /13.4bar | 10.1/10.2/10.1 amps | 401/400/401 v | Not done | compressor defective | replaced compressor with new & filter drier fixed new , n2 test for 24 hrs , vacuum done & gas charge 5 kgs R134a | No | https://drive.google.com/open?id=1p6d2FUxomy23SZqVloZkbTzexjE5OKEC, https://drive.google.com/open?id=1WakbDABihazQJntb9UlxxgZu4OgjN_41, https://drive.google.com/open?id=1X9UD7CEewxpRujLMQFR_J3SbKJZ7klB0, https://drive.google.com/open?id=18ztN4zlfu2Yrr40zlb29XKUzRDPgarFf |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR007/25 | 2025-03-06 11:20 | crm@crystalgroup.in | Symbiotec | Jitendra Malakar | 9630093361 | NA | MYRU4506360 |  |  | hvacsez@symbiotec.in | Pithampur, Madhya Pradesh | Preventive Maintenance |  |  |  | 2025-03-07 11:39 | technician@crystalgroup.in | Simbiotech Indore | MYRU4506360 | 40FT HC RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | PM SERVICE REQ BY CLINTS | PM service done | NA | No | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR007%2F25 | DAIKIN | Daikin | MFG 005137 | DECOS III | Na | USED | NA | SHAHBUDDIN | Yes |  | 2025-04-10 16:15 | tender@crystalgroup.in | YES | MAR025 | 2025-03-10 | Spares | Symbiotec | Pithampur,Madhya Pradesh | MYRU4506360 | SITE | FOC | DAIKIN | 2025-04-25 11:00 | tender@crystalgroup.in | YES | MAR025 | NA | [12 empty] | 2025-03-07 10:41 | 2025-03-06 |  |  |  |  | MYRU4506360 |  |  |  | Daikin | -10c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 8/190 | 9.9/9.8/9.9 | 407/406/407 | Short | Need to replaced filter Drier and Display cover | Unit working as satisfactory & maintaining temperature. | No | https://drive.google.com/open?id=1uV4EMnktj4UGKolmGnx8iE0O8H5wXzgq, https://drive.google.com/open?id=1QCuD4zaNM14cSXDieHlNn8-a4Ze2BhkX |  |  | 77 | No | No | Can be done on next PM | NA | Sheet key & filter Drier | technician@crystalgroup.in | REEFER
MAR008/25 | 2025-03-06 11:23 | crm@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | Jitendra Malakar | 9630093361 | NA | TRIU6632126 |  |  | hvacsez@symbiotec.in | Pithampur, Madhya Pradesh | Preventive Maintenance |  |  |  | 2025-03-07 11:42 | technician@crystalgroup.in | SIMBIOTECH | TRIU6632532 | 20" | Cartier | SERVICE-ON CALL | SALE | CHARGEABLE | PM SERVICE | Tech. On field | NA | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR008 | Carrier | Carrier | MSS60317678 | 541320 | 5178 | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-03-07 10:49 | 2025-03-06 |  |  |  |  | TRIU6632532 |  |  |  | Carrier | + 3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/195 | 12 9/12.8/12.9 | 406/407/406 | Short | Found compressor low oil. Need to adding Oil | Adding oil to compressor & spare given by simbiotec | No | https://drive.google.com/open?id=1rqwnaYp5WcLRrY1vfAy5wyHz5jHpll3C, https://drive.google.com/open?id=1NZPGdQldl7bqZmS7-nmO0ezNeaebjKQD |  |  | 77 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR009/25 | 2025-03-06 11:25 | crm@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | Jitendra Malakar | 9630093361 | NA | TRIU6632532 |  |  | hvacsez@symbiotec.in | Pithampur, Madhya Pradesh | Preventive Maintenance |  |  |  | 2025-03-07 11:46 | technician@crystalgroup.in | Simbiotech Indore | TRIU6632126 | 20" | Carrier | SERVICE-ON CALL | SALE | CHARGEABLE | PM SERVICE | Tech. On field | NO | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR09%2F2025 | Carrier | Thin line 541-320 | MSS60317716 | 541320 | 5176 | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-03-07 10:58 | 2025-03-06 |  |  |  |  | TRIU6632126 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/200 | 13/12.9/13 | 408/407/408 | Short | Need to replaced compressor contactor it's not matching or high Amp. | Unit working as satisfactory | Yes | https://drive.google.com/open?id=1Xg64YPPaDIenxRXuQEgGJuArE8qdtxln, https://drive.google.com/open?id=1ZKRNxJBICBM3vPpPVrxgxc7hp7Mx7ZDi |  |  | 77 | No | No | Can be done on next PM | NA | Compressor contactor 25 AM | technician@crystalgroup.in | REEFER
MAR010/25 | 2025-03-06 18:17 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | NA | NA | CICU1799140 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Running with issues | PCM pads not freezing |  |  | 2025-03-11 03:32 | service@crystalgroup.in | Qwik Supply | CICU1799140 | 10 ft blast | THERMO KING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | need to up lode latest software , for leakage need to visit | software card lp switch temperature sensor return temperature sensor supply filter drier gas 404A 5 kgs vacuum pump | Yes | software or less gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR010%2F25 | 10 FT BLAST REEFER | THERMOKING MP 4000 | OK | OK | OK | BRAND NEW | NO | VIRENDRA | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-04-01 11:48 | operation@crystalgroup.in | YES | MAR027 | 2025-03-31 | Consumables, Spares | Qwik Supply | Rajpura | CICU1799140 | SITE | FOC | TK-MP4000 | 2025-04-28 10:42 | operation@crystalgroup.in | YES | MAR027 | YES |  |  | 2025-05-17 12:06 | qualitycontrol@crystalgroup.in | YES | MAR027 | COURIER | 16530089170 | blue dart |  | https://drive.google.com/open?id=1I27T4sF6wlrg7rCsZPRKV2REX1tdPod8 |  | 2025-07-08 17:48 | 2025-06-09 |  |  |  |  | CICU1799140 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 26.2 | 14.1 / 13.9/14 | 399/401/400 | Short | NA | Unit under observation | No | https://drive.google.com/open?id=1lXAEM43ZL6lxbDbcnNYmwvZOfUlnuWVl | https://drive.google.com/open?id=1_Fy70aQ980ZfeU-87SM9FF0YoISjH1pl |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAR011/25 | 2025-03-06 18:21 | crm@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | Jitendra Malakar | 9630093361 | NA | GESU9568130 |  |  | hvacsez@symbiotec.in | Pithampur, Madhya Pradesh | Preventive Maintenance |  |  |  | 2025-03-07 17:12 | technician@crystalgroup.in | Symbiotec Pharmalab Pvt. Ltd. | GESU9568130 | 40" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | PM service | Tech. On field | NA | No | Pm service only | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR011%2F25 | Carrier | 561-018 | NSJ60396208 | 561018 | 5385 | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-03-07 11:08 | 2025-03-07 |  |  |  |  | GESU9568130 |  |  |  | Carrier | +6c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/170 | 9.9/9.8/9.9 | 407/406/407 | Short | Unit working as satisfactory | NA | No | https://drive.google.com/open?id=1zDZTFVVFF_mbaWnYUjHFLSr4id67OONC, https://drive.google.com/open?id=1OKwAHgtVlp1mQSFSS3M66yKhdX9nbU_a |  |  | 77 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR012/25 | 2025-03-07 16:31 | crm@crystalgroup.in | LAURUS UNIT -1 | Ramakrishna | 8916601403 | Sr. Manager - Engineering | PCIU6006639 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa | ramakrishna.chvvs@lauruslabs.com | Vishakapatnam | Running with issues | Fluctuations in temperature |  |  | 2025-03-08 22:34 | service@crystalgroup.in | Laurus Labs Limited-Unit 1 | PCIU6006639 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | suctions gas sensor or condenser coil dirty | replaced suctions gas sensor with new & clean condenser coil with fresh water | na | No | condenser coil not clean on timely | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR012%2F25 | Daikin | daikin | na | ok | III d | used | na | VIRENDRA | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-04-25 11:18 | tender@crystalgroup.in | NO | [9 empty] | 2025-04-25 11:19 | tender@crystalgroup.in | NO | [14 empty] | 2025-03-08 11:26 | 2025-03-07 |  |  |  |  | PCIU6006639 |  |  |  | Daikin | 1.5C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 44KPA 1186KPA | 9.0A 8.7A 8.9A | 407V 403V 405V | Not done | We found in this unit SGS Sensor df and condenser coil dirty | We have replaced SGS SENSOR and condenser coil wash with normal water | No | https://drive.google.com/open?id=1TJFqhdXr-NixHkn4dbB_5QVbBz5pwqA3, https://drive.google.com/open?id=1uwbnnweE9LGYMWnYmWimyTAE27kkS5r7 |  |  | Trip no 077 | No | No | Can be done on next PM | N/a | Sgs sensor | viru0068@gmail.com | REEFER
MAR013/25 | 2025-03-07 17:42 | crm@crystalgroup.in | DIVIS LAB | Surarchit | 96527 25368 | On duty Officer | Cont 4 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Sahil | M.Ramakrishna@divislabs.com | Hyderabad | Running with issues | Container not cooling down , oil leakage near filter drier |  |  | 2025-03-07 20:10 | service@crystalgroup.in | Divis Labs | Cont 4 | 40 reefer | carrier thine line | SERVICE-ON CALL | LEASE | CHARGEABLE | temperature no achieve as desired | try to find leakage by engg | no yet conform | No | suspected leakage from discharge side | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR013%2F25 | reefer | carrier thine line | na | ok | ok | used | na | RAMIZ | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-03-17 16:20 | tender@crystalgroup.in | NO | [9 empty] | 2025-03-17 16:20 | tender@crystalgroup.in | NO | [14 empty] | 2025-03-10 00:04 | 2025-03-09 |  |  |  |  | CONTAINER 04 |  |  |  | Carrier | +3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | NA | 11.5 AMPS | 404/4O5/404 | Not done | found leakage from condenser coil out let pipe | NEED TO REMOVE & REPAIR & FIX | Yes | https://drive.google.com/open?id=1EcyYhDx8HDjXZzBcBnMieLdHMph920ao, https://drive.google.com/open?id=1VmfdSVpqKNUN_eQ-EW2ST9hWF2K2KtJd |  |  | 76 | Yes | Yes | Urgent | ALL WORK PENDING | BREZING ZET BREZING ROD 6 NOS FILTER DRIER N2 R134a 5 KGS | service@crystalgroup.in | REEFER
MAR014/25 | 2025-03-08 10:58 | tender@crystalgroup.in | PI Industries Limited | Dinesh Jaiswal | 92272 04408 | NA | MYRU4502299 |  |  | dinesh.jaiswal@piind.com | Panoli, Gujarat | Preventive Maintenance |  |  |  | 2025-03-08 11:11 | technician@crystalgroup.in | PI INDUSTRIES LTD | MYRU4502299 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | Done | FilterDrier | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR014%2F25 | Daikin | Daikin | NOT AVAILABLE | LYE10E136A2 | NOT AVAILABLE | Refurbished | NA | RAJ KUMAR | No |  | 2025-03-08 11:06 | tender@crystalgroup.in | YES | MAR003 | 2025-03-08 | Spares | PI INDUSTRY | Panoli | MYRU4502299 | SITE | FOC | DAIKIN | 2025-04-10 15:19 | tender@crystalgroup.in | YES | MAR003 | YES
MAR015/25 | 2025-03-08 11:31 | crm@crystalgroup.in | LAURUS UNIT -1 | Ramakrishna | 8916601403 | NA | CXRU1037308 |  |  | ramakrishna.chvvs@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-03-08 22:28 | service@crystalgroup.in | Laurus Labs Limited-Unit 1 | CXRU1037308 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | AMC | condenser coil normal dirty | clean condenser coil with fresh water . | na | No | no clean condenser coil on time | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR015%2F25 | Daikin | LXE10E147F2 | M000334 | K31505146690 | DECOS 3F 2553 / 1 | Used | na | VIRENDRA | No |  | 2025-04-25 11:19 | tender@crystalgroup.in | NO | [9 empty] | 2025-04-25 11:21 | tender@crystalgroup.in | NO | [14 empty] | 2025-03-10 15:29 | 2025-03-07 |  |  |  |  | CXRU1037308 |  |  |  | Daikin | +1.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 124KPA 1067KPA | 8.3A 8.0A 8.1A | 404V 403V 405V | Not done | We have found condenser coil dirty | We have clean condenser coil with normal water | No | https://drive.google.com/open?id=1ioWQ7ou5OJiLBr3PHKIXFJVCNIlul5LD, https://drive.google.com/open?id=1ghCYwvixVcaEYb4-RE72gN4U8f02-8MR |  |  | Trip no 077 | No | No | Can be done on next PM | N/a | N/a | viru0068@gmail.com | REEFER
MAR016/25 | 2025-03-08 11:34 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | GAURAV GULHANE | 9145242830 | NA | CXRU1030387 | REPAIRS & REPLACEMENT | Ramiz | NA | Hyderabad | Complete Breakdown | Compressor needs to be replaced |  |  | 2025-03-08 22:15 | service@crystalgroup.in | HETERO PLASMA | CXRU1030387 | 40FT STD RF with Anteroom | daikin | SERVICE-AT SITE | LEASE | FOC | ice foundation on evaproter coil & supply air flow block y cargo & Ice foundation t bar floor. | advice them by pallets & keep proper sir circulation away. | na | No | in proper staking cargo | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR016%2F25 | DAikin | LXE10E147F2 | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | na | RAMIZ | No | REPAIRS & REPLACEMENT | 2025-03-08 12:10 | tender@crystalgroup.in | YES | MAR004 | 2025-03-08 | Spares | HETERO PLASMA | Hyderabad | CXRU1030387 | SITE | FOC | DAIKIN | 2025-03-10 16:40 | tender@crystalgroup.in | YES | MAR004 | YES | https://drive.google.com/open?id=1aADntlLhhvHliH7QfF6HRE11JnW71RiP | [11 empty] | 2025-03-17 02:34 | 2025-03-16 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -25C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/13.5 bar | 10.1 10.2/10.1 | 407/406/407 | Not done | temperature no pull down | advice them by pallets & keep proper sir circulation away. | No | https://drive.google.com/open?id=1Jtv6eEq__HiRlU_P9R9UvEfkVGmgNObK, https://drive.google.com/open?id=1RUU1vu9KCXD63gnKtcDcp9NWJtzg4Na1 |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR017/25 | 2025-03-08 16:46 | crm@crystalgroup.in | Softbox | Satish Kondapalli | 8977711235 | NA | GRMU3707470 | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, REPAIRS & REPLACEMENT | Pushpa | Skondapalli@csafeglobal.com | Hyderabad | Complete Breakdown | Compressor making noise, need to replace filter drier |  |  | 2025-03-08 22:03 | service@crystalgroup.in | Softbox | GRMU3707470 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Compressor abnormal noise & less gas suspected & isv & esv valve defective . | have to return mumbai | isv esv gas r134a filter drier breezing set all equipment | Yes | leakage or isv & esv defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR017%2F25 | Daikin | daikin | na | ok | decose iiid | used | yes | RAMIZ | No | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, REPAIRS & REPLACEMENT | 2025-03-10 12:44 | tender@crystalgroup.in | YES | MAR009 | 2025-03-10 | Consumables, Spares | Softbox | Hyderabad | GRMU3707470 | SITE | FOC | DAIKIN | 2025-08-08 14:38 | crm@crystalgroup.in | NO | [14 empty] | 2025-04-29 15:39 | 2025-04-26 |  |  |  |  | GRMU3707470 |  |  |  | Daikin | NA | Damage | Need to replace |  | Need to replace | Need to replace | Need to replace | Need to top up |  | Need to top up |  | Need to replace |  | Okay |  | Okay |  | Need to replace | Okay |  | Need to replace |  | Okay | Need to replace | Okay | Not done | Need to replace |  | NA | NA | NA | Not done | ISSUE NOT RESOLVED | BROUGHT CONTAINER BACK TO CRYSTAL YARD | Yes | https://drive.google.com/open?id=1WbJJupxmqdNjsYpjK89c5kC91HGkpeah |  |  | NA | No | No | Urgent | NA | ISV ESV GAS R134A FILTER DRIER BREEZING SET ALL EQUIPMENTS | technician@crystalgroup.in | REEFER
MAR018/25 | 2025-03-08 23:00 | service@crystalgroup.in | Hetero Unit 5 | Mr. Malyadri ¦ Mr. Prudhvi | 80964 40123/ 99897 18520 | NA | SUDU6218004 |  |  | malyadri.k@hetero.com ¦ prudhviraju.v@hetero.com | Hyderabad | Preventive Maintenance |  |  |  | 2025-03-08 23:03 | service@crystalgroup.in | HETERRO UNIT 5 | SUDU6218004 | 40FT STD RF | CARRIER ELIGHT LINE | PREVENTIVE MAINTENANCE | LEASE | FOC | CONENSER COIL NORMAL DIRTY | CLEAN CONDENSER COIL WITH FRESH WATER |  | MAN TRAF NEED TO FIX | NOT CLEAN IN TIEMLY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR018%2F25 | Carrier-Primeline | Primeline | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | NA | RAMIZ | Yes |  | 2025-03-10 15:09 | crm@crystalgroup.in | NO | [9 empty] | 2025-03-10 15:09 | crm@crystalgroup.in | NO |  |  |  |  | 2025-03-10 15:55 | crm@crystalgroup.in | NO
MAR019/25 | 2025-03-10 12:08 | crm@crystalgroup.in | Qwik Supply | Lalit Saini | 9928034131 | Manager | TRIU6680335 | COMPRESSOR MAKING NOISE | Pushpa | lalit.saini@qwik.co.in | Jaipur | Running with issues | Container currently running on one unit |  |  | 2025-03-10 18:16 | crm@crystalgroup.in | Qwik Supply | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-ON CALL | LEASE | FOC | Motor making heavy noise | Need to replace Bearings, Evp motor (suspected) | Bearings | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR019%2F25 | Daikin | Daikin | NA | NA | NA | Used | NA | RAMIZ | Yes | COMPRESSOR MAKING NOISE | 2025-03-31 15:18 | tender@crystalgroup.in | YES | MAR023 | 2025-03-31 | Spares | Qwik Supply Chain Pvt Ltd | Jaipur | TRIU6680335 | SITE | FOC | DAIKIN | 2025-04-01 12:55 | tender@crystalgroup.in | YES | MAR026 | YES | [12 empty] | 2025-04-07 16:03 | 2025-03-20 |  |  |  |  | TRIU6680335 |  |  |  | Carrier | -30'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-11psi, D-1126 | R-9.1,B-8.9, Y-9.0 | L1 404, L2 403. L3 404 | Short | We have attende tha unit found al E 205 eveporetor moter failure and condenser coil havy durty | We installations the eveporetor moter and condenser coil wash with normal water after container running is fine | No | https://drive.google.com/open?id=1OtEl6k32GougIA1kjjbq94nc3_VWhrKN, https://drive.google.com/open?id=12zTqNMgbfca4yXbtZwEa8FGCrlDq-Kh3, https://drive.google.com/open?id=1EJjcSQxmnveU0lS8vlwYW1fYpMjhDk9U, https://drive.google.com/open?id=1KHQOcBzD4ZBq3DvOmW4e3ooBNNfMslzY, https://drive.google.com/open?id=1_D17foJEgezeEXfSsRYGt-kCklArpg3r |  |  | Na | No | No | Can be done on next PM | No | Filter drier | rajreefertech@gmail.com | REEFER
MAR020/25 | 2025-03-11 03:59 | service@crystalgroup.in | RELIANCE | Mark / Anbu | 77188 81734 ¦ 90040 43704 | NA | CCLU1031918 | MOTOR MAKING NOISE, ALARM CODE VISIBLE | Pushpa mam | mark.Silveira@ril.com / anbu.EZHILAN@ril.com | Jamnagar Gujarat | Running with issues | (1). compressor oil leakage (2) Noise coming from condenser fan motor (3) The keypad is not working properly |  |  | 2025-03-11 04:14 | service@crystalgroup.in | Reliance - Jamnagar | CCLU1031918 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | condenser fan motor bearing noise & key pad defective & compressor oil leakage | need to replace condenser fan motor & keypad | condenser fan motor bearing 2 nos ( suspected to motor defective) key pad | Yes | damaged bearings, a faulty motor, loose components | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR020%2F25 | Carrier - Thinline | Thinline | na | ok | ok | brand New | na | RAJ KUMAR | Yes | MOTOR MAKING NOISE, ALARM CODE VISIBLE | 2025-03-31 16:23 | tender@crystalgroup.in | YES | MAR024 | 2025-03-31 | Spares | Reliance - Jamnagar | Jamnagar | CCLU1031918 | SITE | FOC | CARRIER-THINLINE | 2025-04-01 12:50 | tender@crystalgroup.in | YES | MAR024 | YES |  |  | 2025-04-02 11:53 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-29 16:06 | 2025-03-27 |  |  |  |  | CCLU1031918 |  |  |  | Carrier | +7'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-1.8. D-12.6 | R-13.5. B13.1. Y-13.4 | L1-400. L2-400. L3-400 | Short | We have attende tha unit found keypad not working and condenser coil normal durty and condenser moter noisy | We have work keypad replace and condenser moter greesh and condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1aAEyPtUog0OHKnZut2kMNb9aZ13jTb85, https://drive.google.com/open?id=1GLx87eBiQIFoeJ9yoTTxUhulJ-gySTGS |  |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAR021/25 | 2025-03-11 04:02 | service@crystalgroup.in | RELIANCE | Mark / Anbu | 77188 81734 ¦ 90040 43704 | na | TRIU6618663 | ALARM CODE VISIBLE | Pushpa mam | mark.Silveira@ril.com / anbu.EZHILAN@ril.com | Jamnagar Gujarat | Running with issues | 1). AL /54 - Primary Supply Air Sensor Failure (STS) (2). AL/60- Defrost Termination Sensor Failure (DTS) (3). AL/72-74.(USDA) Temperatures 1. 2.3 Out of Range (4). AL/61- Heaters Failure (defrost heater problem ) |  |  | 2025-03-11 04:08 | service@crystalgroup.in | Reliance - Jamnagar | TRIU6618663 | 20FT STD RF | carrier | SERVICE-ON CALL | LEASE | FOC | al 54,al 60 al 61,al 72 visible | need to replace defective heater & supply temperature sensor | supply temperature sensor 2 nos defrost sensor defrost heater 6 nos | Yes | chemical contamination, damaged transition junctions, self-heating, excessive mechanical stress, and electrical overload. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR021%2F25 | Carrier - Thinline | Thinline | ok | ok | ok | Refurbished | na | RAJ KUMAR | Yes | ALARM CODE VISIBLE | 2025-03-31 16:28 | tender@crystalgroup.in | YES | MAR025 | 2025-03-31 | Spares | Reliance - Jamnagar | Jamnagar | TRIU6618663 | SITE | FOC | CARRIER-THINLINE | 2025-04-01 12:50 | tender@crystalgroup.in | YES | MAR025 | YES |  |  | 2025-04-02 11:52 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-03-28 16:48 | 2025-03-27 |  |  |  |  | TRIU6618663 |  |  |  | Carrier | +7'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-2.1. , dis.-16.8 | R-13.1. ,B-13.5. Y-13.4 | 422, 420, 421 | Short | We have attende tha unit found condenser coil durty and eveporetor coil havy durty, heater not working and Dal 70 supply sensor recorder failure | We have worked condenser coil wash with normal water , eveporetor coil wash with normal water, heater rod 6 nose installation and supply sensor recorder replace after unit running sound condition | No | https://drive.google.com/open?id=1KCVn91cTy8UPZcAak9syVZf2RHqXMWBh, https://drive.google.com/open?id=152a9S-oElmlJ-AwQn-1dmugMR3A19DwW, https://drive.google.com/open?id=1-bD_cC1zN4pj-OF_gEPTQ_1hoxfaVOT3, https://drive.google.com/open?id=1kXslnq5WkVhc1PNZX4jKB-sHAgaC1TVz |  |  | Na | No | No | Can be done on next PM | No | Na | rajreefertech@gmail.com | REEFER
MAR022/25 | 2025-03-12 01:19 | service@crystalgroup.in | Qwik Supply | avinash | 9281026402 | na | CICU1799177 |  |  | na | Shamshabad | Preventive Maintenance |  |  |  | 2025-03-12 01:25 | service@crystalgroup.in | Qwik Supply | CICU1799177 | 10FT Spl RF | tk mp 4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | condense coil very dirty | clean condenser coil with fresh water | na | No | condense coil very dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR022%2F25 | Thermoking MP-4000 | MP 4000 | 20B2876DT | EDGM005148 | ok | BRand NEW | JSGA622180057 | RAMIZ | No |  | 2025-03-17 14:32 | tender@crystalgroup.in | NO | [9 empty] | 2025-03-17 14:36 | tender@crystalgroup.in | NO | [14 empty] | 2025-03-12 01:37 | 2025-03-11 |  |  |  |  | CICU1799177 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1,7 / 16.5 bar | 8.6/8.6/8.6 | 407/408/407 | Not done | found condenser coil heavy dirty | clean condenser with fresh water | No | https://drive.google.com/open?id=1X-p6FDG3lDEpn4wyXoy-aq-MgHWkPQs_, https://drive.google.com/open?id=1vdgHh0LwoAbzUt0f78KLUs6AXLkklFCO |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR023/25 | 2025-03-12 12:32 | tender@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Brhamaiaha | 7095177094 | Asst. Manager – Engineering, | MYRU4500887 | Anti Room Installation |  | Brahmaiah.g@hetero.com | Hyderabad | Installation |  |  |  | 2025-03-13 08:57 | service@crystalgroup.in | Hetero Plasma | MYRU4500887 | 40FT STD RF | daikin | SERVICE-AT SITE | LEASE | FOC | compressor over current & abnormal noise | need to replace compressor | compressor compressor oil gas R134a 6 kgs n2 cylinder big filter drier vacuum pump | Yes | Problems with wiring, contaminated refrigerant oil can cause friction and overheating, leading to overcurrent and compressor failure. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR023%2F25 | Daikin | Daikin | na | LXE10E136A | decose iiid | Refurbished | na | RAMIZ | Yes | Anti Room Installation | 2025-04-17 16:03 | tender@crystalgroup.in | YES | MAR028 | 2025-04-15 | Spares | Hetero Plasma | Hyderabad | MYRU4500887 | SITE | FOC | DAIKIN | 2025-04-17 16:23 | service.support@crystalgroup.in | YES | MAR028 | YES |  |  | 2025-04-17 16:24 | service.support@crystalgroup.in | YES | MAR028 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-04-08 21:00 | 2025-04-06 |  |  |  |  | MYRU4500887 |  |  |  | Daikin | -25.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 44KPA 11KPA 1264KPA 1316KPA | 10.0A 9.5A 9.7A 9.3A 9.9A 9.4A | 397V 393V 395V | Not done | We have found in this evp motor df main unit stand by unit compressor df | Main unit EVP motor replace, और stand by unit compressor replaced fillter Drier replace N2 test vacuum and gas charge R-134a 5kg | No | https://drive.google.com/open?id=12oIa3P42jeKrSGBsYYsw-pZQmZXnq5Ym, https://drive.google.com/open?id=1km1_jLUbu_QLgcMuzxe-kuCeOd8IMaZg |  |  | TRIPNO 080 | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
MAR024/25 | 2025-03-15 14:19 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | CRLU3604920 | AMC |  | tharunkishore.r@sailife.com | Bidar | AMC | [57 empty] | 2025-03-15 15:21 | 2025-03-11 |  |  |  |  | CRLU3604920 |  |  |  | Daikin | +4.0C | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 190KPA 981KPA | 8.7A 8.3A 8.5A | 404V 401V 403V | Not done | WE HV ATTAND THIS UNIT AND FOUND CONDENSOR COIL DIRTY | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | No | https://drive.google.com/open?id=1BS2OMZWVtL8osR9UUfCC_xO2-gI1Lb67 |  |  | TRIP NO 077 | No | No | Can be done on next PM | N/A | N/A | viru0068@gmail.com | REEFER
MAR025/25 | 2025-03-15 14:22 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | NYKU7931149 | AMC |  | tharunkishore.r@sailife.com | Bidar | AMC | [28 empty] | 2025-04-14 12:50 | tender@crystalgroup.in | YES | MAR027 | 2025-03-20 | Spares | Sai Life Science | BIDAR | NYKU7931149 | SITE | FOC | CARRIER-THINLINE | [17 empty] | 2025-03-15 15:28 | 2025-03-11 |  |  |  |  | NYKU7931149 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - / 9.9B | 10A 9.7A 9.9A | 404V 401V 403 | Not done | WE HV ATTAND THIS UNIT AND FOUND DISPLAY NOT SHOWING TEMPRATURE PROPERLY, LITHIAM BETTERY 9V NEED TO REPLACE AND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | Yes | https://drive.google.com/open?id=12lslX3vdcb3KgkZFhE2VdWoXDprn2w_O |  |  | TRIP NO 077 | Yes | No | Can be done on next PM | DISPLAY NEED TO REPLACE AND LITHIAM BETTERY NEED TO REPLACE | DISPLAY 1NOS LITHIAM BETTERY 9V 1NOS | viru0068@gmail.com | REEFER
MAR026/25 | 2025-03-15 14:24 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | MYRU4508120 | AMC |  | tharunkishore.r@sailife.com | Bidar | AMC | [57 empty] | 2025-03-15 15:34 | 2025-03-11 |  |  |  |  | MYRU4508120 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5B 11.3B | 5.3A 5.0A 5.1A | 410V 405V 407V | Not done | WE HV ATTAND THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | No | https://drive.google.com/open?id=1lOBkYsn2T4KHVEUDan59ofnPIWvIzh3O |  |  | TRIP NO 077 | No | No | Can be done on next PM | N/A | N/A | viru0068@gmail.com | REEFER
MAR027/25 | 2025-03-15 14:28 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | PCIU6008382 |  |  | tharunkishore.r@sailife.com | Bidar | Preventive Maintenance | [57 empty] | 2025-03-15 15:44 | 2025-03-11 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | +4.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 80KPA 1532KPA | 9.4A 9.0A 9.1A | 404V 401V 403V | Not done | WE HV ATTAND THIS UNIT AND FOUND CONENSOR COIL HEAVY DIRTY TO WASH ,SUPPLY SENSOR DF 2NOS SECTION SENSOR DF 1NOS | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | No | https://drive.google.com/open?id=1d6J1bzMsEE7uy950YtzzWo384B-MvapN |  |  | TRIP NO 077 | Yes | No | Can be done on next PM | SUPPLY SENSOR NEED TO REPLACE 2NOS AND SECTION SENSOR NEED TO REPLACE 1NOS | SUPPLY SENSOR 2NOS SECTION GAS SENSOR 1NOS | viru0068@gmail.com | REEFER
MAR028/25 | 2025-03-15 14:29 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | TITU9930032 |  |  | tharunkishore.r@sailife.com | Bidar | Preventive Maintenance |  |  |  | 2025-04-17 16:39 | service.support@crystalgroup.in | Sai Life Science Pvt Ltd | TITU9930032 | 40FT Spl RF | Thermo King | SERVICE-AT SITE | LEASE | FOC | Closed PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR028%2F25 | Thermoking | TK-MP4000 | 14E6357AT | EOG10005532 | NA | Used | NA | RAJ KUMAR | No |  | 2025-04-17 16:42 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-17 16:42 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-17 16:44 | service.support@crystalgroup.in | NO | [7 empty] | 2025-03-15 15:53 | 2025-03-11 |  |  |  |  | TITU9930032 |  |  |  | Thermo king | +4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -/ 17.3B | 5.7A 5.4A 5.5A | 398V 395V 397V | Not done | WE HV ATTAND THIS UNIT FOUND CONDENSOR COIL HEAVY DIRTY TO WASH AND DISPALY NOT SHOWING TEMP. PROPERLY , KEYPAD LOGO NEED TO REPLACE | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | Yes | https://drive.google.com/open?id=10ZhtGQFxIkyjoWMmJWshHLl9-hd01sGg |  |  | TRIP NO 077 | Yes | No | Can be done on next PM | DISPLAY NRRD TO REPLACE AND KEYPAD LOGO NEED TO REPLACE | DISPLAY 1NOS KEYPAD LOGO 1NOS | viru0068@gmail.com | REEFER
MAR029/25 | 2025-03-15 14:31 | tender@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | MYRU4518042 | AMC |  | tharunkishore.r@sailife.com | Bidar | AMC |  |  |  | 2025-05-06 16:56 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | MYRU4518042 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR029%2F25 | NA | NA | NA | NA | NA | NA | NA | VIRENDRA | No | AMC | 2025-05-15 16:17 | operation@crystalgroup.in | NO | [26 empty] | 2025-03-15 16:00 | 2025-03-11 |  |  |  |  | MYRU4518042 |  |  |  | Daikin | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 10KPA 1106KPA | 7.4A 7.3A 7.5A | 395V 393V 391V | Not done | WE HV ATTAND THIS UNIT AND FOUND CONDENSOR COIL HEAVY DIRTY TO WASH ,FILLTER DRIER RUSTED TO REPLACE | WE HV CLEAN CONDENSOR COIL WITH NORMAL WATER | Yes | https://drive.google.com/open?id=1lhyUbTXClJTPrkaU4QXqtAchpgVix3YC |  |  | TRIP NO 077 | Yes | No | Can be done on next PM | FILLTER DRIER NEED TO REPLACE AND R-134a NEED TO TOPUP | FILLTER DRIER 1NOS R-134a 4CAN | viru0068@gmail.com | REEFER
MAR030/25 | 2025-03-15 19:35 | service@crystalgroup.in | Dr. Reddy's Labs -Biologics | sureshkasam | 99081 25456 | Plant Engineer | TITU9930074 | DISPLAY NOT VISIBLE | RAMIZ | sureshkasam@drredddys.com | Hyderabad | Display Issue | DISPLAY NOT VISIBLE |  |  | 2025-03-15 19:39 | service@crystalgroup.in | Dr. Reddy's Labs -Biologics | TITU9930074 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | tk mp 400 | SERVICE-AT SITE | LEASE | FOC | display defective | need to replace | display | Yes | getting old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR030%2F25 | Thermoking | MP-4000 | 05G7619AG | E001051602 | ok | used | JSGA622180047 ¦ JSGA622180052 | RAMIZ | Yes | DISPLAY NOT VISIBLE | 2025-03-15 19:41 | service@crystalgroup.in | NO | [9 empty] | 2025-03-15 19:41 | service@crystalgroup.in | NO |  |  |  |  | 2025-03-15 19:41 | service@crystalgroup.in | NO | [7 empty] | 2025-03-15 20:10 | 2025-03-15 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5/117.8 bar | 8.8/8.8/8.9 | 407/408/407 | Not done | display defective | replaced display with new one | No | https://drive.google.com/open?id=1yqJy21gtJ7esbl9gpN5-Cys0XjDyBd3Y, https://drive.google.com/open?id=1zhYbtf459d0IlTPYD9aAWejWDCQBNape |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR031/25 | 2025-03-17 15:40 | tender@crystalgroup.in | Adya Dairy Products Pvt. Ltd. | Raju Bhunia | 9230676077 | NA | BMOU9729398 | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, |  | electrical@adyadairy.com | West Bengal | Running with issues | Compressor issue |  |  | 2025-03-17 21:58 | service@crystalgroup.in | Adya Dairy | BMOU972939 | 40 | daikin | SERVICE-ON CALL | LEASE | FOC | al 109 low pressor / filter drier /FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, | need to replaced filter drier & R134a 5 kgs & vacuum pump | 1) filer drier 2) gas R134a 5 kgs 3)vacuum pump | Yes | filer drier & less gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR031%2F25 | daikin | daikin | na | na | ok | used | ok | Vibak | Yes | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, | 2025-03-21 11:29 | tender@crystalgroup.in | YES | MAR015 | 2025-03-21 | Consumables, Spares | Adya Dairy Products Pvt. Ltd. | West Bengal | BMOU9729398 | SITE | FOC | DAIKIN | 2025-03-21 12:30 | technician@crystalgroup.in | YES | MAR015 | NA |  |  | 2025-03-21 12:53 | technician@crystalgroup.in | YES | MAR015 | ARRENGING AT SITE | [5 empty] | 2025-03-21 12:41 | 2025-03-17 |  |  |  |  | BMOU9729392 |  |  |  | Daikin | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/200 psig | 12.6/12.7/13 | 405/406/405 | Full | Unit Tripping Off due low pressure Al E109 | Reset Expansion value and clean & secure . Maintain Refrigeration pressure. Reset Alam and unit working fine. | Yes | https://drive.google.com/open?id=1LWnFV3ljj2Mt9GK1JQBIJYbT5dCHAaih, https://drive.google.com/open?id=1k8cZigSSoXp1MRDksJesJ4qilYNAjp8x |  |  | NA | No | No | Can be done on next PM | NA | Daikin Temp. Sensor DRS | technician@crystalgroup.in | REEFER
MAR032/25 | 2025-03-18 10:48 | tender@crystalgroup.in | lands flavour | Anant Prabhu | 8105012718 | NA | CXRU1043337 | Anti Room Installation |  | anil.more@naturalicecreams.in | Mangalore | Installation | [28 empty] | 2025-03-18 11:01 | tender@crystalgroup.in | YES | MAR011 | 2025-03-18 | Spares | Lands Flavor | Mangalore | CXRU1043337 | SITE | FOC | NA
MAR033/25 | 2025-03-18 11:30 | tender@crystalgroup.in | DR REDDY FTO 7 | Ajit Sahu | 9822884152 | NA | SEGU9511192 | Anti Room Installation |  | ajitkumarsahu@drreddys.com | Vishakapatnam | Installation |  |  |  | 2025-05-06 17:01 | crm@crystalgroup.in | Dr. Reddy FTO7 | SEGU9511192 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR033%2F25 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | No | Anti Room Installation | 2025-03-18 11:33 | tender@crystalgroup.in | YES | MAR012 | 2025-03-18 | Spares, FOC | Dr. Reddy FTO7 | Duvada | SEGU9511192 | DEPOT | FOC | NA | 2025-06-02 15:25 | operation@crystalgroup.in | YES | MAR012 | YES | https://drive.google.com/open?id=1PZOfyXeDcKtr5kICZ8SYgvlSXR7lpVa1 | Vendor
MAR034/25 | 2025-03-18 12:49 | tender@crystalgroup.in | Eugia Steriles Private Limited | Mr. Vinod | 9944862219 | NA | CICU3876610 | Alarm | Shahbuddin | saravanan.arumugam@qwik.co.in | Coimbatore | Running with issues |  |  |  | 2025-03-18 15:14 | technician@crystalgroup.in | Eugia Steriles Private Limited | CICU3876610 | 10FT STD RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | Temp. | Co. Own house keeping under progress... | NA | Still obs aftet dudpected return tk sendor | Blockage conf.coil & inside bottom area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR034%2F25 | Thermoking | Magnum Plus | E0GM031439 | 0422GM031439 | ABC782900322060170 | Brand New | NA | Not yet unit u/ obs dury person | No | Alarm | 2025-03-21 11:20 | tender@crystalgroup.in | NO | [9 empty] | 2025-03-21 11:23 | tender@crystalgroup.in | NO | [14 empty] | 2025-03-28 16:18 | 2025-03-27 |  |  |  |  | CICU3876610 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/20 bar | 9.9/9.8/9.9 | 406/405/406 | Short | Temp. Issue | Clean In side bottam , air space and pm service done with clen condenser coil. | No | https://drive.google.com/open?id=1MGvUu4-7B4GZST_J6Y-_sxTSDdhBXbz1, https://drive.google.com/open?id=1PRrRP06GDif-ib8LTfLADYZ9sTx4rOWY |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR035/25 | 2025-03-20 15:12 | tender@crystalgroup.in | Swabhimani Agro | Raju Shetty | 9657137666 | NA | DMOU9226840 | REPAIRS & REPLACEMENT | Pushpa ma'am | swabhimaniagro@gmail.com | Kolhapur | Complete Breakdown |  |  |  | 2025-03-24 14:38 | technician@crystalgroup.in | Swabhimani Agro | DMOU9226840 | N/a | N/a | SERVICE-ON CALL | NA | NA | Compressor df due to ground | Need to be replaced compressor | Compressor 1nos Compressor oil 3ltr N2 test and flush Vaccum pump Fillter Drier 1nos R-134a 5kg | Yes | Compressor ground | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR035%2F25 | Reefer unit | Prime line | N/a | N/a | Ml3 | N/a | N/a | VIRENDRA | Yes | REPAIRS & REPLACEMENT | 2025-04-17 16:19 | tender@crystalgroup.in | YES | MAR029 | 2025-03-31 | Consumables, Spares | Swabhimani Agro | Kolhapur | DMOU9226840 | SITE | FOC | CARRIER-PRIMLINE | 2025-04-25 11:04 | tender@crystalgroup.in | YES | MAR029 | NA
MAR036/25 | 2025-03-20 15:28 | tender@crystalgroup.in | QUICK SUPPLY RELIANCE | Mr. Pramod | 8865021446 | NA | SJKU4000017 | REPAIRS & REPLACEMENT | Kunal | NA | Hapur | Complete Breakdown | HPT Compressor ON & OFF |  |  | 2025-05-06 17:05 | crm@crystalgroup.in | Qwik Supply Reliance | SJKU4000017 | NA | NA | NA | NA | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR036%2F25 | NA | NA | NA | NA | NA | NA | NA | RAJ KUMAR | No | REPAIRS & REPLACEMENT | 2025-05-06 17:23 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:36 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-10 14:57 | crm@crystalgroup.in | NO | [7 empty] | 2025-03-24 12:20 | 2025-03-23 |  |  |  |  | SJKU4000017 |  |  |  | Carrier | +16 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .2/12.6 bar | 9.9/10/9.9 | 395/396/396 | Not done | Unit tripping off due to condenser coil chok & blocking | PM service done & clean condenser coil & maintain refrigerant pressure | No | https://drive.google.com/open?id=1Yvfea0EsayScBzSSXyHRUe78G4Nk57FK, https://drive.google.com/open?id=10n71wxtnTeq54EVpvOgX3LVG_G-obCbH |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR037/25 | 2025-03-20 15:39 | tender@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | SJKU4000104 |  |  | NA | Hyderabad | Preventive Maintenance |  |  |  | 2025-03-20 20:46 | service@crystalgroup.in | DSV | SJKU4000104 | 40FT STD RF | 2019 | PREVENTIVE MAINTENANCE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | na | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR037%2F25 | Thermoking | MP-4000 | ok | ok | ok | Refurbished | na | RAMIZ | No |  | 2025-03-20 20:47 | service@crystalgroup.in | NO | [9 empty] | 2025-03-20 20:48 | service@crystalgroup.in | NO |  |  |  |  | 2025-03-20 20:48 | service@crystalgroup.in | NO | [7 empty] | 2025-03-20 20:53 | 2025-03-20 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | +3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1,7 / 16.5 bar | 8.6/8.6/8.6 | 406/407/406 v | Not done | condenser coil dirty | clean condenser coil with fresh water | No | https://drive.google.com/open?id=1qrhllPFReZ48lx9xNoQMkujRx8oB1LgK, https://drive.google.com/open?id=1D_fr5Ep3vxQwNcP-fox25hCzi8eDH4Kw |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR038/25 | 2025-03-20 15:45 | tender@crystalgroup.in | DSV LOGISTIC | Mr. Ramesh | 7799437098 | NA | TITU9930006 |  |  | NA | Hyderabad | Preventive Maintenance |  |  |  | 2025-03-20 20:57 | service@crystalgroup.in | DSV | TITU9930006 | 40FT Spl RF | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | condenser coil dirty | clean condenser coil with fresh water | na | No | due to long run | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR038%2F25 | Thermoking | Plus | 14D8550HT | EOG1000568 | pk | brand New | na | RAMIZ | No |  | 2025-03-20 20:59 | service@crystalgroup.in | NO | [9 empty] | 2025-03-20 20:59 | service@crystalgroup.in | NO |  |  |  |  | 2025-03-20 21:00 | service@crystalgroup.in | NO | [7 empty] | 2025-03-20 21:04 | 2025-03-20 |  |  |  |  | TITU9930006 |  |  |  | Thermo king | +3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1,7 / 16.5 bar | 8.6/8.6/8.6 | 406/407/406 v | Not done | condenser coil dirty | clean condenser coil with fresh water | No | https://drive.google.com/open?id=13MI-3nDCUHOf1Q-6Cn7W-ZzUNbwaq48M, https://drive.google.com/open?id=1lzEIq7Y52kySV283mzBnhDbgtrA_HpKB |  |  | 76 | No | No | Can be done on next PM | na | na | service@crystalgroup.in | REEFER
MAR039/25 | 2025-03-28 10:53 | tender@crystalgroup.in | Crystal | Mr. Vivek Kumar | NA | NA | CXRU1036019 | REPAIRS & REPLACEMENT |  | NA | Dhulagarh, Kolkata | Running with issues |  |  |  | 2025-03-28 11:37 | technician@crystalgroup.in | Crystal Yard | CXRU1036019 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | STOCK | FOC | PTI FAIL WITH ALARM | Need to replaced spare | Power plug / Temp. Sensor Nos.4 | Yes | PTI FAIL | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR039%2F25 | DAikin | LXE10E147F2 | M001044 | K31511115441 | DECOS 3F 2513 / 1 | used | NA | Vendor | Yes | REPAIRS & REPLACEMENT | 2025-03-28 11:10 | tender@crystalgroup.in | YES | MAR019 | 2025-03-28 | Spares | CRYSTAL YARD | Dhulagarh, Kolkata | CXRU1036019 | DEPOT | FOC | DAIKIN LXE10E | 2025-04-01 12:58 | tender@crystalgroup.in | YES | MAR019 | YES |  |  | 2025-04-02 12:24 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-04-02 21:39 | 2025-03-29 |  |  |  |  | CXRU1036019 |  |  |  | Daikin | 0/-18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 13/200 | 13.9/13.7/13.8 | 409/409/410 | Full | Empty- Repair & PTI | Replaced daikin sensor - EOS . DRS.RS | Yes | https://drive.google.com/open?id=13lqp5QDQpcXDGZN2exJXqJfAesoxEuYu |  |  | NA | No | No | Can be done on next PM | NA | Done by vandor | technician@crystalgroup.in | REEFER
MAR040/25 | 2025-03-28 10:55 | tender@crystalgroup.in | Crystal | Mr. Vivek Kumar | NA | NA | CRLU3179858 | REPAIRS & REPLACEMENT |  | NA | Dhulagarh, Kolkata | Running with issues |  |  |  | 2025-03-28 11:31 | technician@crystalgroup.in | Crystal Group mumbai | CRLU3179858 | 20FT STD RF | Carrier | SERVICE-AT SITE | STOCK | FOC | Fan capacitor & power plug Defective | Need to replaced parts | 20 Uf Fan capacitor & power plug | Yes | PTI FAIL | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR040%2F25 | Carrier | Thineline | NA | NA | NA | Used | NA | Vendor | Yes | REPAIRS & REPLACEMENT | 2025-03-28 11:17 | tender@crystalgroup.in | YES | MAR020 | 2025-03-28 | Spares | CRYSTAL YARD | Dhulagarh, Kolkata | CRLU3179858 | DEPOT | FOC | CARRIER-THINLINE | 2025-04-01 12:58 | tender@crystalgroup.in | YES | MAR020 | YES |  |  | 2025-04-02 12:24 | kshirod.khatua@crystalgroup.in | NO | [7 empty] | 2025-04-02 21:46 | 2025-03-29 |  |  |  |  | CRLU3179858 |  |  |  | Carrier | +6c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 12/215 | 12.9/13.2/12.8 | 410/408/409 | Full | Empty container repaired & Replaced spare | Kolkatta- Vandor repair and replaced Evaprator motor capacitor & power plug | No | https://drive.google.com/open?id=1rRMXln6OptLvDNCQ31zhE3ETf0Vi5krJ |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAR041/25 | 2025-03-31 10:50 | tender@crystalgroup.in | Reliance - Lucknow | Gopal Krishna | 6307373723 | NA | MYRU4718356 | Power Issue |  | NA | Lucknow | Complete Breakdown |  |  |  | 2025-04-01 16:05 | technician@crystalgroup.in | Reliance - Lucknow | MYRU4718356 | 40 | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Not working | Electrical wiring check and need to replaced Fuse blown with | PTCT board & Fuse | Yes | Power issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR041%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Used | NA | RAJ KUMAR | No | Power Issue | 2025-04-03 15:52 | operation@crystalgroup.in | YES | 2001-04-01 | 2025-04-03 | Spares | Reliance - Lucknow | LUCKNOW | MYRU4718356 | SITE | FOC | DAIKIN | 2025-04-03 11:01 | operation@crystalgroup.in | NO |  |  |  |  | 2025-04-10 13:22 | kshirod.khatua@crystalgroup.in | YES | 2001-04-01 | COURIER | 17779434945 | Bluedart |  | https://drive.google.com/open?id=150nvWtLnQ7R8adN9evYd-6nCzaCqmAYX |  | 2025-04-09 17:42 | 2025-04-09 |  |  |  |  | MYRU4718356 |  |  |  | Daikin | + 4 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4/190 | 9.9/9.8/9.9 | 406/406/405 | Not done | Replaced PT CT Board Defective | Found daikin unit PT- CT Board Replaced | No | https://drive.google.com/open?id=1Jr3ENuuy9PfJyNE7gxQPb-gycHQuWhHv, https://drive.google.com/open?id=1rBzBVPHMh0oXOAbWNgTdUoUNyrmvUkZK |  |  | Call | No | No | Can be done on next PM | NA | Job Done | technician@crystalgroup.in | REEFER
APR001/25 | 2025-04-03 12:37 | operation@crystalgroup.in | lands flavour | ANIL MORE |  | N/A | CXRU1043337 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, Spare required. 1 curtain... 2 inter tube light/ cable/ tube/ casing Pati Unit working with under observation etc. | Sahabuddin | anil.more@naturalicecreams.in | ADYAR MANGALORE | Temp. Issue - Spare required. 1 curtain... 2 inter tube light/ cable/ tube/ casing Pati etc. | Temperature issue and spares required |  |  | 2025-04-03 12:44 | technician@crystalgroup.in | LAND FLAVOUR BONDA FACTORY | CXRU1043337 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Light / courtan fixing with kick plate & compressor frosting | Unit maintain pressure and under observation / kick plate / courtan fixed | Tube light / cable / tube light/ casing Pati..etc... | Yes | Power issue with compressor low pumping | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR001%2F25 | https://drive.google.com/drive/folders/1-wT8o-5gU0fGeM-zDesg8npMxU6uKTim?usp=sharing | CARRIER-THINLINE | -22 | 541 320 | 5186 | Used | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, Spare required. 1 curtain... 2 inter tube light/ cable/ tube/ casing Pati Unit working with under observation etc. | 2025-04-05 17:05 | service.support@crystalgroup.in | YES | 2003-04-01 | 2025-04-05 | Spares | LAND FLAVOUR BONDA FACTORY | Mangalore | CXRU1043337 | SITE | FOC | DAIKIN | 2025-04-10 16:11 | service.support@crystalgroup.in | YES | 2003-04-01 | YES | https://drive.google.com/open?id=12NnNOpbPG0D-8rxocf9Zx5H--TsVzfva |  | 2025-04-10 16:15 | service.support@crystalgroup.in | YES | 2003-04-01 | ARRENGING AT SITE | [5 empty] | 2025-04-03 21:28 | 2025-04-02 |  |  |  |  | CXRU1043337 |  |  |  | Carrier | - 22 C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/190 | 12.6/12.7/12.7 | 406/408/407 | Short | Fixed internal tube light with new wiring / unit Refrigerant pressure maintain to reduce co.pressor Icing. | As above | No | https://drive.google.com/open?id=1krr5KGqfR6HNg-eI6LOU3M4HnSf3wehY, https://drive.google.com/open?id=1EeaKiqije4-7B4hIPja4K4yxrtZ6Ex8B |  |  | 81 | No | Yes | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR002/25 | 2025-04-03 17:45 | operation@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | N/A | N/A | N/A | MYRU4500887 | EVP MOTOR TO REPLACE | Vicky Saklani | N/A | KOTHUR | RIS EVP MOTOR | CHECKED N2 TEST VACCUM OF STAND UNIT AND R-134A REFILLING 5 KG, LIGHT REF NEW 2 NO.S BOTH UNIT RUNNING IN SOUND CONDITION WITHOUT ANY ALARAM STAND BY UNIT UNDER OBSERVATION |  |  | 2025-04-05 11:05 | technician@crystalgroup.in | HETERO PLASMA | N/A | 40 | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor | Spare on the way HYD | NA | No | Compressor internal | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR002%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | VIRENDRA | Yes | EVP MOTOR TO REPLACE | 2025-04-10 16:50 | service.support@crystalgroup.in | YES | 2002-04-01 | 2025-04-10 | Spares | HETERO PLASMA | Kothur | MYRU4500887 | SITE | FOC | DAIKIN | 2025-04-10 16:55 | service.support@crystalgroup.in | YES | 2002-04-01 | YES | https://drive.google.com/open?id=1p4vQK05vfE9W3zha4t5rShQcJsOYXVbj |  | 2025-04-10 16:56 | service.support@crystalgroup.in | YES | 2002-04-01 | ARRENGING AT SITE | [5 empty] | 4/20/2025 16:57:31 | 2025-04-15 |  |  |  |  | MYRU4500887 |  |  |  | Daikin | -25.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 44KPA 11KPA 1264KPA 1316KPA | 10.0A 9.5A 9.7A 9.3A 9.9A 9.4A | 397V 393V 395V | Not done | We have found in this evp motor df main unit stand by unit compressor df | Main unit EVP motor replace, और stand by unit compressor replaced fillter Drier replace N2 test vacuum and gas charge R-134a 5kg | No | https://drive.google.com/open?id=12oIa3P42jeKrSGBsYYsw-pZQmZXnq5Ym, https://drive.google.com/open?id=1km1_jLUbu_QLgcMuzxe-kuCeOd8IMaZg |  |  | TRIPNO 080 | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
APR003/25 | 2025-04-04 10:50 | operation@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | Mr. Rasmihandar | A | A | HDMU5537036 | COMPRESSOR MAKING NOISE, R134A Gas, N2, Gaskit, Terminal Block Kir, HP Switch | Rajkumar | N/A | Sambalpur | Requires Spares | Oncall check and found with Compressor over heat and High Voltage Compressor Intenral Isuue need to replace. |  |  | 2025-04-04 14:57 | technician@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | HDMU5537036 | 40" | Carrier- Thin Line | SERVICE-AT SITE | LEASE | FOC | Compressor over heat tripping off | Tech Allian for cross check | Thinline carrier compressor/ filter Drier/ R134a Gas/ / N2 / vacum pump etc | Yes | Compressor winding internal faultt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR003%2F25 | Carrier- Reef | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | COMPRESSOR MAKING NOISE, R134A Gas, N2, Gaskit, Terminal Block Kir, HP Switch | 2025-04-08 12:48 | service.support@crystalgroup.in | YES | 2007-04-01 | 2025-04-08 | Spares | Milk Mantra Dairy Pvt Ltd | Sambalpur | HDMU5537036 | SITE | FOC | DAIKIN | 2025-04-10 17:28 | service.support@crystalgroup.in | YES | 2007-04-01 | YES | https://drive.google.com/open?id=18iAg3B1vAzLOEQifEqhjDROl4S-4J9N5 |  | 2025-04-10 17:29 | service.support@crystalgroup.in | YES | 2007-04-01 | COURIER | 1 | SKY logistics |  |  |  | 2025-04-08 15:19 | 2025-04-08 |  |  |  |  | HDMU5537036 |  |  |  | Carrier | 2to 8 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0/180 | 12.1/12.3/12.1 | 410/409/410 | Not done | Compressor LOW pumping and over Heat | Need to replaced compressor | Yes | https://drive.google.com/open?id=1j6egXcnVC4uhfVbKkx-N7yeSRjfSw5bq, https://drive.google.com/open?id=1xo30l8PfZpYjUMPfxTWCnFN6TS_-fyMM; |  |  | NA | Yes | Yes | Can be done on next PM | Compressor on thwway | Compressor - carrier Thin Line & R134a Gas | technician@crystalgroup.in | REEFER
APR004/25 | 2025-04-04 13:10 | operation@crystalgroup.in | Dr Reddy CTO5 | T.Sreeram Naik | 7036305829 | Team member-V4 ESD,CTO-V | CXRU103256A | Spares Requires | Vicky Saklani/Virendra | sreeramnt@drreddys.com | Nalgonda | Need Inlet Sensor | Attened this unit and found condesor coil heavy dirty to wash inlet sensor DIF. Clean condesor coil with normal water, software upgrade with latest version |  |  | 2025-04-04 15:54 | technician@crystalgroup.in | Dr Reddy CTO5 | CXRU1032S64 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | Pm | Spare arrange | Evp motor Daikin | Yes | Evp motor def | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR004%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | VIRENDRA | Yes | Spares Requires | 2025-04-05 17:36 | service.support@crystalgroup.in | YES | 2005-04-01 | 2025-04-05 | Spares | Dr Reddy CTO 5 | Miryalaguda | CXRU1032S64 | SITE | FOC | DAIKIN | 2025-04-10 17:30 | service.support@crystalgroup.in | YES | 2005-04-01 | YES |  |  | 2025-04-10 17:31 | service.support@crystalgroup.in | YES | 2005-04-01 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-04-12 15:15 | 2025-04-10 |  |  |  |  | CXRU1032564 |  |  |  | Daikin | +4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 114KPA 1182KPA | 9.5A 9.1A 9.3A | 395V 392V 393V | Not done | We have found in this container inlet sensor df | We have replaced inlet sensor 1Nos | No | https://drive.google.com/open?id=19y69XFEIsx2KQsRvwBkeWXhE6lMmvwDr, https://drive.google.com/open?id=1LQP-jfd8BP2S3c3hV69VsmQoJwkMrOxV |  |  | TRIPNO 080 | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
APR005/25 | 2025-04-04 14:06 | operation@crystalgroup.in | Dr Reddy CTO5 | T.Sreeram Naik | 7036305829 | "Team member-V4 ESD,CTO-V" | CXRU1045896 | Spare Required Inlet Sensor | Vicky Saklani/Virendra | sreeramnt@drreddys.com | Nalgonda | Inlet Sensor Spare Required | Attend there unit abs found condesor coil heavy dirty to wash Inlet sensor DIF - Also clean condesor coil with Normal Water and Software upgrade with latest version |  |  | 2025-04-04 15:02 | technician@crystalgroup.in | Dr Reddy CTO5 | CXRU1045896 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Evp. Motor | On the way motor | Evp. Motor | Yes | Voltage low or high | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR005%2F25 | https://drive.google.com/file/d/1q4GJVx5gc4pqWsh2QRfHRiY--CfDw21J/view?usp=sharing | DAIKIN | -18 | NA | DAikin | DECOS 3F 2606 / 1 | 1001349 | VIRENDRA | Yes | Spare Required Inlet Sensor | 2025-04-05 17:32 | service.support@crystalgroup.in | YES | 2004-04-01 | 2025-04-05 | Spares | Dr Reddy CTO 5 | PYDIBIMAYARAM | CXRU1045896 | SITE | FOC | DAIKIN | 2025-04-10 17:34 | service.support@crystalgroup.in | YES | 2004-04-01 | YES |  |  | 2025-04-10 17:34 | service.support@crystalgroup.in | YES | 2004-04-01 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-04-12 15:18 | 2025-04-10 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | +4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 12KPA 1197KPA | 7.9A 7.5A 7.7A | 396V 393V 395V | Not done | We have found in this container inlet sensor df | We have replaced inlet sensor 1Nos | No | https://drive.google.com/open?id=1GMECgxz2ZWydiWcVw9bbVkgsLyDnXRxs, https://drive.google.com/open?id=1ayB9yZL3uTzlSrSVg67thRIakt8aWZkS |  |  | TRIPNO 080 | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
APR006/25 | 2025-04-04 15:27 | operation@crystalgroup.in | lands flavour | Ananth Prabhu | 8105012718 | NA | TRIU6616594 | PREVENTIVE MAINTENANCE |  | N/A | ADYAR MANGALORE | Preventive Maintenance |  |  |  | 2025-04-04 16:05 | technician@crystalgroup.in | LAND FLAVOUR BONDA FACTORY | TRIU6616594 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | PM | Done | Condenser fan grill and carrier key pad | Yes | PM due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR006%2F25 | Carrier | CARRIER-THINLINE | NSX60329650 | 541320 | NA | Used | NA | SHAHBUDDIN | No | PREVENTIVE MAINTENANCE | 2025-04-10 19:44 | service.support@crystalgroup.in | YES | 2009-04-01 | 2025-04-10 | Spares | LAND FLAVOUR BONDA FACTORY | ADYAR MANGALORE | TRIU6616594 | SITE | FOC | CARRIER-THINLINE | 2025-04-14 10:28 | service.support@crystalgroup.in | NO | 2009-04-01 | YES |  |  | 2025-04-14 10:29 | service.support@crystalgroup.in | NO | [7 empty] | 2025-05-04 20:14 | 2025-05-02 |  |  |  |  | TRIU6616594 |  |  |  | Carrier | -18.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/A 14.5B | 11.0A 10.7A 10.9A | 399V 395V 397V | Not done | We have found condenser grill miss | We have fix condenser grill 1nos | Yes | https://drive.google.com/open?id=1diKw4N-74mCIdwqZOagpQD6Xvl9lGjYz, https://drive.google.com/open?id=1CsoMqUQxfOXM3xzEHd3UVfFuyLTELMOr |  |  | TRIPNO 084 | Yes | No | Can be done on next PM | Keypad and bearings work pending | Keypad 1nos Bearing 6203 2nos Bearing 6205 2nos | technician@crystalgroup.in | REEFER
APR007/25 | 2025-04-04 15:53 | service.support@crystalgroup.in | Adya Dairy Products Pvt. Ltd. | Raju Bhunia | 9230676077 | Electrical | BMOU9729398 | REPAIRS & REPLACEMENT | Sushma/Pushpa | electrical@adyadairy.com | Kolkata | Complete Breakdown | Temperature setting issue, Shahbuddin said EVV coil need to replace. |  |  | 2025-04-04 15:57 | technician@crystalgroup.in | Adya Dairy Products Pvt. Ltd. | BMOU9729398 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | EEV COIL DEFECTIVE | Spare arrange | EEV COIL daikin | Yes | EEV COIL NOT FUNCTION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR007%2F25 | https://drive.google.com/drive/folders/1Yhya5jN03ZP2Abu9Rry6Lzq5zWNkOdso?usp=drive_link | DAIKIN | NA | NA | NA | Used | NA | RAJ KUMAR | No | REPAIRS & REPLACEMENT | 2025-04-05 13:10 | service.support@crystalgroup.in | YES | MAR041/25 | 2025-04-05 | Spares | Adya Dairy Products Pvt. Ltd. | Kolkata | BMOU9729398 | SITE | FOC | DAIKIN | 2025-04-14 10:32 | service.support@crystalgroup.in | YES | MAR041/25 | YES |  |  | 2025-04-14 10:34 | service.support@crystalgroup.in | YES | MAR041/25 | ARRENGING AT SITE | [5 empty] | 2025-04-20 17:45 | 2025-04-19 |  |  |  |  | BMOU9729398 |  |  |  | Daikin | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/200 psig | 22.2/12.1/12.2 | 409/400/409 | Not done | Unit set temp. Not maintain found EV coil and EV body expansion value Not functional | Removed EV coil & EV body expansion value body with the help brazing set. Fixed new expansion value body & coil.. with the help of brazing set. Leak test used Nitrogen & no found leak. Vacum system . Gas charged 5 kg R134a System run & obs. Working as nor | No | https://drive.google.com/open?id=12OHzu4nwQBgkSXzRuZrCZD54MVZU6pIg, https://drive.google.com/open?id=1bX-1VUK09eljgwJMKen_Y1hFRUhee_MU, https://drive.google.com/open?id=1LHU9_ojkBHjIXNjiplCTPHG99myo1Y96, https://drive.google.com/open?id=1lXhTd5og6SZzluRYZ0DmjHwEfq53O0n7 |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR008/25 | 2025-04-04 16:55 | service.support@crystalgroup.in | Tata Advanced Systems | Sachin Pem | 7337832756 | Engineer | CBHU281176 | FLUCTUATIONS IN TEMEPRATURE | Sushma/Vinod | Sachin.p@tasl.aero | Bangalore | Running with issues | Temperature not maintaining |  |  | 2025-04-05 01:04 | technician@crystalgroup.in | Tata Advanced Systems | CBHU281176 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp not achievement | On call inspection | NA | No | Suspected system leak | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR008%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-04-14 13:11 | tender@crystalgroup.in | YES | APR012 | 2025-04-13 | Spares | Tata Advanced Systems | Jigani, Bangalore | CBHU281176 | SITE | FOC | CARRIER-THINLINE | 2025-04-17 16:22 | service.support@crystalgroup.in | YES | APR012 | YES |  |  | 2025-04-17 17:45 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-23 21:23 | 2025-04-10 |  |  |  |  | CBHU281176 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | .8/14bar | 12.2/12.3/12.3 | 407/408/407 | Not done | On call found unit temp. High & check and found internal Evaprator Secrion and bottom air space area block with frosting- ice | Request to clients clean internal frosting area. After run unit working & maintain temp. Need to replaced key pad & HHT SENSOR | Yes | https://drive.google.com/open?id=1vs-t-W_Q8K7W8RIe_Hvs_nvhtpYxmb-O, https://drive.google.com/open?id=1cMbBlKhh3-6dyyvLQHPUU6ljH83cVaCi |  |  | NA | No | No | Can be done on next PM | NA | Key pad/ HTT/ DTS Sensors | technician@crystalgroup.in | REEFER
APR009/25 | 2025-04-05 17:47 | service.support@crystalgroup.in | Dr Reddy CTO5 | T.Sreeram Naik | 7036305829 | Team member-V4 ESD,CTO-V | GSOU6384153 | MOTOR MAKING NOISE, REPAIRS & REPLACEMENT | Shahbuddin | sreeramnt@drreddys.com | Nalgonda | Complete Breakdown | Not working |  |  | 2025-04-05 23:46 | technician@crystalgroup.in | Dr Reddy CTO5 | GSOU6384153 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Evp motor noisy | Need to replaced mot | NA | Yes | Motor bearing issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR009%2F25 | https://drive.google.com/drive/folders/1_ZK5F29US0GgzcZrr1IzFWttLbFPbfY4?usp=sharing | CARRIER-THINLINE | -18 | NA | Carrier | ML-3 | 1001345 | VIRENDRA | Yes | MOTOR MAKING NOISE, REPAIRS & REPLACEMENT | 2025-04-08 12:23 | service.support@crystalgroup.in | YES | 2006-04-01 | 2025-04-08 | Spares | Dr Reddy CTO 5 | Miryalaguda | GSOU6384153 | SITE | FOC | DAIKIN | 2025-04-10 17:39 | service.support@crystalgroup.in | YES | 2006-04-01 | YES |  |  | 2025-04-10 17:44 | service.support@crystalgroup.in | YES | 2006-04-01 | COURIER | 1 | Dolphin |  |  |  | 2025-04-12 15:10 | 2025-04-10 |  |  |  |  | GSOU6384153 |  |  |  | Carrier | +20.0C | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/a 18.3B | 10.0A 9.7A 9.9A | 401V 397V 399V | Not done | Need to replace refergation gas due to air in system l/s evp motor need to be replaced and compressor Contactor 1nos | We have replaced R-134a 4kg | Yes | https://drive.google.com/open?id=1kVZ-R8E5589evfQ1hlFD6iDSOrmw7loo, https://drive.google.com/open?id=1Vz54HJI5WtMuOYzRZM7Q86WI90aqR63F |  |  | TRIPNO 080 | Yes | No | Can be done on next PM | Evp motor work pending | Evp motor router and it's part Compressor Contactor 1nos | technician@crystalgroup.in | REEFER
APR010/25 | 2025-04-08 13:23 | service.support@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | Mr. Rasmihandar | 9831166664 | Head Quality & Projects/SMT/Gop Plant | TTNU9930069 | SERVICING | Shahbuddin | anil.burman@hap.in | Sambalpur | Running with issues | PM |  |  | 2025-04-14 11:05 | service.support@crystalgroup.in | Milk Mantra Dairy Pvt Ltd | TTNU9930069 |  | Thermoking | SERVICE-AT SITE | LEASE | FOC | PM | PM done | NA | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR010%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | USED | NA | SHAHBUDDIN | No | SERVICING | 2025-04-08 15:24 | service.support@crystalgroup.in | YES | 2008-04-01 | 2025-04-08 | Spares | Milk Mantra Dairy Pvt Ltd | Sambalpur | TTNU9930069 | SITE | FOC | TK-MP4000 | 2025-04-14 11:06 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-14 11:06 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-08 15:05 | 2025-04-08 |  |  |  |  | TTNU9930069 |  |  |  | Thermo king | 2 to 8 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20 | 7.2/7.3/7.2 | 405/408/406 | Short | PM | PM DONE as per shoudule | Yes | https://drive.google.com/open?id=1qe3UWBkC7hktIy3ddo4dwKU7n1GwTZ3u, https://drive.google.com/open?id=1rTu0yD8jX-0YfheMaW6n--Or4g-DWYE4 |  |  | NA | No | No | Can be done on next PM | NA | TK MP 4000 DISPLAY | technician@crystalgroup.in | REEFER
APR011/25 | 2025-04-09 13:26 | service.support@crystalgroup.in | ITC Ltd | Uday kumar | 916305208397 | Driver | CXRU1037294 | FLUCTUATIONS IN TEMEPRATURE | Shahbudin/Vinod | tadikonda.sivakumar@itc.in | Bapatla | Running with issues | Not working |  |  | 2025-04-09 16:09 | service.support@crystalgroup.in | ITC Ltd | MYRU4517508 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | Compressor Icing and not reaching to set point | technician aligned | NA | No | Frosting | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR011%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-04-17 17:45 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-17 17:46 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-17 17:47 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-27 17:35 | 2025-04-11 |  |  |  |  | CGMU2990461 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/210 | 12.4/12.6/12.4 | 406/405/406 | Not done | Temp. Issue low gas/ | Leak test & Gas leak from filter Drier - Replaced filter Drier | Yes | https://drive.google.com/open?id=18CBzfpd2ojSFgNux3HA23jFXmxJa9zxV, https://drive.google.com/open?id=1wEa63c-RPAYRLJ2pdVOARB65egdePKCB |  |  | NA | No | No | Can be done on next PM | NA | Filter Drier & Gas 4 kg R 134a | technician@crystalgroup.in | REEFER
APR012/25 | 2025-04-09 15:20 | service.support@crystalgroup.in | Sai Life Science Pvt Ltd | Ashok Sahoo | 8217399165 | Asst Manager | TITU9930032 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Sushma | ashok.sahoo1@cipla.com | Bidar | Running with issues | Unit Tripping |  |  | 2025-04-09 16:29 | service.support@crystalgroup.in | Sai Life Science Pvt ltd | TITU9930032 | 40" | Thermoking Mp-4000 | SERVICE-AT SITE | LEASE | FOC | Unit tripping off | Technician visit | Filter Drier | Yes | High pressure | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR012%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-04-12 17:46 | service.support@crystalgroup.in | YES | 2011-04-01 | 2025-04-12 | Consumables, Spares | Sai Life Science | Bidar | TITU9930032 | SITE | FOC | TK-MP4000 | 2025-04-17 15:45 | service.support@crystalgroup.in | YES | 2011-04-01 | YES |  |  | 2025-04-17 16:07 | service.support@crystalgroup.in | YES | 2011-04-01 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-05-05 14:00 | 2025-05-26 |  |  |  |  | TITU9930032 |  |  |  | Thermo king | -18.0C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | N/A | 9.6A 9.1A 8.5A | 392V 389V 390V | Not done | WE HAVE ATTAND THIS UNIT AND FOUND COMPRESSOR DF | WE HAVE REPLACE COMPRESSOR BUT COMPRESSOR CREATE ABNORMAL NOISE NEED TO REPLACE | Yes | https://drive.google.com/open?id=1XQe0QPYKRMMsuv2Eny7XPd2cqiBJaHwF, https://drive.google.com/open?id=1riA_2R4J8LuN3V4P1x7rWFjUJrVtJI1f |  |  | TRIPNO 084 | Yes | No | Urgent | COMPRESSOR 1NOS COMPRESSOR OIL 3LTR FILLTER DRIER 1NOS N2 FLUSH VACCUM R-404a 5KG GAUGE SET 1NOS | COMPRESSOR 1NOS COMPRESSOR OIL 3LTR FILLTER DRIER 1NOS N2 FLUSH VACCUM R-404a 5KG GAUGE SET 1NOS | technician@crystalgroup.in | REEFER
APR013/25 | 2025-04-10 12:14 | service.support@crystalgroup.in | Navin Fluorine | Viral Shah | 0261 6715540 | Electrical Engineer | CGMU2988654 | Tripping issue | Puspha/Vinod | naimesh.dalia@nfil.in | Surat | Running with issues | Container power cable laid & connection provided(On 08.04.2025) but ELCB tripping issue |  |  | 2025-04-15 18:41 | service.support@crystalgroup.in | Navin Fluorine International Limited | CGMU2988654 | 10FT STD RF | Carrier | Breakdown | LEASE | FOC | Tripping | Light connection wiring |  | No | Electric issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR013%2F25 | NA | CARRIER-THINLINE | -18 | NA | Carrier - Thinline | Used | N/A | SHAHBUDDIN | Yes | Tripping issue | 2025-04-15 18:43 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-15 18:44 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-15 18:44 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-20 16:58 | 2025-04-15 |  |  |  |  | CGMU2988654 |  |  |  | Carrier | +20C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4/200 psig | 12.4/12.5/12.4 | 400/401/401 | Not done | Unit tripping off not working . | On call found with trouble shoot unit tripping off due to internal Lighting shortage with body earth. Temperley disconnected and run unit & observation found maintain set temperature. Next pm need to replaced internal tube light & wiring. | No | https://drive.google.com/open?id=1ADOgMEl4IFJlxfJPNq8B-Du-a9kAmojB, https://drive.google.com/open?id=1WNtRMSMSguONUcCN9hp8YB7ol4rUs19t |  |  | NA | Yes | No | Can be done on next PM | Need to fix new wiring for tube light | Tube light & wire .mcb. | technician@crystalgroup.in | REEFER
APR014/25 | 2025-04-11 18:11 | tender@crystalgroup.in | ITC Ltd | Debanjan Choudhary | 7431808441 | NA | CGMU2990461 | Temperature Issue |  | NA | Bardhaman, Kolkata | Running with issues |  |  |  | 2025-04-12 13:12 | service.support@crystalgroup.in | ITC Limited | CGMU2990461 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Temperature issue | Leak found thru video call. | Filter Drier, R134a gas 4kg | Yes | Temperature Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR014%2F25 | Carrier - Thinline | CARRIER-THINLINE | 4612UD6633 | LSM60197686 | NA | New | NA | SHAHBUDDIN | No | Temperature Issue | 2025-04-12 13:24 | service.support@crystalgroup.in | YES | 2010-04-01 | 2025-04-12 | Consumables, Spares | ITC Limited | Bardhaman | CGMU2990461 | SITE | FOC | CARRIER-THINLINE | 2025-04-17 16:05 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-17 16:05 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-20 16:41 | 2025-04-11 |  |  |  |  | CGMU2990461 |  |  |  | Carrier | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Need to replace | Done | Clean |  | .5/200 psig | 12.4/12.3/12.5 | 405/406/405 | Short | Unit not maintaining temp. & found leakage from filter Drier. | By Vandor: replaced filter Drier /Vcum system/ Gas charging . Unit working fine. | No | https://drive.google.com/open?id=1xYhvYDfoE1AWb1dezKX8Q1jF6LkUz8tu, https://drive.google.com/open?id=1rj6oWz9y7HIC_m2UUgmVLbL0653EuKQW |  |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR015/25 | 2025-04-16 18:21 | swati.barot@crystalgroup.in | Crystal | Virendra |  | na | CR0010 | REPAIRS & REPLACEMENT |  | technician@crystalgroup.in | JNPT | Reefer Machine | EVP Coil leakage |  |  | 2025-04-17 11:17 | technician@crystalgroup.in | Crystal Yard | CR0010 | N/A | 2011 | REPAIR | NA | NA | EVP COIL LEAKAGE | NEED TO REPAIR | EVP COIL 1NOS, FILLTER DRIER 1NOS,R-134a 5KG | Yes | EVP COIL LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR015%2F25 | DAIKIN | DAIKIN LXE10E | MOO2030 | LXE10E147F2 | DECOS IIIF | N/A | N/A | VIRENDRA | No | REPAIRS & REPLACEMENT | 2025-08-08 11:06 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-08 11:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 11:12 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-08 11:13 | [54 empty] | crm@crystalgroup.in | DRY/Others
APR016/25 | 2025-04-16 18:22 | swati.barot@crystalgroup.in | Crystal | Virendra |  | - | CR0002 | REPAIRS & REPLACEMENT |  | technician@crystalgroup.in | JNPT | Running with issues | EVP MOTOR DEFECTIVE |  |  | 2025-04-17 11:12 | technician@crystalgroup.in | Crystal YArd | CR0002 | N/A | 2003-10-01 | REPAIR | NA | NA | LEAKAGE AND STAPPER MOTOR DF,EVP MOTOR DF | NEED TO REPAIR | STAPER MOTOR 1NOS,EVPMOTOR 2NOS,FILLTER DRIER 1NOS,R-134a 5KG CONTROLLER ML3I | Yes | EVPMOTOR DF 2NOS,LEAKAGE ,STAPER MOTOR DF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR016%2F25 | THINELINE | CARRIER-THINLINE | JSL90656195 | 69NT40-541363 | ML2I | N/A | N/A | VIRENDRA | No | REPAIRS & REPLACEMENT | 2025-04-17 17:44 | tender@crystalgroup.in | YES | 2014-04-01 | 2025-04-17 | Consumables, Spares | CRYSTAL YARD | DIGHODE | CR0002 | DEPOT | FOC | CARRIER-THINLINE | 2025-05-20 14:24 | qualitycontrol@crystalgroup.in | NO |  |  |  |  | 2025-05-22 06:48 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-05-22 06:49 | [5 empty] | CR0002 | [48 empty] | qualitycontrol@crystalgroup.in | DRY/Others
APR017/25 | 2025-04-16 18:23 | swati.barot@crystalgroup.in | Crystal | vIREDNRA |  | - | CR0011 | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE, REPAIRS & REPLACEMENT |  | tECHNICIAN@CRYSTALGROUP.IN | JNPT | Running with issues | LEAKAGE AND COMPRESSOR DEFECTIVE |  |  | 2025-04-17 10:50 | technician@crystalgroup.in | Crystal Yard | CR0011 | N/A | 2010 | REPAIR | NA | NA | LEAKAGE FROM LSV VALVE,EVP MOTOR DF , | NEED TO REPAIR | LSVALVE, EVP MOTOR 2NOS, COMPRESSOR OIL 3LTR, COMPRESSOR 1NOS, FILLTER DRIER 1NOS, SECTION AND DISCHARGE GASKIT | Yes | LEAKAGE AND EVP MOTOR DF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR017%2F25 | DAIKIN | DAIKIN LXE10E | M003245 | LXE10E136A2 | DECOS IIIE | N/A | N/A | VIRENDRA | No | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE, REPAIRS & REPLACEMENT | 2025-08-08 11:18 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-08 14:30 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-29 15:37 | crm@crystalgroup.in | NO
APR018/25 | 2025-04-16 18:27 | swati.barot@crystalgroup.in | Crystal JNPT | vIRENDRA |  | - | CR0012 | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE, LEAKAGE |  | TECHNICIAN@CRYSTALGROUP.IN | JNPT | Running with issues |  |  |  | 2025-04-17 10:43 | technician@crystalgroup.in | CRYSTAL GROUP | CR0012 | N/a | Thineline | REPAIR | NA | NA | Staper motor df 1nos Evp motor df 2nos Compressor heavy rusted to replace | NEED REPAIR | STAPER MOTOR 1NOS, EVP MOTOR 2NOS, FILLTER DRIER 1NOS, SECTION AND DISCHARGE GASKIT 1NOS EACH | Yes | STAPER MOTOR DF ,EVP MOTOR DF, | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR018%2F25 | Yes | CARRIER-THINLINE | NSG60383850 | 69NT40-541-320 | ML3I | N/A | N/A | VIRENDRA | No | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE, LEAKAGE | 2025-04-17 18:02 | tender@crystalgroup.in | YES | 2015-04-01 | 2025-04-17 | Consumables, Spares | CRYSTAL YARD | Dighode | CR0012 | DEPOT | FOC | CARRIER-THINLINE | 2025-05-20 14:29 | qualitycontrol@crystalgroup.in | NO |  |  |  |  | 2025-05-22 12:20 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-05-22 12:21 | [54 empty] | qualitycontrol@crystalgroup.in | DRY/Others
APR019/25 | 2025-04-17 14:38 | service.support@crystalgroup.in | Tianish Laboratories Private Limited | R V SURYANARAYANA | 8008999353 | GM | TRLU1741601 | Humdity setting issue | Puspha/Vinod | suryanarayana.rampalli@tianishpharma.com | Chodavaram | Running with issues | Humdity setting issue |  |  | 2025-04-17 14:58 | service.support@crystalgroup.in | Tianish Laboratories Private Limited | TRLU1741601 | 40FT STD RF | Thermo King | SERVICE-ON CALL | LEASE | FOC | Humidity setting issue | Guide setting process for humidity set |  | No | Setting issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR019%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | used | NA | VIRENDRA | No | Humdity setting issue | 2025-04-17 14:59 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-17 15:05 | service.support@crystalgroup.in | NO |  |  |  |  | 2025-04-17 15:20 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-17 15:45 | 2025-04-17 |  |  |  |  | TRLU1741601 |  |  |  | Thermo king | N/a | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | N/a | N/a | N/a | Not done | Humidity not set up | We have set humidity on phone call | No | https://drive.google.com/open?id=1Zbg96o11S4zhWUdUZdbuuBJxEcmpasF2, https://drive.google.com/open?id=1mmc0KoCpLvEtm4dgKQfTGOtlEKgmvXv6 |  |  | N/a | No | No | Can be done on next PM | N/a | N/a | technician@crystalgroup.in | REEFER
APR020/25 | 2025-04-19 10:48 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | PRGU4958724 | Breakdown | Shahbudin | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues | Not working |  |  | 2025-04-21 11:52 | technician@crystalgroup.in | Lauras Lab Unit 2 | PRGU4958724 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Evaprator & condenser fan motor not working | Waiting spare | ML controller/ Evaprator motor & condenser fan blade | Yes | Motor break down | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR020%2F25 | Carrier- Thin Line | CARRIER-THINLINE | NA | NA | NA | Usam | Used | SHAHBUDDIN | Yes | Breakdown | 2025-04-19 12:20 | service.support@crystalgroup.in | NO | [9 empty] | 2025-05-12 16:28 | crm@crystalgroup.in | YES | 2024-04-01 | YES |  | Stock | [10 empty] | 2025-06-02 22:37 | 2025-05-29 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | +5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.5 | 12.5 | 404 | Not done | Found unit off & wrong connection R/ EVP Motor | Fix wrong connection, Replaced L/S Evp moto with good one, Fix condenser fan blade with new one.AA59& 60 Av need to replace HTT & Defrost sensor. Key pad not working, Need to fix controller . | Yes | https://drive.google.com/open?id=1dY3ZFEDLSMj46EANdHRgXkBIcVAcwN_x | https://drive.google.com/open?id=17ap5UGQsuFMstMYUcIpQc4D1V_1TALiE |  | NA | Yes | Yes | Urgent | 1)Defrost sensor 2)HTT 3)Key pad 4)Controller configuration. | 1)Defrost sensor 2)HTT 3)Key pad | rrmondal.786@gmail.com | REEFER
APR021/25 | 2025-04-19 10:50 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | GESU9529290 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 12:03 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9529290 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR021%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:21 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:37 | technician@crystalgroup.in | NO | [14 empty] | 2025-04-20 14:55 | 2025-04-19 |  |  |  |  | GESU9529290 |  |  |  | Carrier | +23C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190 psig | 12.3/12.4/12.3 | 398/ 399/399 | Short | Unit working as satisfactory | PM job completed | No | https://drive.google.com/open?id=1yJEGPFp86H83DVlxYgOA6kkqzI3HMHI2, https://drive.google.com/open?id=10Pv9Uk9Rx05FWRaG7zGbPzHNeJGhEcKq |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR022/25 | 2025-04-19 10:52 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | GESU9454776 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:44 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9454776 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM | EVP MOTOR SINGLE PHASE | Yes | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR022%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:21 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:39 | technician@crystalgroup.in | NO | [14 empty] | 2025-04-30 11:21 | 2025-04-18 |  |  |  |  | GESU9454776 |  |  |  | Carrier | +22c | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/180 psig | 12.4/12.5/12.4 | 399/398/399 | Short | Unit working as satisfactory with Evp. Noisy | PM completed and waiting Evaprator motor need to replaced | Yes | https://drive.google.com/open?id=1atmToLDbIlojYKFtH88t2MpvKF2gpNSl |  |  | 83 | Yes | No | Can be done on next PM | Need to rep. Evp. | Evaprator .motor thin line carrier - single phase | technician@crystalgroup.in | REEFER
APR023/25 | 2025-04-19 10:53 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | TITU9930222 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:46 | service.support@crystalgroup.in | Lauras Lab Unit 2 | TITU99302223 | 40FT Spl RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM | CURTAIN LIGHT MP4000 DISPLAY | YES | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR023%2F25 | Thermoking MP-4000 | TK-MP4000 | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:21 | service.support@crystalgroup.in | NO | [26 empty] | 2025-04-30 11:31 | 2025-04-18 |  |  |  |  | TITU9930222 |  |  |  | Thermo king | +22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/20br | 10.2/10.3/10.2 | 398/397/397 | Short | Unit working as satisfactory with Display Defective | PM Complited & need to replaced tk mp 4000 Display . Clints request for courtan | Yes | https://drive.google.com/open?id=13qDKyM1LZcxgc-cYZZimxsN6iZoJOPxI |  |  | 83 | No | No | Can be done on next PM | NA | Tk mp 4000 Display & courtan door | technician@crystalgroup.in | REEFER
APR024/25 | 2025-04-19 10:54 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | CXRU2031845 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:53 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CXRU2031845 | 40ft | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR024%2F25 | NA | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:22 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:37 | technician@crystalgroup.in | NO | [14 empty] | 2025-04-20 15:15 | 2025-04-18 |  |  |  |  | CXRU1031845 |  |  |  | Daikin | +22C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/200 psig | 9.9/9.8/9.8 | 399/398/399 | Short | Found AL E 406- suction gas sensor & ALE 411 Ambient sensor faulty3. Sheet key & Dispaly broken. | Repaired & Replaced suction gas sensor & Ambi | No | https://drive.google.com/open?id=1ML-D-rgayi8bwzZ5Z7rddZp1l9QmyLFk, https://drive.google.com/open?id=12hivgc8ANAc0yWraViOA034D7LxeM1cM |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR025/25 | 2025-04-19 10:55 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | CRSU6101910 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:51 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CRSU6101910 | 40FT STD RF | Carrier | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR025%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:22 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:37 | technician@crystalgroup.in | NO |  |  |  |  | 2025-04-20 14:30 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-20 14:39 | 2025-04-19 |  |  |  |  | CRSU6101910 |  |  |  | Carrier | + 4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/190 psig | 12.3/12.4/12.4 | 399/398/398 | Short | Unit workingassatisfactory | PM job completed | No | https://drive.google.com/open?id=154jxWNF_Y9vPVMZhmoAGzMuqoNnNsSyk, https://drive.google.com/open?id=132fy8-rNpsNEFqnYnTzG3MEi2eYYma6r |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR026/25 | 2025-04-19 10:57 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | CXRU1036533 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:55 | service.support@crystalgroup.in | Lauras Lab Unit 2 | CXRU1036533 | 40ft | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR026%2F25 | NA | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:22 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-25 10:50 | tender@crystalgroup.in | NO
APR027/25 | 2025-04-19 10:58 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | BMOU9782197 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:56 | service.support@crystalgroup.in | Lauras Lab Unit 2 | BMOU9782197 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR027%2F25 | DAikin | DAIKIN | NA | DECOSIIIF/2553/1 | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:23 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:37 | technician@crystalgroup.in | NO | [14 empty] | 2025-04-20 15:34 | 2025-04-19 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | +22C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/180 psig | 9.8/9.9/9.8 | 399/399/398 | Short | Found AL E 411- Ambient sensor faulty | Replaced Ambient sensor | No | https://drive.google.com/open?id=1yj9yoD_0365YdVeUNeH6PyQiuagi7CCS, https://drive.google.com/open?id=1FexAX4K0iS1H8MfNbJWlMgH-0z324wQX |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR028/25 | 2025-04-19 10:59 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | HDMU5584444 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 11:59 | service.support@crystalgroup.in | Lauras Lab Unit 2 | HDMU5584444 | 40FT STD RF | Thermo King | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR028%2F25 | Thermoking MP 4000 | TK-MP4000 | NA | NA | NA | USed | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:23 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:35 | technician@crystalgroup.in | NO | [14 empty] | 2025-04-20 15:59 | 2025-04-20 |  |  |  |  | HDMU5584444 |  |  |  | Thermo king | +5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/22 bar | 9.9/9.8/9.9 | 399/398/399 | Short | Unit working as satisfactory | PM service complited | No | https://drive.google.com/open?id=13i1pOcWx1qV-l1YTJr2pPKTvp8w-pVPt, https://drive.google.com/open?id=1R546ksFTJij0SnwoCXOfNKENizpvZQk3 |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR029/25 | 2025-04-19 11:00 | service.support@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site incharge | HDMU5586473 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-19 12:01 | service.support@crystalgroup.in | Lauras Lab Unit 2 | HDMU5586473 | 40FT STD RF | Thermoking | PREVENTIVE MAINTENANCE | LEASE | FOC | PM | PM |  |  | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR029%2F25 | Thermoking MP 4000 | TK-MP4000 | PM | PM | PM | USed | NA | SHAHBUDDIN | Yes |  | 2025-04-19 12:24 | service.support@crystalgroup.in | NO | [9 empty] | 2025-04-20 13:34 | technician@crystalgroup.in | NO |  |  |  |  | 2025-04-20 13:34 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-20 15:47 | 2025-04-20 |  |  |  |  | HDMU5586473 |  |  |  | Thermo king | +20C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6bar/21bar | 9.8/9.9/9.8 | 399/399/398 | Short | Unit working as satisfactory | PM service complited | No | https://drive.google.com/open?id=1UVVpjc_8ynawVazR2sGeQxBPH4Oc6vOr, https://drive.google.com/open?id=1fcKmBjJBwGeCdqx57jC7xPqYG015Kfmf |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR030/25 | 2025-04-19 16:35 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | WIKU5237623 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:49 | tender@crystalgroup.in | Mundra Depot | WIKU5237623 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR030%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-04-21 11:54 | tender@crystalgroup.in | YES | 2017-04-01 | 2025-04-21 | Consumables | Mundra Depot | Mundra | WIKU5237623 | SITE | FOC | DRY | 2025-04-21 15:38 | tender@crystalgroup.in | YES | 2017-04-01 | YES | https://drive.google.com/open?id=1UqWPVzCw5V1IGAIGH9DaHt_Umu4tyqro |  | 2025-04-23 11:07 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-24 16:10 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR031/25 | 2025-04-19 16:37 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | HNKU6113303 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:51 | tender@crystalgroup.in | Mundra Depot | HNKU6113303 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR031%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-04-21 11:55 | tender@crystalgroup.in | YES | 2018-04-01 | 2025-04-22 | Consumables | Mundra Depot | Mundra | HNKU6113303 | DEPOT | FOC | DRY | 2025-04-21 15:38 | tender@crystalgroup.in | YES | 2018-04-01 | YES | https://drive.google.com/open?id=15YPabwQPRkwpEprNbj8FkhUBIFOnZxps |  | 2025-04-23 11:08 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-24 16:10 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR032/25 | 2025-04-19 16:38 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | WIKU5243523 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:53 | tender@crystalgroup.in | Mundra Depot | WIKU5243523 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | Paint | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR032%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-04-21 11:57 | tender@crystalgroup.in | YES | 2019-04-01 | 2025-04-21 | Consumables | Mundra Depot | Mundra | WIKU5243523 | DEPOT | FOC | DRY | 2025-04-21 15:42 | tender@crystalgroup.in | YES | 2019-04-01 | YES | https://drive.google.com/open?id=1luUkBOtqfgoa1z2h-3CVjo8JqKHxlV9D |  | 2025-04-25 14:12 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-28 16:38 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR033/25 | 2025-04-19 16:40 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | HNKU6272619 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:55 | tender@crystalgroup.in | Mundra Depot | HNKU6272619 | 40ft HC | NA | REPAIR | SALE | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR033%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-04-21 12:05 | tender@crystalgroup.in | YES | 2020-04-01 | 2025-04-21 | Consumables | Mundra Depot | Mundra | HNKU6272619 | DEPOT | FOC | DRY | 2025-04-21 15:43 | tender@crystalgroup.in | YES | 2020-04-01 | YES | https://drive.google.com/open?id=14pEZwU4sysoUXz7l0kh6S9lY1u2eMJBW |  | 2025-04-28 16:39 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-29 16:40 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR034/25 | 2025-04-19 16:41 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | HNKU6272820 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:56 | tender@crystalgroup.in | Mundra Depot | HNKU6272820 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | NA | NA | NA | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR034%2F25 | NA | DRY | NA | NA | NA | Brand New | na | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-04-21 12:06 | tender@crystalgroup.in | YES | 2021-04-01 | 2025-04-21 | Consumables | Mundra Depot | Mundra | HNKU6272820 | DEPOT | FOC | DRY | 2025-04-21 15:49 | tender@crystalgroup.in | YES | 2021-04-01 | YES | https://drive.google.com/open?id=1LcFtC6QMQbJFOo5ez2BrU1Fhgq0tDs3r |  | 2025-04-23 11:08 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-24 16:11 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR035/25 | 2025-04-19 16:42 | tender@crystalgroup.in | Mundra Depot | Azad | 9099619083 | NA | HNKU6282622 | REPAIRS & REPLACEMENT |  | NA | Mundra | Repair Work |  |  |  | 2025-04-19 17:58 | tender@crystalgroup.in | Mundra Depot | HNKU6282622 | 40ft HC | NA | REPAIR | SALE | CHARGEABLE | NA | NA | NA | No | PAINT | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR035%2F25 | NA | DRY | NA | NA | NA | Brand New | NA | AKSHAY | No | REPAIRS & REPLACEMENT | 2025-04-21 12:09 | tender@crystalgroup.in | YES | 2022-04-01 | 2025-04-21 | Consumables | Mundra Depot | Mundra | HNKU6282622 | DEPOT | FOC | DRY | 2025-04-21 15:50 | tender@crystalgroup.in | YES | 2022-04-01 | YES | https://drive.google.com/open?id=1GnckrMq3TeWaIfdchIGpnsaFStei7sc_ |  | 2025-04-25 14:11 | purchase.ops@crystalgroup.in | NO | [7 empty] | 2025-04-28 16:38 | [54 empty] | purchase.ops@crystalgroup.in | DRY/Others
APR036/25 | 2025-04-22 14:47 | kam@crystalgroup.in | Swadesh Milk | Vibhuti | 7459091115 | Purchase | GESU9290991 | REPAIRS & REPLACEMENT, Condenser fan motor with blade | Shahbuddin | v.nsingh@hotmail.com | Barabanki Bihar | Spares requirement | bearing noise issue in its fan. |  |  | 2025-04-23 20:53 | technician@crystalgroup.in | SWADESH MILK | GESU9290991 | 40" | CARRIER | SERVICE-AT SITE | SALE | CHARGEABLE | Condenser fan motor heavy Noisy | Need to replaced | Condenser Fan Motor - carrier thin line single phase with Fan Blade. | Yes | Motor Rust with old | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR036%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | No | REPAIRS & REPLACEMENT, Condenser fan motor with blade | 2025-04-22 16:44 | tender@crystalgroup.in | YES | 2023-04-01 | 2025-04-22 | Spares | Swadesh Mill | Barabokmi | GESU9290991 | SITE | FOC | CARRIER-THINLINE | 2025-05-08 18:08 | operation@crystalgroup.in | YES | 2023-04-01 | YES |  | Stock | [10 empty] | 2025-05-29 15:41 | 2025-04-21 |  |  |  |  | GESU9290991 |  |  |  | Carrier | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/18br | 12.4/12.5/12.4 | 402/404/402 | Not done | Unit Instalation done . Unit tripping off & found Earth is not provided properly...advise to earth pit and properly for earth. After run unit obs operation and found worked Unit. | Unit observation on vedeo call found working as normal | No | https://drive.google.com/open?id=1Oglr3uusTexJLy-GgT7ICUjcre1T8nhE | https://drive.google.com/open?id=1rf8TXzLml8TsgA6EDkOWGhfEifArOsDq |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR037/25 | 2025-04-23 11:31 | tender@crystalgroup.in | Crystal Vizag Depot | PRAVALICK | 9133228334 | NA | MYRU4509035 | REPAIRS & REPLACEMENT |  | NA | Vishakapatnam | Repair & PTI |  |  |  | 2025-04-23 15:11 | technician@crystalgroup.in | Crystal Vizag Depot | MYRU4509035 | 40FT STD RF | Daikin | SERVICE-AT SITE | STOCK | FOC | Power cable & plug missing and for PTI | Spare arrange | 15 Mt power cable and powwer plug with 16A ncb | Yes | Empty repair missing cable & plug mcb | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR037%2F25 | Daikin | DAIKIN | 802602 | LXE10E136A | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-04-25 15:06 | tender@crystalgroup.in | YES | 2027-04-01 | 2025-04-25 | Spares | Crystal Vizag Depot | Vizag | MYRU4509035 | SITE | FOC | DAIKIN | 2025-04-28 15:23 | operation@crystalgroup.in | YES | 2027-04-01 | YES | https://drive.google.com/open?id=1LqYd_pRDS3P-2S1GCXN85G51PkFGubPV | Vendor | 2025-04-29 11:03 | operation@crystalgroup.in | YES | 2027-04-01 | ARRENGING AT SITE | [5 empty] | 2025-04-28 19:59 | 2025-04-21 |  |  |  |  | MYRU4509035 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0/210 br | 9.9/9.8/9.9 | 412/413/412 | Full | Empty unit at Vishakapatnam. Kamal Depo : Found main power cable & plug missingwith Light MCB | Fixed 15 Mtr . Cable with power plugand light ncb . Run unit test PTI Pass | Yes | https://drive.google.com/open?id=1nzzRvJlkNx0Get5k8jjX_9bHDstrPmH4 |  |  | 83 | No | No | Can be done on next PM | NA | 15 mtr power cable & power plug and 16A mcb for light | technician@crystalgroup.in | REEFER
APR038/25 | 2025-04-23 11:34 | tender@crystalgroup.in | Crystal Vizag Depot | PRAVALICK | 9133228334 | NA | ARCU4530675 | REPAIRS & REPLACEMENT |  | NA | Vishakapatnam | Repair & PTI |  |  |  | 2025-04-23 15:06 | technician@crystalgroup.in | Crystal Vizag Depot | ARCU4530675 | 40" | Carrier | SERVICE-AT SITE | STOCK | FOC | Power cable & plug missing after PTI | Fixed cable plug | 15 never power cable & power plug with 15 A mcb | Yes | Empty repair & Pti | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR038%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-04-25 15:08 | tender@crystalgroup.in | YES | 2028-04-01 | 2025-04-25 | Spares | Crystal Vizag Depot | Vizag | ARCU4530675 | SITE | FOC | CARRIER-THINLINE | 2025-04-28 15:24 | operation@crystalgroup.in | YES | 2028-04-01 | YES | https://drive.google.com/open?id=1xu5NFSoT6ablgdjDiB3Y_N-lOjOkosuZ | Vendor | 2025-04-29 11:03 | operation@crystalgroup.in | YES | 2028-04-01 | ARRENGING AT SITE | [5 empty] | 2025-04-28 20:10 | 2025-04-22 |  |  |  |  | ARCU4530675 |  |  |  | Carrier | +2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/16br | 12.4/12.3/12.4 | 412/413/412 | Short | Empty Depo Vishakapatnam- kamal Ent. Found main power cable missing with power plug. | Fixed new 15 mtr. Power cable & plug .run unit test in PTI PASS SHORT - UNIT USE FOR +2 to 8 cargo only....... | Yes | https://drive.google.com/open?id=1yZ6oHdJSLheNG_t7MHGWfbmbPW99Y3k2 |  |  | 83 | No | No | Can be done on next PM | NA | 15 mtr power cable & plug | technician@crystalgroup.in | REEFER
APR039/25 | 2025-04-24 18:57 | tender@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | MYRU4505847 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-25 01:00 | technician@crystalgroup.in | Laurus Unit 3 | MYRU4505847 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | Done | NA | No | Pm service only | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR039%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | No |  | 2025-04-25 11:18 | tender@crystalgroup.in | NO | [9 empty] | 2025-04-25 11:18 | tender@crystalgroup.in | NO |  |  |  |  | 2025-04-25 15:29 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-25 01:07 | 2025-04-24 |  |  |  |  | MYRU4505847 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19 bar | 9.9/9.8/9.9 | 402/403/403 | Short | Unit working as satisfactory | PM SERVICE DONE with clean condenser coil with fresh water. | No | https://drive.google.com/open?id=1PPl4MMxEDalCO-DvIX9JsTX1W2n0nJ2o, https://drive.google.com/open?id=1E-c23JCqtikIudXdn1vgaMF8i2WTvi01 |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR040/25 | 2025-04-24 18:58 | tender@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | PCLU1912290 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-25 00:44 | technician@crystalgroup.in | Laurus Unit 3 | PCLU1912290 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | PM service | PM service arranged | EIS SENSOR & TEMP. SENSOR | Yes | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR040%2F25 | Daikin | DAIKIN | MFG:M .004715 | NA | NA | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-04-25 00:56 | 2025-04-24 |  |  |  |  | TCLU1912290 |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/20 bar | 9.9/9.8/9.7 | 406/407/407 | Short | Fail unit with AL E 407 | Need to replaced EIS Sensors | Yes | https://drive.google.com/open?id=1DrOTdSqFFwkT8ZSRHAn-SHh5Hdnpqh3Q, https://drive.google.com/open?id=1x7U-Kqpl1lAtZuuTAaeBehBoyN_ORWuJ |  |  | 83 | Yes | No | Can be done on next PM | Need to replaced EIS Sensors | EIS . TEMP. SENSOR | technician@crystalgroup.in | REEFER
APR041/25 | 2025-04-24 18:59 | tender@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | +91 99853 69677 | NA | BMOU9784137 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-25 00:19 | technician@crystalgroup.in | Laurus Unit 3 | BMOU9784137 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | PM SERVICE DONE | Daikin sheet key complit set /EIS /EOS/TEMP. SENSOR | Yes | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR041%2F25 | Daikin | DAIKIN | NA | NA | NA | used | NA | SHAHBUDDIN | Yes |  | 2025-05-06 17:24 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:35 | crm@crystalgroup.in | NO | [14 empty] | 2025-04-25 00:31 | 2025-04-24 |  |  |  |  | BMOU9784137 |  |  |  | Daikin | -12c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/19 bar | 9.8/9.9/9.8 | 406/405/406 | Not done | Found unit Display cover & key pad da.aged.and EIS/EOS/STS TEMP. SENSOR READING ABNORMAL | PM Complited with clean condenser coil and | Yes | https://drive.google.com/open?id=1T1JLB264UqkvGwcgcDIDFi56MJYeQiPE |  |  | 83 | Yes | No | Can be done on next PM | Need to replaced sheet key & sensor | Daikin sheet key / EOS/ EOS/TEMP. SENSOR | technician@crystalgroup.in | REEFER
APR042/25 | 2025-04-24 19:00 | tender@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | +91 99853 69677 | NA | TDRU7153256 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-25 00:04 | technician@crystalgroup.in | Laurus Unit 3 | TDRU7153256 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | PM service | PM service Done | NA | No | Pm service due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR042%2F25 | Daikin | DAIKIN | MFG : A001117 | NA | NA | used | NA | SHAHBUDDIN | Yes |  | 2025-04-25 11:18 | tender@crystalgroup.in | NO | [9 empty] | 2025-04-25 11:21 | tender@crystalgroup.in | NO |  |  |  |  | 2025-04-25 15:28 | service.support@crystalgroup.in | NO | [7 empty] | 2025-04-25 00:16 | 2025-04-24 |  |  |  |  | TDRU7153256 |  |  |  | Daikin | +4.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/19 bar | 10.1/10.2/10.1 | 406/405/405 | Short | Unit for pm service | PM service complited/ and clean condenser coil | No | https://drive.google.com/open?id=1dqDVgtGnE6iQrP71WkL4FAiYCv0SxAM2, https://drive.google.com/open?id=1OIFbbs5VDCpdVSrdA9Wl1t99_OB_D32E |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR043/25 | 2025-04-28 13:10 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | KKFU6711724 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 15:34 | technician@crystalgroup.in | Laurus Unit 3 | KKFU6711724 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service | PM service Done | NA | No | Due pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR043%2F25 | Carrier - Thinline | CARRIER-THINLINE | LSX60253435 | 541321 | 5487 | used | NA | SHAHBUDDIN | Yes |  | 2025-05-01 16:35 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-01 16:44 | operation@crystalgroup.in | NO | [14 empty] | 2025-04-28 15:44 | 2025-04-24 |  |  |  |  | KKFU6711724 |  |  |  | Carrier | 20 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .3/14 bar | 12.3/12.4/12.4 | 405/406/405 | Short | Unit working as satisfactory | PM SERVICE DONE | No | https://drive.google.com/open?id=1wdrzk8kThT00O1ZnSIkcFH_vCjqmVdmP |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR044/25 | 2025-04-28 13:11 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | MYRU4519115 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 15:48 | technician@crystalgroup.in | Laurus Unit 3 | MYRU4519115 | 40FT STD RF | Dakin | SERVICE-AT SITE | LEASE | FOC | PM Due | PM SERVICE DONE | NA | No | P. M. Due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR044%2F25 | Daikin | DAIKIN | 806162 | LXE10E136A2 | Na | Refurbished | NA | SHAHBUDDIN | Yes |  | 2025-05-01 16:35 | operation@crystalgroup.in | NO | [26 empty] | 2025-04-28 15:58 | 2025-04-25 |  |  |  |  | MYRU4519115 |  |  |  | Daikin | + 20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20 bar | 10.2/10.1/10.2 | 406/407/407 | Short | Unit working as satisfactory | PM SERVICE DONE | No | https://drive.google.com/open?id=12fGhHlfR2Im6dmbp3rJblbHnhAA803cg |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR045/25 | 2025-04-28 14:20 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | KKFU6710760 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 16:30 | technician@crystalgroup.in | Laurus Unit 3 | KKFU6710760 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Due pm | PM DONE | Supply sensor cartoer nos.2 & Discharge transducer jack | Yes | Pm due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR045%2F25 | Carrier - Thin line | CARRIER-THINLINE | LSU60253959 | 541321 | 5167 | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-04-28 16:41 | 2025-04-25 |  |  |  |  | KKFU6710760 |  |  |  | Carrier | +21c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/13bar | 12.3/12.4/22.3 | 406/407/407 | Short | Unit working as satisfactory | PM DONE & Need to replaced Discharge transducer jack , Temperley by pass and need two supply sensor | Yes | https://drive.google.com/open?id=1LuoQAt8IDhgLIv8Nrn-nGvNxKDBRizEf |  |  | 83 | No | No | Can be done on next PM | NA | Two supply sensor carrier & dis . Ja k. | technician@crystalgroup.in | REEFER
APR046/25 | 2025-04-28 14:21 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | APRU5091340 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 16:46 | technician@crystalgroup.in | Laurus Unit 3 | APRU5091340 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Due pm | P. M. Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR046%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA A | Used | NA | SHAHBUDDIN | Yes |  | 2025-05-01 16:37 | operation@crystalgroup.in | NO | [26 empty] | 2025-04-28 16:56 | 2025-04-25 |  |  |  |  | APRU5091340 |  |  |  | Daikin | +25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/21bar | 9.9/9.9/9.8 | 407/408/408 | Short | Unit working as satisfactory | PM DONE | No | https://drive.google.com/open?id=17zcPGh5wYMs9yF2_bBGze2nsxFJHul_f |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR047/25 | 2025-04-28 14:23 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | SUDU6257274 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 17:08 | technician@crystalgroup.in | Laurus unit 3 | SUDU6257274 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Due pm | PM Done | NA | No | Due pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR047%2F25 | Carrier - prime line | CARRIER-PRIMLINE | NSR60443683 | NA | NA | Used | NA | SHAHBUDDIN | Yes |  | 2025-05-01 16:37 | operation@crystalgroup.in | NO | [26 empty] | 2025-04-28 17:16 | 2025-04-25 |  |  |  |  | SUDU6257274 |  |  |  | Carrier | +2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/14bar | 9.8/9.9/9.8 | 406/407/406 | Short | Unit working as satisfactorypm complited | PM Complited | No | https://drive.google.com/open?id=10z9SHetKC0QY9HY-85je0bc9djEQxPxY |  |  | 83 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR048/25 | 2025-04-28 14:24 | operation@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | DFOU6120384 |  |  | NA | Vishakapatnam | Preventive Maintenance |  |  |  | 2025-04-28 17:33 | technician@crystalgroup.in | Laurus Unit 3 | DFOU6120384 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Due pm | P. M. Complit | PT/CT BOARD & EIS DAIKIN SENSOR | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR048%2F25 | Daikin | DAIKIN LXE10E | MOO4338 | NANA | NA | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-04-28 17:51 | 2025-04-25 |  |  |  |  | DFOU6120384 |  |  |  | Daikin | +22 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/20bar | 9.9/9.8/9.8 | 406/407/407 | Short | PM Complited | Unit working as satisfactory | Yes | https://drive.google.com/open?id=1PVRl2u9J6DnIXP7ykRngvY8rlxyBkSuc |  |  | 83 | No | No | Can be done on next PM | NA | Eis sensor daikin & PTCT BOARD | technician@crystalgroup.in | REEFER
APR049/25 | 2025-04-28 18:11 | operation@crystalgroup.in | Zepto | Mr. Happy Singh | 9717519295 | NA | SEGU9052030 | ALARM CODE VISIBLE, Power Fluctuation | Kunal | narender.kumar@zeptonow.com | Faruk Nagar, Haryana | Running with issues |  |  |  | 2025-04-29 15:11 | technician@crystalgroup.in | Zepto | SEGU9052030 | 40FT STD RF | Carrier prime line | SERVICE-AT SITE | LEASE | FOC | Tripping | Tech on way | NA | No | Power issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR049%2F25 | Carrier | CARRIER-PRIMLINE | NANA | NA | NA | Used | NA | RAJ KUMAR | Yes | ALARM CODE VISIBLE, Power Fluctuation | 2025-05-01 16:49 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-01 16:50 | operation@crystalgroup.in | NO | [14 empty] | 2025-05-06 20:34 | 2025-04-30 |  |  |  |  | SEGU9052030 |  |  |  | Carrier | +10.1c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-1.7bar. d-15.3bar | R-10.0a. B-9.9a. Y-10.1a | L1-384v. L2-385v. L3-384v | Short | We have attende tha unit found condenser coil durty and al-23 phese loss | We have work condenser coil wash with normal water and supply re connection alarm 23 clear After unit running sound condition | No | https://drive.google.com/open?id=1rq4pVbeiegfA66xJJ2GRFygvTTc6aNGU | https://drive.google.com/open?id=1qG301L_otpXw8tx4q_WZJ5X4YCcN89R- |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
APR050/25 | 2025-04-28 18:40 | operation@crystalgroup.in | Indradeep Infra India Private Limited | S. Rama Reddy | 9701670090 | Site Engineer | MYRU4513729 | Temperature Issue |  | NA | Kandivali | Running with issues |  |  |  | 2025-04-28 18:44 | technician@crystalgroup.in | Indradeep Construction | MYRU4513729 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp. Sensor abnormal reading | Check & need to replaced | Daikin supply sensor nos. 3 | Yes | Sensors dauilty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR050%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | Yes | Temperature Issue | 2025-05-02 15:40 | operation@crystalgroup.in | YES | 1931-04-01 | 2025-04-29 | Spares | INDRADEEP CONSTRUCTION | Kandivali | MYRU4513729 | SITE | FOC | DAIKIN | 2025-05-02 15:46 | operation@crystalgroup.in | YES | 1931-04-01 | YES |  | Stock | 2025-05-10 13:09 | crm@crystalgroup.in | YES | 1931-04-01 | TECHNICIAN |  |  | Sarvesh |  |  | 2025-05-07 22:51 | 2025-05-01 |  |  |  |  | MYRU 4513429 |  |  |  | Daikin | 12 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1V24UENnWyvMwFLZfzeQkTO0vBUlQGvtt | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S- 0.6 And D- 210 | 9.6, 9.5, 9.6 | 395396394 | Short | PM service complete Temperature issue Return sencer is defective | 1 return sencer replace again sort PTI pass no any issue | Yes | https://drive.google.com/open?id=1oes-88gW_Dgcsif4Gt8hPIU8spc6Y3vF | https://drive.google.com/open?id=1OM2mL9UMtADlO7xgBzg0Nzb5UHaMK6Jt |  | Na | No | No | Can be done on next PM | NA | 1 return sencer | sarveshk392@gmail.com | REEFER
APR051/25 | 2025-04-29 12:24 | tender@crystalgroup.in | Gyan Enterprises | P K Sharma | +977 980 2520211 | NA | CXRU1030854 | COMPRESSOR MAKING NOISE | Pushpa ma'am | NA | Nepal | Running with issues | Compressor Noisy Need to replace |  |  | 2025-04-29 14:57 | technician@crystalgroup.in | Gyan Enterprises Nepal gung | CXRU1030854 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor Noisy & leak back | Need to replaced | DIkin compressor/ suction gasket / O ring discharge/ filter Drier / Gas R 134a 5 kg/ Nitogen leak test/ vacum pump | Yes | Frequency | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR051%2F25 | Daikin | DAIKIN LXE10E | M000843 | K31410138906 | DECOS 3F 2551 / 1 | Used | NA | RAJ KUMAR | Yes | COMPRESSOR MAKING NOISE | 2025-05-01 17:23 | operation@crystalgroup.in | YES | 2029-04-01 | 2025-04-25 | Consumables, Spares | Gyan Enterprises Nepal gung | Nepal | CXRU1030854 | SITE | FOC | DAIKIN | 2025-08-08 14:32 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 14:32 | crm@crystalgroup.in | NO
APR052/25 | 2025-04-29 12:42 | operation@crystalgroup.in | Qwik Supply | Mr. Rambabu | 7869533375 | NA | CRLU6220410 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Kunal | NA | Bhopal | Running with issues | (-22 REQUIRED TEMPERATURE) (temperature achieved up to -16 only) |  |  | 2025-05-02 16:39 | technician@crystalgroup.in | Qwik Supply | CRLU6220410 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp | Advise to clints duty person to clen inside | NA | No | Air flow blocking | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR052%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-06 16:03 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-06 16:04 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-14 15:42 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-05-15 13:48 | 2025-05-10 |  |  |  |  | CRLU6220410 |  |  |  | Carrier | -18c | Dirty | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | 403/402/404 | Not done | On line unit temp. Issue | On checked unit found internal air space bottom air flow blocked due to carbage and icing . Advise to duty person to clean co ntrainer with removed ice & carbage .with hot water. After cleaning container is working and maintaining temp | No | https://drive.google.com/open?id=1Rmnul085BzeXCIecwhVUnbCSJ2kgwm17 | https://drive.google.com/open?id=1iR7aBb1oqYcKXlbAyYm8QhYzFDi8qMfn |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR053/25 | 2025-04-29 13:24 | operation@crystalgroup.in | Crystal | NA | NA | NA | CRSU6017476 | EVP MOTOR NOISY | Kunal | NA | JNPT | Repair | EVP MOTOR NOISY |  |  | 2025-05-05 16:07 | crm@crystalgroup.in | Crystal Yard | CRSU6017476 | 40 FT | NA | REPAIR | NA | NA | EVP MOTOR NOISY | Need to replace Bearing | 6203 tune wise & 6205 tunewise | Yes | Bearing Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR053%2F25 | CARRIER-THINLINE | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | No | EVP MOTOR NOISY | 2025-05-15 12:28 | operation@crystalgroup.in | YES | IN020 | 2025-05-15 | Spares | CRYSTAL YARD | Dighode | CRSU6017476 | DEPOT | FOC | CARRIER-THINLINE | 2025-08-08 14:35 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 14:36 | crm@crystalgroup.in | NO
APR054/25 | 2025-04-29 13:25 | operation@crystalgroup.in | Crystal | NA | NA | NA | GESU9454950 | EVP MOTOR NOISY | Kunal | NA | JNPT | Repair | EVP MOTOR NOISY |  |  | 2025-05-05 16:10 | crm@crystalgroup.in | Crystal Yard | GESU9454950 |  | NA | REPAIR | NA | NA | EVP MOTOR NOISY | Need to replace bearing | 6203 tune wise, 6205 tune wise | Yes | Bearing Issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR054%2F25 | CARRIER-THINLINE | CARRIER-THINLINE | NA | NA | NA | NA | NA | RAMIZ | No | EVP MOTOR NOISY | 2025-05-15 12:30 | operation@crystalgroup.in | YES | IN021 | 2025-05-15 | Spares | CRYSTAL YARD | Dighode | GESU9454950 | DEPOT | FOC | CARRIER-THINLINE | 2025-08-08 14:37 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 14:37 | crm@crystalgroup.in | NO
APR055/25 | 2025-04-29 15:42 | operation@crystalgroup.in | Crystal | NA | NA | NA | GRMU3707470 | COMPRESSOR MAKING NOISE | NA | NA | JNPT | Complete Breakdown |  |  |  | 2025-04-29 16:22 | service@crystalgroup.in | crystal yard | GRMU3707470 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Compressor abnormal noise & less gas suspected & isv & esv valve defective . | have to return mumbai | isv esv gas r134a filter drier breezing set all equipment | Yes | leakage or isv & esv defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAR017%2F25 | Daikin | daikin | na | ok | decose iiid | used | yes | RAMIZ | No | COMPRESSOR MAKING NOISE | 2025-04-30 12:18 | tender@crystalgroup.in | YES | 1930-04-01 | 2025-04-30 | Consumables, Spares | Softbox | Hyderabad | GRMU3707470 | SITE | FOC | DAIKIN
APR056/25 | 2025-04-29 15:56 | tender@crystalgroup.in | Tata Advanced Systems Ltd | Mr. Sachin | 7337832756 | NA | CXRU1037294 |  |  | NA | Bangalore | Preventive Maintenance | [57 empty] | 2025-05-17 00:16 | 2025-05-16 |  |  |  |  | CXRU1037294 |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/20br | 9.9/9.8/9.9 | 417/416/416 | Short | Found unit display with sheetkey damaged & broken | Replaced Display & sheet key.with pm service completed | No | https://drive.google.com/open?id=1DhDeO2cdge_jxKK8AzajG8VCetqzngE3 | https://drive.google.com/open?id=1MC7868OubRbATlIzwE3Q3WcKCKgHq9he |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR057/25 | 2025-04-29 15:58 | operation@crystalgroup.in | Tata Advanced Systems | Mr. Sachin | 7337832756 | NA | HDMU5501938 |  |  | NA | Bangalore | Preventive Maintenance | [57 empty] | 2025-05-11 20:12 | 2025-05-11 |  |  |  |  | HDMU5501938 |  |  |  | Daikin | -23c | Clean | Clean | https://drive.google.com/open?id=1WstXD-hUmLXzwDZP7d-2V26q2UEeyScu | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1E-SbrxhVHjYswU3xeyi8_R2n4f_KYDRO | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/19 br | 9.9/9.8/9.8 | 407/408/407 | Short | Unit working as satisfactory | PM Complited | No | https://drive.google.com/open?id=15ybv1qENgMHD6iVnKfUc2EWascPPsgsx | https://drive.google.com/open?id=1vzsukgZQBrMnR1TnkpngqOM6DLJbbDeh |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR058/25 | 2025-04-29 16:02 | operation@crystalgroup.in | Tata Advanced Systems Ltd | Mr. Sachin | 7337832756 | NA | CZZU6009100 |  |  | NA | Bangalore | Preventive Maintenance | [57 empty] | 2025-05-11 20:16 | 2025-05-11 |  |  |  |  | CZZU6009100 |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 9.8/9.7/9.7 | 406/405/407 | Short | Unit working as satisfactory | PM service complited | No | https://drive.google.com/open?id=1NYKvcVaHABEiDyEcJG_hGGwn-uSAqAqi | https://drive.google.com/open?id=1-C-8OzaDlQ75mJnP8lpZnlnk6QqpxyLO |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
APR059/25 | 2025-04-29 16:04 | operation@crystalgroup.in | Tata Advanced Systems Ltd | Mr. Sachin | 7337832756 | NA | CBHU2811760 |  |  | NA | Bangalore | Preventive Maintenance | [57 empty] | 2025-05-15 10:50 | 2025-05-14 |  |  |  |  | CBHU2811760 |  |  |  | Carrier | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/19br | 12.4/12 5/12.4 | 417/418/417 | Short | Unit front side need to left at least 1/2 fit for proper drain wateras well as air flow | PM done & replaced Defrost sensor & key pad .. with rearrangec& repairing evp Heater wiring | Yes | https://drive.google.com/open?id=1PdCVYan-8qZjDBxdYMeRqlbRcQ2CFdPy | https://drive.google.com/open?id=1ovPDek3mR-8fS65ZH6AuMxLrrfmIWBTO |  | 89 | No | No | Can be done on next PM | N | HTT SENSOR for carrier thin line | technician@crystalgroup.in | REEFER
APR060/25 | 2025-04-29 16:07 | operation@crystalgroup.in | Lupin Limited | Mr. Akash | 9370588166 | NA | CCLU1036859 | FLUCTUATIONS IN TEMEPRATURE | Shahbuddin | NA | Bhiwandi | Running with issues | Temperature Fluctuation |  |  | 2025-05-02 16:33 | technician@crystalgroup.in | Lupin | CCLU1036859 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. & Display faded | Need to replaced display & service | Carrier Display | Yes | Display | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR060%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-05-06 17:24 | crm@crystalgroup.in | YES | 1932-04-01 |  | Spares | LUPIN LTD | Bhiwandi | CCLU1036859 | SITE | CHARGEABLE |  | 2025-05-06 17:35 | crm@crystalgroup.in | YES | 1932-04-01 | YES |  | Stock | 2025-05-10 13:02 | crm@crystalgroup.in | YES | 1932-04-01 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-05-08 13:59 | 2025-05-06 |  |  |  |  | CCLU1036859 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 11.1B | 9.0A 9.5A 9.7A | 391V 389V 390V | Not done | WE HAVE FOUND IN THIS UNIT CONDENSOR COIL HEAVY DIRTY TO WASH | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER ,FILLTER DRIER REPLACE 1NOS AND R-134a REFILL 2KG | No | https://drive.google.com/open?id=1m9gTpnEDPBQWX6c3SNWjJLOfD-lEp-Nc | https://drive.google.com/open?id=1RIuzlTyhv6Rb-urXtlW64hhOFmn7MrhG |  | N/A | No | No | Can be done on next PM | N/A | N/A | technician@crystalgroup.in | REEFER
APR061/25 | 2025-04-29 16:22 | operation@crystalgroup.in | BCC | Omprakash | 8005535259 | NA | CRIU2152251 | ISO TANK WALL LEAKAGE | Jyotirlin | NA | Bikaner, Rajasthan | Wall Leakage | ISO TANK WALL LEAKAGE |  |  | 2025-05-03 16:27 | qualitycontrol@crystalgroup.in | BCC | CRIU2152251 |  | ISO Tank | SERVICE-ON CALL | LEASE | CHARGEABLE | Leakage from foot valve as been told but the customer is not able to provide clear photo /video of the leakage | First need to check properly |  | Not clear at present | Mishandling by the client | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR061%2F25 | NA | ISO TANK | NA | NA | NA | USED | NA | VIRENDRA | Yes | ISO TANK WALL LEAKAGE | 2025-05-15 12:34 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-15 12:34 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 12:34 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-05 17:11 | 2025-06-28 |  |  |  |  | CRIU2152251 | [48 empty] | crm@crystalgroup.in | DRY/Others
APR062/25 | 2025-04-29 16:32 | operation@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | GESU9454776 | Spares |  | NA | Vishakapatnam | Running with issues |  |  |  | 2025-04-29 15:14 | service.support@crystalgroup.in | Lauras Lab Unit 2 | GESU9454776 | 40FT STD RF | Carrier | RUNNING WITH ISSUES | LEASE | FOC | RUNNING WITH ISSUES | PM | EVP MOTOR SINGLE PHASE | Yes | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR022%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | Spares | 2025-05-06 17:26 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:34 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 17:13 | qualitycontrol@crystalgroup.in | YES | NO | COURIER | 51623608326 | BLUE DART |  | https://drive.google.com/open?id=1j7HPxR9WyymUf9X7cNas_NoIr9IE37_j |  | 2025-06-02 22:50 | 2025-05-30 |  |  |  |  | GESU9454776 |  |  |  | Carrier | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7&11.4 b | 407 | 13.2 | Not done | Found Both sides EVP Motors Heavy noise | Replace L/S Evp motor with good one | Yes | https://drive.google.com/open?id=1UUsMjZ1Wg5SCSAptkRMFDu1uxIv1917B | https://drive.google.com/open?id=12VMkI2pUut8AC5MFFt-5YpdXCBLRTxAm |  | NA | Yes | Yes | Urgent | Need to replace R/S EVP Motor | EVP Motor One nos singh please | rrmondal.786@gmail.com | REEFER
APR063/25 | 2025-04-29 16:33 | operation@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | TITU9930223 | REPAIRS & REPLACEMENT, |  | NA | Vishakapatnam | Running with issues |  |  |  | 2025-04-29 15:20 | service.support@crystalgroup.in | Lauras Lab Unit 2 | TITU99302223 | 40FT Spl RF | Carrier | RUNNING WITH ISSUES | LEASE | FOC | RUNNING WITH ISSUES | PM | CURTAIN LIGHT MP4000 DISPLAY | YES | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR023%2F25 | Thermoking MP-4000 | TK-MP4000 | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT, | 2025-05-06 17:26 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:34 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 17:14 | qualitycontrol@crystalgroup.in | YES | NO | COURIER | 51623608326 | BLUE DART |  | https://drive.google.com/open?id=1gp5vbKYAWgvng8hrtmf_g84IIV788HxL |  | 2025-06-05 17:23 | 2025-05-30 |  |  |  |  | TITU9930223 |  |  |  | Thermo king | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5/16.1b | 8.5 | 407 | Not done | Found Condenser coil very dirty & Display defective | Clean condenser coil with fresh water & Replace display with New one Checked all parameters are good. | No | https://drive.google.com/open?id=10iErv-2CAMeIwHr5wAAY9rll57Yzuq_4 | https://drive.google.com/open?id=1uYmf_6CVZJBnGSfUOAfrvxssjbGeP5Mv |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
APR064/25 | 2025-04-29 16:34 | operation@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | CXRU1036334 | REPAIRS & REPLACEMENT |  | NA | Vishakapatnam | Running with issues |  |  |  | 2025-05-03 16:39 | technician@crystalgroup.in | Laurus Unit 2 | CXRU1036334 | 40 | Carrier | SERVICE-AT SITE | LEASE | FOC |  | On way tech | All daikin sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=APR064%2F25 | Daikn | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-05-06 17:27 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-06 17:32 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-14 17:25 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-06-05 17:26 | 2025-05-30 |  |  |  |  | CXRU1036334 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/11.5b | 9.1 | 407 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked all parameters are good. | No | https://drive.google.com/open?id=12cksG4Nbv5WLOdgrw_8fy2A-F9fEEmo8 | https://drive.google.com/open?id=1ymfSspecifNrveBgmHGgMgbF1Pv0TtIS |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
MAY002/25 | 2025-05-02 19:10 | tender@crystalgroup.in | UPS | Nadeem | 9700137866 | CRM | HDMU5220720 | FLUCTUATIONS IN TEMEPRATURE | Kunal | NA | Hyderabad | Running with issues | REQUIRED TEMP +5 TEMPERATURE OBTAINED IS +7 TO +7.5 |  |  | 2025-05-03 16:43 | technician@crystalgroup.in | UPS | HDMU5220720 | 20FT STD RF | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Tech on way | NA | Depend check | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY002%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | USed | NA | RAMIZ | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-05-12 12:27 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-12 12:28 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-12 14:59 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-12 20:57 | 2025-05-11 |  |  |  |  | HDMU 5220720 |  |  |  | Carrier | 3.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1zoHGUX1j_XR0Bo1Da19nAXtMuUvYSfqb | Okay | https://drive.google.com/open?id=15psX9Ce7clGm9Irb0lC7Rx0VsF40E5Sh | Okay |  | Okay | Okay | https://drive.google.com/open?id=1gmRlBX-zDH9IFGd5OWIJcJSl6W0bE-EE | Okay |  | Okay | Okay | Okay | Done | Clean | https://drive.google.com/open?id=1lyFz9E4Ms7HfYFWgOyb6BWX9IzCFW7_Q | 0.7 and 19 | 9.6,9.7,9.8 | 405408406 | Short | PM service | Sencer issue done and clean tha condenser coil .and chek tha unit all ok | No | https://drive.google.com/open?id=1VWM1HozCTEyg-PiJ9_LSwOvS3B8vCMkI | https://drive.google.com/open?id=1MoJRfFCe7otC6VxiGfKciTDxB06YVkeq |  | Na | No | Yes | Urgent | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY001/25 | 2025-05-02 19:12 | tender@crystalgroup.in | Qwik Supply |  | 8926779233 | NA | CICU3876610 | Under observation | Kunal | NA | Coimbatore | Running with issues |  |  |  | 2025-05-10 17:58 | service@crystalgroup.in | Qwik Supply | CICU3876610 | 10FT STD RF | Thermoking | SERVICE-ON CALL | NA | NA | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin |  | No | customer phone is switched off, as per Kunal issue resolved at phone by Shahabuddin | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY001%2F25 | Thermoking | Magnum Plus | E0GM031439 | 0422GM031439 | ABC782900322060170 | Brand New | nill | SHAHBUDDIN | No | Under observation | 2025-05-12 12:38 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-12 12:38 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-12 14:58 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-13 01:15 | 2025-05-05 |  |  |  |  | CICU3876610 |  |  |  | Thermo king | -35c | Clean | Clean | https://drive.google.com/open?id=1T7vhyex2jd6Bpzl-4Sfkj_pgsVcpU4_f | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1f8XIh-8TTMWHkCMmGv9y5q392tcRReFB | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/21br | 9.9/9.8/9.9 | 407/406/406 | Short | Unit working as satisfactory | On call resolved temp. Issue | No | https://drive.google.com/open?id=1ykcLU20wjlIjYmTr8JjXqwSrdCsa8Wt6 | https://drive.google.com/open?id=1vYxgg54FxAUNBpsg20qyWKfgBXlzg1LO |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY003/25 | 2025-05-05 10:36 | service@crystalgroup.in | Lupin Limited | Prasanna Kumar | 9676999956 | manager | TRIU6681882 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | AMRENDRA | prasannakota@lupin.com | Bhiwandi | Complete Breakdown | TEMPERATURE NOT ACHIEVED UPTO SET TEMP. - 8C |  |  | 2025-05-05 14:30 | service@crystalgroup.in | LUPIN LIMITED | TRIU6681882 | 20 ft | carrier thin line | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor tripping issue | Filter Drier replacement, refrigerant top up | Filter Drier 01 nos. Refrigerant | Yes | FILTER DRIER CHOKED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY003%2F25 | 20 ft Reefer | CARRIER-THINLINE | 0 | 0 | Advance | USED | 0 | VIRENDRA | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-06 17:28 | crm@crystalgroup.in | YES | 1933-04-01 |  | Spares | LUPIN LTD | Bhiwandi | TRIU6681882 | SITE | CHARGEABLE |  | 2025-05-06 17:32 | crm@crystalgroup.in | YES | 1933-04-01 | YES |  | Stock | 2025-05-10 13:04 | crm@crystalgroup.in | YES | 1933-04-01 | TECHNICIAN |  |  | VIRENDRA |  |  | 2025-05-08 14:07 | 2025-05-06 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | +5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Need to replace |  | Okay | Okay | Okay | Done | Clean |  | 12.2B | 9.0A 8.7A 8.9A | 388V 386V 387V | Not done | WE HAVE FOUND CONDENSOR COIL HEAVY DIRTY TO WASH EVP HIGH SPEED CONTACTOR BURN | WE HAVE CLEAN CONDENSOR COIL WITH NORMAL WATER EVP HIGH SPEED CONTACTOR BYPASS FILLTER DRIER REPLACE 1NOS R-134a REFILL 2KG | Yes | https://drive.google.com/open?id=19lVT9hNXfBBWxrkmBM8HFsKQdBkBbFdT | https://drive.google.com/open?id=10vzUeBK695ZINuRhP5ItAKSvR-G7LN9g |  | N/A | Yes | No | Can be done on next PM | EVP CONTACTOR 1NOS | CONTACTOR 12A 1NOS | technician@crystalgroup.in | REEFER
MAY004/25 | 2025-05-05 13:39 | service@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | Dharmender Tiwari | 9700033475 | Deputy Manager | SJKU400010 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | SUSHMA | dharmender.tiwari@dsv.com | Hyderabad | Running with issues | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  |  | 2025-05-05 17:40 | service@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | SJKU4000104 | 40FT | NA | SITE INSPECTION | LEASE | CHARGEABLE | Extreme sound coming from, Condenser Fan, variation in temperature | on site inspection |  | on site inspection | Need To Check Physically | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY004%2F25 | 40REEFER | NA | 0 | 0 | 0 | USED | 0 | VIRENDRA | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-12 12:29 | operation@crystalgroup.in | YES | IN014 | 2025-05-12 | Consumables, Spares | DSV Air & Sea Pvt. Ltd. | Hyderabad | SJKU400010 | SITE | FOC | TK-MP4000 | 2025-05-12 16:06 | operation@crystalgroup.in | YES | IN014 | YES | https://drive.google.com/open?id=1sCD1KIZehlhtFiLx7r4bp6MbAgeVI0sN | Vendor | 2025-05-15 17:01 | qualitycontrol@crystalgroup.in | YES | IN014 | COURIER | 1094 | DOLPHINE TRAVELS VASHI |  | https://drive.google.com/open?id=14yyqmQSQwFhGjQwFJ76RLGM-CXqq2q7y |  | 2025-05-17 20:06 | 2025-05-10 |  |  |  |  | SJKU 4000104 |  |  |  | Thermo king | NA | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay | https://drive.google.com/open?id=1CZaj50jrlExFKpISFVvNI2QsB7ZWR9hB | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0 | 0 | 390390389 | Not done | Complen attended | After checking everything it turned out that the compressor is grounded. | Yes | https://drive.google.com/open?id=1Hq0cgf00AixjtjCJef7nGgyh4fBJlti6 | https://drive.google.com/open?id=163XXs6ota8-QdiqxjaaYk0uD9YjOBHya |  | NA | Yes | Yes | Urgent | 1 Compressor cheng | Compressor Gass 404 | sarveshk392@gmail.com | REEFER
MAY005/25 | 2025-05-05 15:16 | crm@crystalgroup.in | Verka Amritsar Dairy | Hazoor Singh | 78887-47805 | Manager | CXRU1186385 | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | Lina | engg.asr@verka.coop | Amritsar | Running with issues | Compressor of the container is creating abnormal noise and the motor of outdoor fan is not working |  |  | 2025-05-05 17:52 | crm@crystalgroup.in | Verka Amritsar Dairy | CXRU1186385 | 40FT STD RF | NA | REPAIR | LEASE | CHARGEABLE | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | Compressor 3 abnormal noise | New Compressor, R134A Gas - 5KG, Drier Filter, Gaskit & Compressor Oil 3Ltr | Yes | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY005%2F25 | Daikin | DAIKIN | M002086 | K31505147912 | DECOS 3F 2557 / 1 | Used | CXRU1186385 | RAMIZ | Yes | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | 2025-05-08 16:44 | operation@crystalgroup.in | YES | IN003 | 2025-05-08 | Spares | Verka Dairy | Amritsar | CXRU1186385 | SITE | FOC | DAIKIN LXE10E | 2025-05-12 16:08 | operation@crystalgroup.in | YES | IN003 | YES |  | Stock | 2025-05-14 12:01 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-14 14:13 | 2025-05-13 |  |  |  |  | CXRU1186385 |  |  |  | Daikin | +4.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-186. D-1872 | R-13.9A. B-13.8A. Y-13.9A | L1-391V. L2-392V. L3-391V | Short | We have attende tha unit found condenser coil durty and supply issue | We have work condenser coil wash with normal water and supply cable reconnection after unit running good condition | No | https://drive.google.com/open?id=1n-SG6eVI4JaYMXbptK1pbcRdqgEv8oeu | https://drive.google.com/open?id=1fKIFvm2I3K_h9n-BT8M0wQiKOGyGbygL |  | TRIP091 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY006/25 | 2025-05-06 17:49 | crm@crystalgroup.in | ITC AQUEA | Shiva | 9849765331 | NA | MYRU4517508 | FLUCTUATIONS IN TEMEPRATURE | Amendra | NA | Bapatla | Running with issues | Temperature not achieving |  |  | 2025-05-08 09:28 | technician@crystalgroup.in | ITC AQUA | MYRU4517508 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Temp. | NA | EIS sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY006%2F25 | Daikin | DAIKIN LXE10E | M002805 | LXE10E136A | NOT AVAILABLE | Used | NA | SHAHBUDDIN | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-05-08 10:02 | operation@crystalgroup.in | YES | IN002 | 2025-05-08 | Spares | ITC | Baptla | MYRU4517508 | SITE | FOC | DAIKIN | 2025-05-12 16:26 | crm@crystalgroup.in | YES | IN002 | YES | https://drive.google.com/open?id=1VfS6lLRG3mPw9jpxOvtWGhv6SRZWsR5F | Vendor | 2025-05-15 17:27 | qualitycontrol@crystalgroup.in | YES | IN002 | HARSHA MARINE SERVICES // 16530089203 | [5 empty] | 2025-05-22 16:40 | 2025-05-22 |  |  |  |  | MYRU4517508 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/18 bar | 9.9/9.8/9.9 | 398/397/398 | Short | Unit alram E 407 | Replaced Evaprator Inlet sensor | No | https://drive.google.com/open?id=171FwDZUFgpyqy7WhuGTazrft6lE8ducV | https://drive.google.com/open?id=1Zm3JfXyudNy5k3c5AIPV9nin_lueOJti |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY007/25 | 2025-05-07 12:20 | operation@crystalgroup.in | CIPLA | Anant Ravut | 7774089236 | Sr. Engineer | CRIU4024033 | 2 Bay Installation | Kunal | anant.ravut@cipla.com | Goa | Installation | 2 BAY INSTALLATION |  |  | 2025-05-07 22:33 | technician@crystalgroup.in | CIPLA | CRIU4024033 | 40FT 2BAY RF | Thermoking | INSTALLATION | SALE | CHARGEABLE | Two way Instalation | Job start | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY007%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | Yes | 2 Bay Installation | 2025-05-12 12:24 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-12 12:26 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-15 16:52 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-05-09 14:37 | 2025-05-08 |  |  |  |  | CRIU4024033 |  |  |  | Thermo king | +5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 9.9/9.8/9.9 | 415/416/416 | Short | Twoway Instalation | Job completed for two way Instalation | No | https://drive.google.com/open?id=1RK4wot3HDSGSrukGqybxNxkfYKLBZtAC | https://drive.google.com/open?id=1o9zHUwIruqmm4AXSbrOvwIcGp0rJRK4L |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY008/25 | 2025-05-07 12:27 | crm@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | CPC Manager | CICU3876586 |  |  | kuldeep18.yadav@qwik.co.in | Hapur | Preventive Maintenance | [57 empty] | 2025-05-11 19:29 | 2025-05-06 |  |  |  |  | CICU3876586 |  |  |  | Thermo king | -35.c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-0.8bar. D-21.6bar | R-8.1. B-8.3. Y-8.2 | L1-399. L2-400. L3-398 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water unit running good condition | No | https://drive.google.com/open?id=1t_zZ5WdoMP_7qSkDj1XfHqEVgUOlYI0M | https://drive.google.com/open?id=14dAOou19fYcmIBQB19xW3IyV0mWZE-G3 |  | Na | No | No | Can be done on next PM | Na | Na | rajreefertech@gmail.com | REEFER
MAY009/25 | 2025-05-07 12:30 | crm@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | CPC Manager | SJKU4000017 |  |  | kuldeep18.yadav@qwik.co.in | Hapur | Preventive Maintenance | [57 empty] | 2025-05-11 19:40 | 2025-05-06 |  |  |  |  | SJKU4000017 |  |  |  | Carrier | +17.2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-4.1bar. D-9.2bar | R-7.2A. B-7.5A. Y-7.3A | L1-399v. L2-398v. L3-400v | Not done | We have attende tha unit found condenser coil durty | We have condenser coil wash with normal water after unit running good condition | No | https://drive.google.com/open?id=1C7ZqeLh7ergXwt0T9RWa4wcjcfrxLmM7 | https://drive.google.com/open?id=12ZA-ZIpi8ldY2r4kiTpgjk5M39ueBH5Z |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY010/25 | 2025-05-07 12:31 | crm@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | CPC Manager | CXRU1043912 |  |  | kuldeep18.yadav@qwik.co.in | Hapur | Preventive Maintenance | [57 empty] | 2025-05-11 20:00 | 2025-05-09 |  |  |  |  | CXRU1043912 |  |  |  | Daikin | -22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S- -8psi. D-1378psi | R-10=8A. B-10.2A. Y-10.8A | L1-402v. L2-401v. L3-403v | Short | We have attende tha unit found condenser coil havy durty and eveporetor coil havy iecing and temperature issue | We have condenser coil wash with normal water and eveporetor coil ice clean,drier filter replace,R134a gas top up 0.5kg after unit running good condition | No | https://drive.google.com/open?id=1D5hUcpD5-atRlRtWP2tcEupPGRsHrFhM | https://drive.google.com/open?id=1SQ1w9iw34K9qpsq335kLYW3CQTM0AggQ |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY011/25 | 2025-05-07 12:33 | crm@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | CPC Manager | CXRU1040322 |  |  | kuldeep18.yadav@qwik.co.in | Hapur | Preventive Maintenance | [57 empty] | 2025-05-11 20:19 | 2025-05-09 |  |  |  |  | CXRU1040322 |  |  |  | Daikin | -22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S- -11.2psi. D-1306psi | R-9.1A. B-9.2A. Y-8.9A | L1-393v. L2-394v. L3-394v | Not done | We have attende tha unit found condenser coil havy durty and eveporetor coil havy iecing and temperature issue | We have condenser coil wash with normal water and eveporetor coil ice clean, drier filter replace, R134a gas top up 0.5kg after unit running good condition temperature in range | No | https://drive.google.com/open?id=1u9IWhMKb5xMn8dpU7WSJ60skT3inTy6S | https://drive.google.com/open?id=14KZZVuZ_aaBMRj5_Z9l5tMZ06TQKil3r |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY012/25 | 2025-05-07 12:37 | operation@crystalgroup.in | CIPLA | Anant Ravut | 7774089236 | Sr. Engineer | CRIU4024049 | 2 Bay Installation | Kunal | anant.ravut@cipla.com | Goa | Installation | 2 Bay Installation |  |  | 2025-05-07 22:27 | technician@crystalgroup.in | CIPLA | CRIU4024049 | 40" | Thermoking | INSTALLATION | SALE | CHARGEABLE | New container for Instalation Two way | Job strat | NA | No | Instalation two way | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY012%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | Yes | 2 Bay Installation | 2025-05-12 12:26 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-12 12:33 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-12 12:31 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-09 15:06 | 2025-05-09 |  |  |  |  | CRIU4024049 |  |  |  | Thermo king | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6//19br | 9.8/9.9/9.8 | 416/426/416 | Short | Two way Instalationcomplit | Job completed for two way Instalation | No | https://drive.google.com/open?id=1FMw5dOHA83CgsJRnTGppQODUu_AfNqrj | https://drive.google.com/open?id=1AZdBL3wVXm8elFWuj3fvn2PhSZ4EP9ze |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY013/25 | 2025-05-08 11:11 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | KKFU6710760 | REPAIRS & REPLACEMENT | Kunal | NA | Vishakapatnam | Running with issues |  |  |  | 2025-05-13 00:35 | technician@crystalgroup.in | Lauras unit III | KKFU6710760 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Cable transducer | Temperley repaired | Discharge transducer jack& two supply sensor carrier | Yes | Cabale damaged small | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY013%2F2025 | Carrier | CARRIER-THINLINE | LSU60353959 | 541321 | 5178 | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-05-14 10:28 | operation@crystalgroup.in | YES | IN016 | 2025-05-13 | Spares | Laurus unit 3 | Vizag | KKFU6710760 | SITE | FOC | CARRIER-THINLINE | 2025-06-02 11:11 | operation@crystalgroup.in | YES | IN016 | YES |  | Stock | 2025-06-04 17:32 | crm@crystalgroup.in | YES | IN016 | COURIER | 17815029702 | BLUEDART |  | https://drive.google.com/open?id=11NOT4aG8wTSIvnUEAL3_8-aszNz4Sj54 |  | 2025-06-05 16:10 | 2025-06-03 |  |  |  |  | KKFU6710760 |  |  |  | Carrier | +21'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3/13.1Bar | 9.5 | 407 | Not done | Found Condenser coil very dirty, AL54 & AL68 active | Replace supply temperature sensors with New both & replace CPT cable with good one. | No | https://drive.google.com/open?id=1nb0nWse9Eus8F1VeqDBE4QrDTMICNkRy | https://drive.google.com/open?id=1OixtnoEihblFwaKWy7WG9oRRK011hSpu |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
MAY014/25 | 2025-05-08 11:18 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | DFOU6120384 | REPAIRS & REPLACEMENT | Kunal | NA | Vishakapatnam | Running with issues |  |  |  | 2025-05-13 00:40 | technician@crystalgroup.in | Lauras unit III | DFOU6120384 | 40" | Daikin | SERVICE-AT SITE | LEASE | FOC | AL E407 | Temperley unit run | EIS SENSOR & PT CT BOARD | Yes | EIS SENSOR FAILURE& PTCT BOARD | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY014%2F2025 | Daikin | DAIKIN LXE10E | M004338 | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-05-14 10:32 | crm@crystalgroup.in | YES | IN017 | 2025-05-13 | Spares | Luras Unit 3 | Vishakapatanam | DFOU6120384 | SITE | FOC | DAIKIN | 2025-05-22 15:03 | operation@crystalgroup.in | YES | IN017 | YES | https://drive.google.com/open?id=1HVWzpOrGnIhnXMAn7aRIxTrDGqqmE-M6 | Vendor | 2025-06-02 14:18 | qualitycontrol@crystalgroup.in | YES | IN017 | COURIER | 17815029702 | Blue dart |  | https://drive.google.com/open?id=1FYp6ESlSmWND7AJAnW8ddrPizAmIknKE |  | 2025-06-03 00:17 | 2025-05-31 |  |  |  |  | DFOU6120384 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/11.3b | 9.1 | 405 | Not done | EIS defective & PTCT suspected & condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. Note- EIS sensor & PTCT need to fix | No | https://drive.google.com/open?id=1dveKmpbNPM1ihnEV-ULNKG8ugOVi9vqq | https://drive.google.com/open?id=1fWGjQk3i3Msxw3iiwgziqKzPXP-ZEC5- |  | Na | Yes | Yes | Urgent | - EIS sensor & PTCT need to fix | EIS sensor & PTCT. | rrmondal.786@gmail.com | REEFER
MAY015/25 | 2025-05-08 11:21 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | TCLU1912290 | REPAIRS & REPLACEMENT |  | NA | Vishakapatnam | Running with issues |  |  |  | 2025-05-13 00:44 | technician@crystalgroup.in | Lauras unit III | PCIU1912290 | 20" | Daikin | SERVICE-AT SITE | LEASE | FOC | E407 | Temperley unit run by pass | EIS SENSOR | Yes | EIS SENSOR FAILURE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY015%2F2025 | Daikin | CARRIER-ELITLINE | M004715 | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-05-14 10:32 | operation@crystalgroup.in | YES | IN018 | 2025-05-13 | Spares | Laurus Unit 3 | Vizag | PCLU1912290 | SITE | FOC | DAIKIN | 2025-05-22 15:05 | operation@crystalgroup.in | YES | IN018 | YES | https://drive.google.com/open?id=1OX8mzCMYXQp_E03r-qW9rK24NXZW4jwX | Vendor | 2025-06-02 14:19 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-06-02 23:54 | 2025-05-31 |  |  |  |  | TCLU1912290 |  |  |  | Daikin | -20'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7&14.1b | 10.2 | 406 | Not done | Found Condenser coil dirty & EIS sensor failed & Evaporator coil ice foundation. | Replaced EIS sensor & remove all ice from evaporator coil & Clean condenser coil with fresh water | No | https://drive.google.com/open?id=122r5rz09NnV6WHHHbqE0MNseMzFYqeEB | https://drive.google.com/open?id=1F9qSBn2InSQrpzCu6aN80xFl57YL6y5F |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
MAY016/25 | 2025-05-08 11:27 | crm@crystalgroup.in | Crystal Vizag Depot | PRAVALICK | 9133228334 | NA | MYRU4509035 | REPAIRS & REPLACEMENT |  | NA | Vishakapatnam | Running with issues |  |  |  | 2025-05-12 15:57 | service@crystalgroup.in | Crystal Vizag Depot | MYRU4509035 | 40FT STD RF | Daikin | SERVICE-ON CALL | NA | NA | Power cable not available, display not working | Need to replace Diakin Dispaly, Machine has moved to Customer | Diakin Dispaly | Yes | Power cable not available, display not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY016%2F25 | RFH40R | DAIKIN | 802602 | LXE10E136A | LXE10E136A | USED | 0 | SHAHBUDDIN | No | REPAIRS & REPLACEMENT | 2025-05-15 12:46 | operation@crystalgroup.in | YES | IN022 | 2025-05-15 | Spares | Crystal Vizag Depot | To be checked | MYRU4509035 | SITE | FOC | DAIKIN | 2025-06-07 15:13 | operation@crystalgroup.in | NO |  |  |  |  | 2025-06-10 11:35 | operation@crystalgroup.in | NO | [7 empty] | 2025-06-10 11:47 | 2025-06-10 |  |  |  |  | MYRU4509035 |  |  |  | Daikin | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0/210 bar | 9.9 / 9.8 /9.9 | 412 / 413 /412 | Full | Container moved to JNPT depot | NA | No | https://drive.google.com/open?id=17q5Ldmw1ik1T9xT4iyZGQ6ugRowCMGOg | https://drive.google.com/open?id=1CqprekXSFueJHgyE6n-LLFOZfALUH3KV |  | NA | No | Yes | Can be done on next PM | NA | na | operation@crystalgroup.in | REEFER
MAY017/25 | 2025-05-08 11:31 | crm@crystalgroup.in | Lupin Limited | Prasanna Kumar | 9676999956 | Manager | TRIU6681882 | REPAIRS & REPLACEMENT |  | NA | Bhiwandi | Running with issues |  |  |  | 2025-05-10 18:07 | service@crystalgroup.in | LUPIN LIMITED | TRIU6681882 | 20FT STD RF | Carrier - Thinline | SERVICE-ON CALL | NA | NA | Need Temperature alarm system quotation | Need share quotation |  | No | Need Temperature alarm system quotation | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY017%2F25 | Carrier - Thinline | CARRIER-THINLINE | RFG20R | nill | imart | Used | na | VIRENDRA | No | REPAIRS & REPLACEMENT | 2025-05-22 15:09 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-22 15:10 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-22 15:13 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-22 17:07 | 2025-05-06 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/19br | 12.2/12.3/12.3 | 402/403/402v | Short | Unit temp. Issue with found low Gas | Top off unit with 1kg R134a Gas | No | https://drive.google.com/open?id=1_k5BIfuKuyp-BhFRyDPsShQ1IpEr_uGp | https://drive.google.com/open?id=1Q7i_iH-7uuGOITwrvk0vFp00FHVUVLKM |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY018/25 | 2025-05-08 16:32 | crm@crystalgroup.in | DR REDDY CTO 06 | Sai Babu | +91 96188 49181 | NA | CXRU1033616 | REPAIRS & REPLACEMENT | Tushar | NA | Vishakapatnam | Complete Breakdown | Sensors need to replace |  |  | 2025-05-12 12:47 | service@crystalgroup.in | Dr Reddy CTO 6 | CXRU1033616 | 40FT STD RF | DAikin | SERVICE-AT SITE | NA | NA | No cooling | Replacement of Supply and return sensor. 06 nos. | Diakin Thermistor- 2509541 Supply and return sensor. 06 nos. | Yes | no cooling | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY018%2F25 | LXE10E147F2 | DAIKIN | M001192 | K31508150460 | DECOS 3F 2557 / 1 | used | 0 | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-05-12 13:05 | operation@crystalgroup.in | YES | IN015 | 2025-05-12 | Spares | DR REDDY CTO 6 | Srikakulam | CXRU1033616 | SITE | FOC | DAIKIN LXE10E | 2025-05-12 13:06 | operation@crystalgroup.in | YES | IN015 | YES | https://drive.google.com/open?id=1WHUt4VFWH34sL-b3cIZ8A08kTGg4_QuY | Vendor | 2025-05-15 17:29 | qualitycontrol@crystalgroup.in | YES | IN015 | COURIER | 25017200066341 | SHREE MARUTI |  |  |  | 2025-05-17 16:57 | 2025-05-15 |  |  |  |  | CXRU 1033616 |  |  |  | Daikin | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1fDXBj9-sdc7g9TEtkvKCBZUVMUfeC1S3 | Okay | https://drive.google.com/open?id=1BgGP43T4J7UQ89dV3Okg1IWOoWF0h1kc | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | https://drive.google.com/open?id=1kvqSHUPqbbUXdsggF4IPGBf00dUqsBQe | 0.8,20 | 10,10.2,10.1 | 389386385 | Short | Service coll and complaint | Sencer issu Cheng supply sencer, return sencer, uopareter sencer and clean condenser coil and chek voltage, moter amp and chek all unit .control. And sort pti pass. | No | https://drive.google.com/open?id=1ymGw_9EysVB9dSbysPPdsa6rNooA6bty | https://drive.google.com/open?id=10u4KoFIsakxTd94M0fcD025KVv3aaKOe |  | Na | No | Yes | Can be done on next PM | 0 | Replace sencers | sarveshk392@gmail.com | REEFER
MAY019/25 | 2025-05-08 17:07 | crm@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | Meghana Joshi | 74996 11761 | CEO | GRMU3707485 | Installation of Container | Kunal | NA | Dahanu | Installation | [57 empty] | 2025-05-10 20:43 | 2025-04-28 |  |  |  |  | GRMU3707485 |  |  |  | Daikin | -28 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1bVJLkLn4Gh8fWVNddTAx0Fhssai14eMD | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3 and 210 | 9.5,9.6,9.5 | 394395395 | Short | Installation unit 3 way unit | Installation complete and testing don | No | https://drive.google.com/open?id=1tVvpj_pSPEYdOTQ0uGm2gnyFuuyaipJG | https://drive.google.com/open?id=1-I_9PIX9pWtZLrLzVEqhiP9SADhAdvAo |  | NO | No | Yes | Urgent | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY020/25 | 2025-05-08 17:09 | crm@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | Meghana Joshi |  | 74996 11761 | SJKU4000038 | Installation of Container |  | NA | Dahanu | Installation | [57 empty] | 2025-05-10 20:52 | 2025-04-28 |  |  |  |  | SJKU4000038 |  |  |  | Carrier | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=11J1_-Dqtvp2HafhvsPw4Mf_3wKZFATCh | Okay | https://drive.google.com/open?id=1V-BCs2AGCzJkOhsQApKyNTaKM10-8Y-m | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4, 208 | 9.5,9.5,9.6 | 396397395 | Short | Installation unit | Installation complete and unit ok | No | https://drive.google.com/open?id=16Uuqu35oQ7Sm_MSCOxwbr5UNO9A9GRxU | https://drive.google.com/open?id=1lHwZrO-X-Ixw4LRm3kP_lEV74rUxzvA0 |  | NA | No | Yes | Urgent | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY021/25 | 2025-05-08 17:15 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Ganesh | +91 70660 00195 | NA | CICU2094005 |  |  | NA | Pune | Preventive Maintenance | [57 empty] | 2025-05-10 19:55 | 2025-04-30 |  |  |  |  | CICU2094005 |  |  |  | Thermo king | 3.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 and 19 | 9.7,9.8,9.7 | 415416415 | Short | PM service | Sort PTI Pass no any alarm | No | https://drive.google.com/open?id=1w1PmtRIH8GLPo-xwBvxQcOnCfGdqeKh9 | https://drive.google.com/open?id=1swyaCFnuQp0KHs4oBCqqCvXMtXt-i6Rv |  | NA | No | Yes | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY022/25 | 2025-05-08 17:25 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Ganesh | +91 70660 00195 | NA | CICU2094010 |  |  | NA | Pune | Preventive Maintenance | [57 empty] | 2025-05-10 21:33 | 2025-04-30 |  |  |  |  | CICU2094010 |  |  |  | Thermo king | 3.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1lisNleYkWwwUQxfh0vALGCux02Hepk6d | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6. , 20 | 9.6,9.8,9.7 | 415417416 | Short | PM service | PM service complete checked unit operation volt and motor amp and gass level, check sencer reading and pressure unit sort PTI pass. | No | https://drive.google.com/open?id=11CSINIDaQYhCCZCnamO-z4FPIVA4JiXX | https://drive.google.com/open?id=1l2QdH7Mq32gO3M0zeyoJ75eXb4Xxt_j8 |  | NA | No | No | Urgent | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY023/25 | 2025-05-08 17:29 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Ganesh | +91 70660 00195 | NA | CICU2093992 |  |  | NA | Pune | Preventive Maintenance | [57 empty] | 2025-05-10 21:43 | 2025-04-30 |  |  |  |  | CICU 2093992 |  |  |  | Thermo king | 3.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 and 20 | 9.7,9.8,9.7 | 415415416 | Short | PM service | PM service complete checked unit operation volt and motor amp and gass level, check sencer reading and pressure unit sort PTI pass. | No | https://drive.google.com/open?id=1qHDHDO3_dAUHdApv_3jrvQpohfYAF8ON | https://drive.google.com/open?id=1ycia_dKatMh-AT0PIR3D77XaJO5ubTgp |  | NA | No | Yes | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY024/25 | 2025-05-08 17:31 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Ganesh | +91 70660 00195 | NA | CICU2094026 |  |  | NA | Pune | Preventive Maintenance | [57 empty] | 2025-05-10 21:51 | 2025-04-30 |  |  |  |  | CICU 2094026 |  |  |  | Thermo king | 3.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6 and 19 | 9.8,10,9.7 | 415415416 | Short | PM service | PM service complete checked unit operation volt and motor amp and gass level, check sencer reading and pressure unit sort PTI pass. | No | https://drive.google.com/open?id=1tSg0AX6Ym-p4JxPW2XQCRfFTJn87pAbX | https://drive.google.com/open?id=1bZz--3Ai-12jTvmDzzbdy80cyLlsSjCH |  | Na | No | No | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY025/25 | 2025-05-08 17:33 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Ganesh | +91 70660 00195 | NA | CICU1938565 |  |  | NA | Pune | Preventive Maintenance | [57 empty] | 2025-05-10 22:02 | 2025-04-30 |  |  |  |  | CICU 1938565 |  |  |  | Thermo king | 4.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7 and 20 | 12.6,12.9,13 | 416416417 | Short | PM service ( super frigar ) | PM service complete checked unit operation volt and motor amp and gass level, check sencer reading and pressure unit sort PTI pass. | No | https://drive.google.com/open?id=179X6L8uRM6vNZp2FCIZVAcBVZ56dZYIv | https://drive.google.com/open?id=19MkX0gtaRQwWsgkh4ij3ig6VO-0m89za |  | NA | No | No | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY026/25 | 2025-05-09 11:02 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | NA | HDMU5542114 | DISPLAY NOT VISIBLE | Lina | NA | Bidar | Running with issues | Display not visible properly |  |  | 2025-05-10 16:40 | service@crystalgroup.in | Sai Life | HDMU5542114 | 40FT STD RF | Carrier | SERVICE-AT SITE | SALE | AMC | Controller Display is not readable in sun light | Discussed with customer, and agreed for PM and check the controller display | CARRIER THINELINE CONTROLLER | Yes | Controller Display is not readable in sun light | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY026%2F25 | RFH40R | CARRIER-THINLINE | HDMU5542114 | RFH40R | 0 | used | 0 | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE | 2025-05-10 17:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-10 17:43 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-12 09:27 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-17 11:56 | 2025-05-10 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | -18 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call we have done | On call we have done | On call we have done | Full | On call we have done | Discussion on Phone Call & resolve the issue. In the next PM technician would carry a digital display controller. Check & replace. | Yes | https://drive.google.com/open?id=1zge9AySxhZkFPkZ9Vi7LmTjN7M-jBdvu | https://drive.google.com/open?id=1tRoz83wuX_DyORlV_jXMD6-iP3LLTUFy |  | ON CALL | No | No | Can be done on next PM | NO | Controller Display | crm@crystalgroup.in | REEFER
MAY027/25 | 2025-05-10 17:34 | crm@crystalgroup.in | MEDISPARAY LOBORATORIES PVT.LTD. | Uday | 98819 97107 | NA | TRIU6681434 |  |  | NA | Goa | Preventive Maintenance |  |  |  | 2025-05-10 17:45 | technician@crystalgroup.in | MEDISPARAY LOBORATORIES PVT.LTD. | TRIU6681434 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service Due | PM service | NA | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY027%2F25 | Carrier - Thinline | CARRIER-THINLINE | NSG60383847 | 541320 | 5176 | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-05-11 20:23 | 2025-05-10 |  |  |  |  | TRIU6681434 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/21br | 12.2/12.3/12.2 | 415/414/415 | Short | Unit working as satisfactory | PM service complited | No | https://drive.google.com/open?id=1dSGGvG4LPSRzYxbXfulhk8wtyy5nnaM9 | https://drive.google.com/open?id=1fMrr6EHfHI9hVCrpBtnTVTC5lfyacsLl |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY028/25 | 2025-05-12 18:02 | crm@crystalgroup.in | Hetero Bio Pharma Unit 1 | Mr. Prasanna | 9989579331 | Manager | CICU3876539 | DISPLAY NOT VISIBLE | Pushpa Mam | Prasanna.B@hetero.com | Jadcherala | Running with issues | Display Failed |  |  | 2025-05-17 18:59 | service@crystalgroup.in | Hetero Bio Pharma Unit 1 | CICU3876539 | 10FT STD RF | Thermoking | SERVICE-AT SITE | NA | CHARGEABLE | Display found Defective | Need Replace Display | Thermoking Magnum Plus Display | Yes | Display defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY028%2F25 | Magnum Plus | TK-MP4000 | E0GM030961 | 0222GM030291 | ABC782800321480005 | Brand New | 0 | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE | 2025-05-26 12:29 | operation@crystalgroup.in | NO | [9 empty] | 2025-05-26 12:30 | operation@crystalgroup.in | NO |  |  |  |  | 2025-05-26 12:32 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-08 12:24 | 2025-06-25 |  |  |  |  | CICU3876539 |  |  |  | Thermo king | -37c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6/20 | 9.9/9.9/9.9 | 412/413/412 | Short | In warrenty replaced digital display TK MP 4000. | Unit found in warrenty with digital display | No | https://drive.google.com/open?id=1eiPV4FjVzkvu1jV8mjuK2qqeJ6uNNvjL | https://drive.google.com/open?id=1nfCjvrgMvv0F9GbWm6SIuMzhkOCB3Nh3 |  | 101 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAY029/25 | 2025-05-12 18:26 | crm@crystalgroup.in | Reliance Retail Ltd | Surjit Singh | 9779944073 | NA | CICU3876631 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | surjit3.singh@ril.com | Shambhuklan | Running with issues | Temperature Issue |  |  | 2025-05-14 18:01 | technician@crystalgroup.in | Ril - Retail punjab | CICU3876631 | 10" | Thermoking | SERVICE-AT SITE | LEASE | FOC | Unit high pressure tripping off compressor | Advise to clean coil with water by clints | NA | No | Condenser coil dirty with mud & dust | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY029%2F2025 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | RAJ KUMAR | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-15 11:32 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-15 11:33 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 11:37 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-26 12:26 | 2025-05-19 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S--- D-19.8bar | R-11.3. B-11.7. Y-11.1 | L1-375. L2-378. L3-380 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1HyCP43OxcBc37g0YfBvAE1eBFa18oqVi | https://drive.google.com/open?id=1xHd5TdpIj5hgMsO_mWPvX0s1hDKvzOR- |  | Trip091 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY030/25 | 2025-05-13 12:02 | crm@crystalgroup.in | Lupin Limited | Akash Gorle | 9370588166 | WAREHOUSE MANAGER | CCLU1036859 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | NA | Bhiwandi | Running with issues |  |  |  | 2025-05-14 17:55 | technician@crystalgroup.in | Lupin Bhivandi THANE | CCLU1036859 | 20" | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. & DISPLAY faded | Tech.chk | Carrier Display / Gas | Yes | Display faded & low Gas | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY030%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-15 14:27 | operation@crystalgroup.in | YES | IN023 | 2025-05-15 | Consumables, Spares | LUPIN LTD | Bhiwandi | CCLU1036859 | SITE | PAID | CARRIER-THINLINE | 2025-06-04 17:15 | crm@crystalgroup.in | NO |  |  |  |  | 2025-06-04 17:15 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-26 11:26 | 2025-05-22 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | -5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/19br | 12.2/12.3/12.3 | 402/403/402v | Short | Unit temp. Issue with found low Gas | Top off unit with 1kg R134a Gas | No | https://drive.google.com/open?id=1wdgJ-tU-r_KLjclyNzKVOfdKErsOLpUl | https://drive.google.com/open?id=1EdoUDfFwpl0YxbhsFzY59ItZWUKHuxUg |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAY031/25 | 2025-05-13 12:50 | crm@crystalgroup.in | BIOCON | Manjunath Kelur | +91 90081 76576 | NA | TRIU6681542 | MOTOR MAKING NOISE | Kunal | NA | Bangalore | Running with issues |  |  |  | 2025-05-13 23:23 | technician@crystalgroup.in | Biocon | TRIU6681542 | 20FT STD RF With Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | PM service & Evaprator .motor left not working | PM plan | Evaprator motor single phase for Thin Line | Yes | Evaprator motor & p. M. Service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY031%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | MOTOR MAKING NOISE | 2025-05-15 14:39 | operation@crystalgroup.in | YES | IN024 | 2025-05-15 | Spares | Biocon | Bangalore | TRIU6681542 | SITE | PAID | CARRIER-THINLINE | [17 empty] | 2025-05-15 11:06 | 2025-05-12 |  |  |  |  | TRIU6681542 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/20br | 12.4/12.3/12.5 | 417/416/417 | Short | PM service & Evaprator motor issue | PM Complited & bypass one Evaprator motor run unit and maintaining temp. | Yes | https://drive.google.com/open?id=1LU1zKgzJtP1SkzdS3WcM6mhjg51T9ctV | https://drive.google.com/open?id=1jTgeb6m8BvWTzz0YHPvWrYznud7Mf_mS |  | 89 | No | No | Can be done on next PM | NA | Evaprator motor with complit set carrier thin line / single phase | technician@crystalgroup.in | REEFER
MAY032/25 | 2025-05-13 12:52 | crm@crystalgroup.in | BIOCON | Manjunath Kelur | +91 90081 76576 | NA | CCLU1035976 |  |  | NA | Bangalore | Preventive Maintenance |  |  |  | 2025-05-13 23:21 | technician@crystalgroup.in | BIOCON | CCLU1035976 | 20FT STD RF- Dual Machine - Carrier Thinline with Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | PM SERVICE | PM service plan | NA | No | Pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY032%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | used | NA | SHAHBUDDIN | Yes |  | 2025-05-15 10:57 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-15 10:57 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 10:58 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-15 10:59 | 2025-05-12 |  |  |  |  | CCLU1035976 |  |  |  | Carrier | +5c & + 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/.5/19/20br | 12 2/12.4/12.6/12 4/12.3/22.4 | 417/416/417 | Short | Two way unit for pm | PM Complited & unit working as satisfactory | No | https://drive.google.com/open?id=1FKcejS47La_J2yd33H1WfrmvugezqpG2 | https://drive.google.com/open?id=1fqW5iItZ6Tci1pVIWx2wjoCOZBbMttbE |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY033/25 | 2025-05-13 15:53 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | NYKU793145 | ALARM CODE VISIBLE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | Nitin55.Sharma@ril.com | Sirhind, Punjab | Complete Breakdown |  |  |  | 2025-05-14 17:50 | technician@crystalgroup.in | Quick supply srihind punjab | NYKU793145 | 40" | Carrier | SERVICE-AT SITE | LEASE | FOC | Discharge pipe Gas leakage | Tech. On location | Brazing Rod/ R234a Gas / brazing set / vacum pump etc. | Yes | Gas leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY033%2F2025 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | ALARM CODE VISIBLE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-15 15:40 | operation@crystalgroup.in | YES | IN025 | 2025-05-15 | Consumables, Spares | Qwik Supply | Srihind, Punjab | NYKU793145 | SITE | FOC | CARRIER-THINLINE | 2025-06-04 17:23 | crm@crystalgroup.in | NO |  |  |  |  | 2025-06-04 17:24 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-21 13:07 | 2025-05-17 |  |  |  |  | MYRU7931452 |  |  |  | Carrier | -19'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S--- D-17.9 | R-16.1. B-163. Y-16.2 | L1-403. L3-405. L3-404 | Not done | We have attende tha unit found condenser coil havy durty and al 54 - supply sensor failure, High pressure line leakeg | We have brazing work 1 nose ,R134a gas 4.5kg vaccum test, N2 test condenser coil wash with normal water after unit running good condition temperature in range | Yes | https://drive.google.com/open?id=1jucFWyzNywtOv3xwNuenOcYGAQDPzRl3 | https://drive.google.com/open?id=1cmci9zVtnKr0Y2QRT9mtAopy-IO47zmp |  | Trip091 | Yes | No | Can be done on next PM | Sensor replace panding | Supply air sensor 2 nose | rajreefertech@gmail.com | REEFER
MAY034/25 | 2025-05-13 16:44 | crm@crystalgroup.in | Laurus Unit 3 | Ramakrishna CHVVS | 1.0013 | Sr. Manager - Engineering | BMOU9784137 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | ramakrishna.chvvs@lauruslabs.com | Vishakapatnam | Running with issues | This container is to maintain 20 c to 80 c, but daily we are facing temperature issue |  |  | 2025-05-14 17:44 | technician@crystalgroup.in | Lauras unit III | BMOU9784137 | 40" | DAIKIN | SERVICE-AT SITE | LEASE | FOC | EIS /"STS / SHEET KEY REQUIRED | Spare on the way | DAIKIN - TEMP SENSIR-2 / EIS SENSOR- 1& SHEET KEY | Yes | Sensor's abnormal temp. Readings | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY034%2F2025 | Daikin | DAIKIN LXE10E | Mooo881 | NA | NA | Used | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-16 11:06 | crm@crystalgroup.in | YES | IN039 | 2025-05-16 | Spares | WAREHOUSE | LAURUS UNIT 3 | BMOU9784137 | SITE | FOC | DAIKIN LXE10E | 2025-05-21 15:40 | operation@crystalgroup.in | YES | IN029 | YES |  | Stock | 2025-06-04 17:30 | crm@crystalgroup.in | YES | IN029 | COURIER | 17779420831 | Bluedart |  | https://drive.google.com/open?id=1ADph42f0YtHF3FOVGqxHjfRLtemdRtUz |  | 2025-07-25 17:43 | 2025-05-21 |  |  |  |  | BMOU9784137 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | NA | NA | No | https://drive.google.com/open?id=1a3RcA2kaK9skThSG7MCrGijXdL7GwlYe | https://drive.google.com/open?id=15ivfnQ6sygQsK2avrtje9iO18ZLyASv5 |  | NA | No | No | Can be done on next PM | CONTAINER TO BE OFFLEASE- CLOSED AS PER DISCUSSION WITH PUSHPA MAM | NA | crm@crystalgroup.in | REEFER
MAY035/25 | 2025-05-14 14:14 | crm@crystalgroup.in | Qwik Supply | Mohit Rai | 9023419864 | NA | CICU2779935 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | Tejinder5.Singh@ril.com | Ahmedabad | Running with issues | PCM freezing issue |  |  | 2025-05-14 17:24 | technician@crystalgroup.in | Qwik Supply | CICU2779935 | 10 ft reefer | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Advise to clean clints | NA | No | Cond. Coil dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY035%2F25 | Thermoking | TK-MP4000 | E0GM030274 | ABC782800322010476 | NA | BrandNew | NA | SHAHBUDDIN | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-15 10:48 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-15 10:48 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 10:48 | crm@crystalgroup.in | NO | [7 empty] | 2025-06-26 16:07 | 2025-06-20 |  |  |  |  | CICU2779935 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 16.7B | NA | 410/419 | Not done | Check & found that the unit is working fine without alarm | unit attend & found fuctioning fine | No | https://drive.google.com/open?id=1sdydiOMs2G9zJmwXn1XARxKsxtHvjxxm | https://drive.google.com/open?id=1u8uDqyo5AvEkPTLh5xs5LHZXVl632iTr |  | NA | No | No | Can be done on next PM | na | na | crm@crystalgroup.in | REEFER
MAY036/25 | 2025-05-14 14:17 | crm@crystalgroup.in | Qwik Supply | Mohit Rai | 9023419864 | NA | CICU2779909 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | mohit2.rai@qwik.co.in | Ahmedabad | Running with issues | PCM freezing issue |  |  | 2025-05-14 17:28 | technician@crystalgroup.in | Qwik Supply | CICU2779909 | 10 ft reefer | Thermoking | SERVICE-AT SITE | LEASE | FOC | Temp. | Advise to clean by clints | NA | No | Condenser coil dirty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY036%2F25 | Thermoking | TK-MP4000 | E0GM030263 | ABC782800322010201 | NA | BrandNew | NA | SHAHBUDDIN | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-15 10:45 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-15 10:46 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-15 10:47 | crm@crystalgroup.in | NO | [7 empty] | 2025-06-26 16:00 | 2025-06-20 |  |  |  |  | CICU2779909 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 16.5 | NA | NA | Not done | Unit has gas less. | R404a Gas 1kg after attending the unit started working fine without ay alarm. | No | https://drive.google.com/open?id=11i5VPHRslthACuMg45sBNp3fW3DF4rYF | https://drive.google.com/open?id=1G-EzFTOpjbEEqHEmRa5frlZhBkdamPbv |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAY037/25 | 2025-05-14 14:30 | crm@crystalgroup.in | Qwik Supply | Lalit Saini | 9928034131 | Manager | TRIU6680335 | MOTOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | lalit.saini@qwik.co.in | Jaipur | Running with issues | one unit is functioning properly while the other is unable to maintain the desired temperature and is making a lot of noise. The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze. |  |  | 2025-05-14 17:33 | technician@crystalgroup.in | Qwik Supply | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-AT SITE | LEASE | FOC | Motor Noisy | Plan for vandor | NA | Waiting for vandor respond | Motor Noisy Bearing | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY037%2F25 | Daikin | DAIKIN LXE10E | NA | NANA | NA | Used | NA | SHAHBUDDIN | Yes | MOTOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-26 15:21 | crm@crystalgroup.in | YES | IN036 | 2025-05-26 | FOC | Qwik Supply | Jaipur | TRIU6680335 | SITE | FOC | DAIKIN | 2025-05-28 12:28 | crm@crystalgroup.in | YES | IN036 | YES |  | Stock | 2025-05-28 12:30 | crm@crystalgroup.in | YES | IN036 | COURIER | 51565758462 | Bluedart |  | https://drive.google.com/open?id=18ssth0_Y4-WNzWCvzz2ng-2PHj1I3GGA |  | 2025-07-10 18:45 | 2025-07-27 |  |  |  |  | TRIU6680335 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | COMPRESSOR REPLACED | COMPRESSOR REPLACED | No | https://drive.google.com/open?id=1JDKmzPGuNPVmZG2oMUGsghKwjv01LY09 | https://drive.google.com/open?id=1lXAsrMrnXzIO15klhMlVC6nkQiE_0HEr |  | TRIP105 | No | No | Can be done on next PM | NA | NA | operation@crystalgroup.in | REEFER
MAY038/25 | 2025-05-15 14:07 | crm@crystalgroup.in | BIOCON UNIT II | D. Nagaraja Reddy | 9959335767 | Sr. Manager | BMOU9748382 | Installatoion Work | Lina | dnagaraja.reddy@biocon.com | Bangalore | Installation | [57 empty] | 2025-05-15 16:33 | 2025-05-13 |  |  |  |  | BMOU9748382 |  |  |  | Daikin | +15c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4/19br | 9.9/9.8/9.9 | 409/410/410 | Short | Unit for Instalation & PM | Instalation complited with pm and run test done | No | https://drive.google.com/open?id=1rPyMYxJnHBA-u4jeeDtSeQ3xe2rptqM5 | https://drive.google.com/open?id=1qMc8xJ7fNpH7SPxXnkWvRYDCT35N1sqZ |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY039/25 | 2025-05-15 14:11 | crm@crystalgroup.in | BIOCON UNIT II | D. Nagaraja Reddy | 9959335767 | Sr. Manager | BMOU9759767 | Installatation Work | Lina | dnagaraja.reddy@biocon.com | Bangalore | Installation | [57 empty] | 2025-05-15 16:39 | 2025-05-13 |  |  |  |  | BMOU9759767 |  |  |  | Daikin | +15c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .3/20br | 9.9/9.9/9.8 | 409/408/409 | Short | Unit for Instalation & pm | Instalation completed with pm run test done | No | https://drive.google.com/open?id=1B7YjsQwlSjMFsLQIMQ2-ginatRlJIe3c | https://drive.google.com/open?id=1oBPE1YEeWQHC4b6eGKV2_uxtXLiDxcVs |  | 89 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY040/25 | 2025-05-17 16:12 | crm@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | Meghana Joshi | 74996 11761 | CEO | SJKU4000038 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Pushpa Mam | NA | Dahanu | Running with issues | 40ft container set temperature -18 achieve -4 only |  |  | 2025-05-19 19:51 | technician@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | SJKU4000038 | 40FT HC RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Temp. Not received to set | Spare | Carrier prime line scroll compressor/ Gadket/ filter Drier/ Gas 5kg/ vacum pump/N2 | Yes | Compressor leak back | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY040%2F25 | Carrier-Primeline | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-05-20 16:31 | operation@crystalgroup.in | YES | IN032 | 2025-05-20 | Consumables, Spares | TAKSHAVI PRIVATE LIMITED | Dahanu | SJKU4000038 | SITE | PAID | CARRIER-PRIMLINE | 2025-05-22 14:53 | operation@crystalgroup.in | YES | IN032 | YES | https://drive.google.com/open?id=1UyiaxDbX2eWUNem_UeTpv90tMeURS924 | Vendor | 2025-05-23 18:14 | qualitycontrol@crystalgroup.in | YES | IN032 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-06-14 21:14 | 2025-05-25 |  |  |  |  | SJKU4000038 |  |  |  | Carrier | -23c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/220 psig | 10.1/10.2/10.2 | 405/406/405 | Full | Unit found not suitable for pulp cargo | Replaced Evaprator sensor& compressor and Gas and found unit not suitable for pulp cargo to advise to replaced container from normal to blast unit two way. | No | https://drive.google.com/open?id=1JG7nZwX9CQ8KFN2qaMe3iYd9z-EbcL2G | https://drive.google.com/open?id=1L2458Yf6XGR_zmGzlMRUj5hMw148yMPo |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY041/25 | 2025-05-17 16:18 | crm@crystalgroup.in | DR REDDY CTO 06 | Sai Babu | +91 96188 49181 | NA | TRIU6632949 |  |  | NA | Vishakapatnam | Preventive Maintenance | [57 empty] | 2025-05-21 12:45 | 2025-05-15 |  |  |  |  | TRIU6632949 |  |  |  | Carrier | 3 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=13NJIxAYwOOoE4IkLtSJcSt9z_0HB5L07 | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 and 20 | 9.6,9.7,9.8 | 385386385 | Short | PM service | PM Sarvice comperted chek all unit opration Valtoge and moter Ams gas lavel and Presser. Chek all Sencer reding. Sort PTI Pass, The Condenter lauld coul was very dirty, Cleaned it with water. | No | https://drive.google.com/open?id=1fgeuB7xiBfki7rjm4I2xfByyM8BVWuwU | https://drive.google.com/open?id=1rnNOX9mclXL8-t8FCGQdN15YJ_8YEEuH |  | NA | No | Yes | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY042/25 | 2025-05-17 16:21 | crm@crystalgroup.in | DR REDDY CTO 06 | Sai Babu | +91 96188 49181 | NA | KKFU6712802 |  |  | NA | Vishakapatnam | Preventive Maintenance | [57 empty] | 2025-05-21 12:58 | 2025-05-15 |  |  |  |  | KKFU6712802 |  |  |  | Carrier | 4.2 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 and 20 | 9.6,9.8,9.7 | 385386386 | Short | PM service | PM Service Completed check all unit operation Voltage and moter ams and gass loved chak all Sencer reading and Presser. Unit sort PTI Pass. The Condenser cuil was very dirty, cleaned it with water. | No | https://drive.google.com/open?id=1qxxweqZq2b-8eLHO-ZVgcveTtz9soiMx | https://drive.google.com/open?id=1lJ5yPdDeKMoUtt0lrkkPF4OKHf33JrVF |  | NA | No | No | Can be done on next PM | 0 | 0 | sarveshk392@gmail.com | REEFER
MAY043/25 | 2025-05-19 17:39 | crm@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | Meghana Joshi | 74996 11761 | CEO | GRMU3707485 | MOTOR MAKING NOISE | Shahbuddin Sir | NA | Dahanu | Running with issues |  |  |  | 2025-05-19 19:57 | technician@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | GRMU3707485 | 20FT STD - 3 machine | Carrier | SERVICE-AT SITE | LEASE | FOC | Unit not working with AL 22 | Disconnected Defective motor & wiring | Thin Line single phase Evaprator motor | Yes | Evaporator motor Defective over heating | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY043%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | used | NA | SHAHBUDDIN | Yes | MOTOR MAKING NOISE | 2025-05-20 15:22 | operation@crystalgroup.in | YES | IN031 | 2025-05-20 | Spares | TAKSHAVI PRIVATE LIMITED | Dahanu | GRMU3707485 | SITE | PAID | CARRIER-THINLINE | 2025-05-22 14:58 | operation@crystalgroup.in | YES | IN031 | YES | https://drive.google.com/open?id=1bItqlExbJ4q0jfsoxiCZAHoKQzlsxE6W | Vendor | 2025-05-23 18:14 | qualitycontrol@crystalgroup.in | YES | IN031 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-05-21 13:23 | 2025-05-17 |  |  |  |  | MURU4501435 |  |  |  | Daikin | -19'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S-33. D1240 | R-9.6. B-9.7. Y-9.8 | 404/405/404 | Not done | We have attende tha unit found condenser coil havy durty and keypad not working and al E406 section gas temperature sensor,alE411ambient temperature sensor | We have condenser coil wash with normal water after unit running good condition | Yes | https://drive.google.com/open?id=1BectOp-sKuOn-a6CkuUORtWon1Bz8qCs | https://drive.google.com/open?id=1vHv1j1iK2ctAjizXAUd4oD0ejItM6XXb |  | Trip091 | Yes | Yes | Can be done on next PM | Sensor replace, keypad replace | Section gas temperature sensor, ambient temperature sensor | rajreefertech@gmail.com | REEFER
MAY044/25 | 2025-05-19 18:04 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | NA | NA | CXRU1045453 |  |  | NA | Rajpura, Punjab | Preventive Maintenance | [57 empty] | 2025-05-26 12:17 | 2025-05-18 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | +2'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-151. D-1872 | R-11.6. B-11.8. Y-11.7 | L1-393. L2-395. L3-394 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1dLB59sBSzNm2K1gr7wt6hAhgisdhBcfa | https://drive.google.com/open?id=1JK4Fp8b0A8M0BDhPWTm6BR-q3xsfwkjS |  | Trip091 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY045/25 | 2025-05-19 18:05 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | NA | NA | TCLU1130265 |  |  | NA | Rajpura, Punjab | Preventive Maintenance | [57 empty] | 2025-05-26 12:03 | 2025-05-18 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | -20'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-... D-21.2 bar | R-10.8. B-11.5. Y10.9 | L1-389. L2-390. L3-389 | Short | We have attende tha unit found condenser coil havy durty and eveporetor coil havy iecing | We have work condenser coil wash with normal water and eveporetor coil ice clean after unit running sound condition | No | https://drive.google.com/open?id=1g81DkY1W0sZg1_Ve6uXHG2SnPICp10XR | https://drive.google.com/open?id=12SATGN9utkvj3Iv7tSK8w9edZuY9W6as |  | Trip091 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY046/25 | 2025-05-19 18:07 | crm@crystalgroup.in | ITC Ltd | Neeraj Mani | +91 73199 35205 | NA | BMOU9785278 | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | Pushpa Mam | NA | Munger, Bihar | Complete Breakdown |  |  |  | 2025-05-21 11:08 | service@crystalgroup.in | ITC LTD | BMOU9785278 | 40FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Compressor not working/ No cooling | Need to change compressor terminal/ Compressor. | Compressor Terminal, Compressor, compressor gasket, refrigerant | Yes | Compressor not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY046%2F25 | RFH40R | DAIKIN | 0 | 0 | 0 | Used | 0 | RAJ KUMAR | Yes | COMPRESSOR MAKING NOISE, MOTOR MAKING NOISE | 2025-05-30 10:21 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-30 10:22 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-30 10:22 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-30 10:53 | 2025-05-29 |  |  |  |  | BMOU9785278 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | ON CALL | ON CALL | No | https://drive.google.com/open?id=1skHMBP9wFSnJAYybWy8-1IGwiNuHleC5 | https://drive.google.com/open?id=1q24nClyyCbMV6ZbPavizAgZuLJBURGrT |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAY047/25 | 2025-05-21 12:45 | crm@crystalgroup.in | Hetero Bio Pharma | Ramesh AVS | 9099033689 | NA | CICU3876565 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Lina | VenkataSitaRamesh.A@hetero.com | Jadcherala | Running with issues | Pay load Cap: 8.140 Kgs as per the details on container, is causing in the control system low pressure tripping around – 18 Deg C during running condition after discussion with technician also problem will not resolved. This issue is affecting our workflow and needs immediate attention. |  |  | 2025-05-22 19:27 | service@crystalgroup.in | Hetero Bio Pharma | CICU3876565 | 10FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Display not working, compressor tripping above the set temp. | Onsite check | Daikin Display | Yes | compressor tripping, temperature not going below -16 c. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY047%2F25 | Daikin | DAIKIN | 0 | 0 | 0 | Brand New | 0 | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-07-02 12:41 | operation@crystalgroup.in | YES | IN086 | 2025-06-26 | Spares | Hetero Bio Pharma | Hyderabad | CICU3876565 | SITE | FOC | DAIKIN | 2025-07-02 12:58 | operation@crystalgroup.in | YES | IN086 | YES | https://drive.google.com/open?id=1L3kYQKKrtHVwEVUFJoQS2DaJWuZ0l1Wd | Vendor | 2025-07-04 10:55 | qualitycontrol@crystalgroup.in | YES | IN086 | COURIER | 34498854806 | BLUE DART |  | https://drive.google.com/open?id=1lbnvMUZuUqWrLJMJKsEoF2izWGtrjHru |  | 2025-07-17 12:20 | 2025-07-07 |  |  |  |  | CICU3876565 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/20br | 9.9/9.8/9.9 | 393/394/393 | Short | Defective compressor & LP switch | Replaced compressor & LP switch | No | https://drive.google.com/open?id=1YBwZAkC6FuoFzrj1lX4QccrngbEQlOf1 | https://drive.google.com/open?id=1RNGkuG94nH4LMKRg490NLYy18vdb2aiT |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
MAY048/25 | 2025-05-21 13:22 | crm@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | Dharmender Tiwari | 9700033475 | Deputy Manager | TITU9930004 | DISPLAY NOT VISIBLE | Pushpa Mam | dharmender.tiwari@dsv.com | Hyderabad | Running with issues |  |  |  | 2025-05-22 19:37 | service@crystalgroup.in | DSV Air & Sea Pvt. Ltd. | TITU9930004 | Thermoking | Plus | SERVICE-AT SITE | NA | CHARGEABLE | Display not working | Replace display | Thermoking Display | Yes | Display not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY048%2F25 | 14D8550HT | plus | 14D8550HT | EOG1000568 | 0 | NEW | 0 | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE | [29 empty] | 2025-05-27 17:11 | 2025-05-20 |  |  |  |  | TITU9930004 |  |  |  | Thermo king | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Full | Need to replaced Control Panel Display | Gas top up done & run tested | Yes | https://drive.google.com/open?id=1J4FF--5zDROevkNsT8_Bwp2soYnOMVfh | https://drive.google.com/open?id=1X-rky1MOh0USCv_10lbIw7ldp-GPM7Kv |  | NA | No | Yes | Can be done on next PM | NA | Control Panel Display | crm@crystalgroup.in | REEFER
MAY049/25 | 2025-05-22 17:53 | crm@crystalgroup.in | Zepto | Paras | 918882625720 | NA | KKFU6711832 | FLUCTUATIONS IN TEMEPRATURE | Lina | NA | Delhi | Complete Breakdown |  |  |  | 2025-05-22 19:45 | service@crystalgroup.in | Zepto | KKFU6711832 | 40FT STD RF | Carrier - Thinline | SERVICE-AT SITE | NA | NA | Temperature fluctuation, breakdown | site check |  |  | site check | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY049%2F25 | Carrier - Thinline | CARRIER-THINLINE | 0 | 0 | 0 | Refurbished | 0 | RAJ KUMAR | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-05-26 15:34 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-26 15:35 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-26 15:35 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-26 11:29 | 2025-05-23 |  |  |  |  | KKFU6711832 |  |  |  | Carrier | 1.2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Need to replace | Okay | Okay | Done | Clean |  | S1.8bar D17.9bar | R19.1 B17.9. Y18.8 | L1-370. L2-372. L3-372 | Short | We have attende tha unit found condenser coil havy durty and eveporetor coil havy durty | We have work condenser coil and eveporetor coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=17nRAg8Nrltbf0ezUP5duDwErKxh0-a_w | https://drive.google.com/open?id=1_AgrPNao7dGGrzJH-CiobIZIn0LBFT-R |  | TRIP091 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY050/25 | 2025-05-23 15:24 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | MYRU4501435 |  |  | Nitin55.Sharma@ril.com | Sirhind, Punjab | Preventive Maintenance | [57 empty] | 2025-06-08 16:18 | 2025-05-17 |  |  |  |  | MYRU4501435 |  |  |  | Daikin | -19'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S-33. D-1240 | R-9.6. B-9.7. Y-9.8 | L1-404. L2-405. L3-404 | Not done | We have attende tha unit found condenser coil havy durty and keypad not working and E-411, ambient temperature sensor E-406 section gas temperature sensor | We have work condenser coil wash with normal water after unit running good condition | Yes | https://drive.google.com/open?id=1gbSOuNjbdIw7prYknn42oQE28i78Rb3r | https://drive.google.com/open?id=1HXD6VlIDnzPdhxq1i6L8TDLILhJn97P9 |  | Trip095 | Yes | No | Can be done on next PM | Sensor and keypad | Ambient temperature sensor, section gas temperature sensor | rajreefertech@gmail.com | REEFER
MAY051/25 | 2025-05-26 10:39 | crm@crystalgroup.in | RIL QWIK SUPPLY | Suman | 8471812230 | NA | CICU1799135 | Tripping Issue | Pushpa Mam | NA | Chennai | Complete Breakdown |  |  |  | 2025-05-26 18:44 | service@crystalgroup.in | RIL QWIK SUPPLY | CICU1799135 | 10FT Spl RF | Thermoking MP-4000 | SERVICE-ON CALL | NA | NA | Compressor tripping issue, Cooling Low | On call service done by technician , now cooling is okay. |  | No | Compressor tripping issue, Cooling Low | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY051%2F25 | Thermoking MP-4000 | TK-MP4000 | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | BRand NEW | 0 | SHAHBUDDIN | No | Tripping Issue | 2025-05-27 12:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-05-27 12:42 | crm@crystalgroup.in | NO |  |  |  |  | 2025-05-27 12:42 | crm@crystalgroup.in | NO | [7 empty] | 2025-05-29 16:02 | 2025-05-18 |  |  |  |  | CICU1799135 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 9.9/9.8/9.8 | 406/407/406 | Not done | Unit found on vedeo call with single phase tripping off | Found main MCB Defective advise to replaced 32A main mcb. After replaced advise to clints for pm and complete Run unit observe working & maintain set temp. | No | https://drive.google.com/open?id=130rRdZHNlXFawONDzxbmrnE-ItrVrgfU | https://drive.google.com/open?id=1GFR4wi3N4qkR_JbnaloxdH-4JfnXZkN1 |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY052/25 | 2025-05-26 11:38 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | NYKU7931452 | REPAIRS & REPLACEMENT | Rajkumar | Nitin55.Sharma@ril.com | Sirhind, Punjab | Running with issues | Supply Sensor |  |  | 2025-05-26 11:47 | crm@crystalgroup.in | Qwik Supply | NYKU7931452 | 40 Feet Refer | Carrier | REPAIR | LEASE | FOC | Supply Sensor Replacement | Sensor required 2nos | Supply Sensor 2 Nos | Yes | SUPPLY SENSOR INSTALLATION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY052%2F25 | Carrier 40 Feet | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | REPAIRS & REPLACEMENT | 2025-05-26 15:20 | operation@crystalgroup.in | YES | IN037 | 2025-05-26 | Spares | QWIK Supply | Sirhind | NYKU7931452 | SITE | FOC | CARRIER-THINLINE | 2025-05-28 09:30 | operation@crystalgroup.in | YES | IN037 | YES |  | Stock | 2025-05-30 17:54 | qualitycontrol@crystalgroup.in | YES | IN037 | COURIER | 17815028766 | blue dart |  | https://drive.google.com/open?id=1HBZv27PU2BRU2fiyUWAhc7sqwO_CeWCT |  | 2025-06-26 08:07 | 2025-06-12 |  |  |  |  | NYKU7931452 |  |  |  | Carrier | -19'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 bar/ 12.8bar | R-11.1/B-10.9/Y-110 | 390/392/391 | Not done | We have attende tha unit found al 54 - supply sensor failure | We have work supply sensor 2 nose replace on call after unit running sound condition | No | https://drive.google.com/open?id=1kb0THZ5AiES6lYkyGdjXUzLb69y2tQ4B | https://drive.google.com/open?id=11tWriUf4SVXMzFK_8zdWKQBZwswu9_lH |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY053/25 | 2025-05-26 12:45 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | MYRU4501435 | REPAIRS & REPLACEMENT |  | Nitin55.Sharma@ril.com | Sirhind, Punjab | Running with issues |  |  |  | 2025-05-26 14:32 | crm@crystalgroup.in | Qwik Supply | MYRU4501435 | 40 Feet | Daikin | SERVICE-ON CALL | LEASE | FOC | After completing PM service required spares | Keypad, Section Gas Sesor, Ambient Sensor | Keypad, Section Gas Sesor, Ambient Sensor | Yes | Spares required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY053%2F25 | DAIKIN III | DAIKIN | NA | LXE10E136A | NA | Refurbished | NA | RAJ KUMAR | Yes | REPAIRS & REPLACEMENT | 2025-05-26 15:23 | crm@crystalgroup.in | YES | IN038 | 2025-05-26 | FOC | Qwik Supply | Sirhind | MYRU4501435 | SITE | FOC | DAIKIN | 2025-05-28 09:31 | operation@crystalgroup.in | YES | IN038 | YES |  | Stock | 2025-05-30 17:55 | qualitycontrol@crystalgroup.in | YES | IN038 | COURIER | 17815028766 | blue dart |  | https://drive.google.com/open?id=1kMjAmBl-EAI4afEyakRgumH_LgBmXN2I |  | 2025-06-26 08:15 | 2025-06-12 |  |  |  |  | MYRU4501435 |  |  |  | Daikin | -19'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -11.9psi. /1120psi | 9.8/9.9/10 | 399/400/400 | Not done | We have attende tha unit found al E-406 section gas temperature sensor,E411- ambient temperature sensor, keypad not working | We have work section gas temperature sensor ambient temperature sensor keypad replace after unit running sound condition | No | https://drive.google.com/open?id=1bah9NpTxeN-qn7ln0ZLqshWToX63-vG1 | https://drive.google.com/open?id=1QemE1thWJFqcSjIntb3HP3JGP45LbDBG |  | Na | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
MAY054/25 | 2025-05-27 15:28 | crm@crystalgroup.in | Vins Bio Products Pvt Ltd | Phani Kumar | +91 9398316260/ +91 9666392909 | NA | CPLU3181670 | MOTOR MAKING NOISE | Pushpa Mam | NA | Hyderabad | Complete Breakdown | EVP Motor not working properly 2nos |  |  | 2025-05-27 19:33 | service@crystalgroup.in | Vins Bio Products Pvt Ltd | CPLU3181670 |  | NA | SERVICE-AT SITE | NA | NA | MOTOR MAKING NOISE | REPLACEMENT OF EVP Motor - 2nos | EVP Motor - 2nos | Yes | EVP Motor not working properly 2nos | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY054%2F25 | NA | NA | 0 | 0 | 0 | NA | 0 | SHAHBUDDIN | Yes | MOTOR MAKING NOISE | 2025-06-19 15:28 | crm@crystalgroup.in | YES | IN075 | 2025-06-19 | Consumables, Spares | Vins Bio Products Pvt Ltd | Hyderabad | CPLU3181670 | SITE | PAID | CARRIER-THINLINE | 2025-07-04 11:29 | operation@crystalgroup.in | YES | IN075 | YES | https://drive.google.com/open?id=1jEx29xzj-TasCdlMtqP5gWqXu2ekQbY_ | Stock and Vendor | 2025-07-04 11:44 | qualitycontrol@crystalgroup.in | YES | IN075 | COURIER | 34498854795 | BLUE DART |  | https://drive.google.com/open?id=1mnkzSRg1W2lFLLoHuCE7rpwFgwXXlazq |  | 2025-07-10 19:57 | 2025-07-09 |  |  |  |  | CPLU3181670 |  |  |  | Carrier | 4c | Clean | Clean |  | Okay | Clean | Need to replace | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/12 bar | 13.2/13.3/13.3 | 412/413/412 | Short | Trouble shots & found Filter Drier clogged. compressor contactor burn/ found low a gas R134 a. | pump down systemc& replaced new filter Drier . run unit observation working as satisfactory. need to replaced compressor contactor | Yes | https://drive.google.com/open?id=1-9w_I2w5-K4iXZ3ylMJpJcLahxlhASiH | https://drive.google.com/open?id=1kBCQ4KufkWNMzxMKPv6a7_9bitvAdA_w |  | 101 | No | No | Can be done on next PM | evp. motor & contactor | 1. Evaprator motor thin line single phase2. Compressor contactor 30A | technician@crystalgroup.in | REEFER
MAY055/25 | 2025-05-27 16:38 | crm@crystalgroup.in | UPS | Nadeem & Venkat | 9700137866 & 99517 80321 | CRM | SJKU4000110 | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE |  | Nadeemuddin.mohammed@marken.com | Hyderabad | Running with issues |  |  |  | 2025-05-27 19:42 | service@crystalgroup.in | UPS | SJKU4000110 | 40FT STD RF | Thermoking | SERVICE-AT SITE | NA | NA | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | need to replace display Thermoking mp- 4000 | Thermoking mp- 4000 | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY055%2F25 | Thermoking | TK-MP4000 | 0 | 0 | 0 | Brand New | 0 | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | 2025-05-28 15:43 | operation@crystalgroup.in | YES | IN045 | 2025-05-28 | Spares | UPS | Hyderabad | SJKU4000110 | SITE | FOC | TK-MP4000 | 2025-06-07 15:15 | operation@crystalgroup.in | YES | IN049, IN051 | YES | https://drive.google.com/open?id=1xshJSy6cMSdiky9UjM-fJ2MlLu9-pqxp | Vendor | 2025-06-26 17:31 | crm@crystalgroup.in | YES | IN045 | COURIER | 25017200066374 | Shree Maruti Courier Tracking |  |  |  | 2025-06-30 23:20 | 2025-06-29 |  |  |  |  | SJKU4000110 |  |  |  | Thermo king | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19br | 9.9/9.9/9.8 | 405/406/405 | Short | Check & found Return air sensor faulty reading abnormal temperature& Display faded not readable | Replaced Return air sensor & Display. | No | https://drive.google.com/open?id=1ZibRVqAokV5iNKWAUswuMc0Gm7GBDXj7 | https://drive.google.com/open?id=1AGAVgUXpivekK0mua9G2PReU_d1xN_ld |  | 101 | No | No | Can be done on next PM | N | NA | technician@crystalgroup.in | REEFER
MAY056/25 | 2025-05-27 16:41 | crm@crystalgroup.in | UPS | Nadeem & Venkat | 9700137866 & 99517 80321 | CRM | HDMU5220720 | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE |  | Nadeemuddin.mohammed@marken.com | Hyderabad | Running with issues |  |  |  | 2025-05-27 19:46 | service@crystalgroup.in | UPS | HDMU5220720 | 20FT STD RF | Carrier Thineline | SERVICE-AT SITE | NA | NA | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | Replacement of of Carrier Thinline Display | Carrier Thinline Display | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY056%2F25 | Carrier Thineline | CARRIER-THINLINE | 0 | 0 | 0 | USed | 0 | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE, ALARM CODE VISIBLE | 2025-05-28 15:45 | operation@crystalgroup.in | YES | IN044 | 2025-05-28 | Spares | UPS | Hyderabad | HDMU5220720 | SITE | FOC | CARRIER-THINLINE | 2025-06-07 15:21 | operation@crystalgroup.in | YES | IN056 | YES |  | Stock | 2025-06-11 16:37 | operation@crystalgroup.in | YES | IN056 | COURIER | 25017200066374 | SHREE MARUTI |  | https://drive.google.com/open?id=1Wzxv06TXFtxca-5Rcp3RMJmuGoMp8Eoz |  | 2025-06-20 11:49 | 2025-06-06 |  |  |  |  | HDMU5220720 |  |  |  | Carrier | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/180PSIG | 12.4/12.5/12.4 | 417/416/417 | Short | Unit Internal tube light burnt wiring | Repaired burnt wiring & replaced tube light. Unit run & observation found working as satisfactory | No | https://drive.google.com/open?id=1VorUrhRDymH0nslmJvOZU7XtdlZBFAoa | https://drive.google.com/open?id=1_MqQEchCw3a2Nxybw0ppM1X8ZD_9bEu_ |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY057/25 | 2025-05-28 12:10 | crm@crystalgroup.in | Hetero Unit 5 | B. SHYAMSUNDER | 9154266430 | Asst Manager | SUDU6218004 | REPAIRS & REPLACEMENT | Pushpa Mam | ShyamSunder.B@hetero.com | Jadcherala | Running with issues | Main power control unit inside panel wiring is not presentable and need to proper wiring and dressing. Main power control unit panel door gaskets failure and rain water enter into the unit. Cold chamber container inside temperature sensor is not in position and needs to fixed properly. Container inside chamber SS wall sheet screws is missing and gaps observed, needs to fixed properly. Electrical hooter wiring connection needs to be laying though inside the container and verified the working condition of hooter with in the set temperature limits. Emergency push buttons provision required cold chamber container inside and out side. If any abnormality SMS communication alerts massage required at lest two mobile numbers. |  |  | 2025-05-29 11:29 | service@crystalgroup.in | Hetero Unit 5 | SUDU6218004 | 40FT STD RF | Carrier-Primeline | SERVICE-AT SITE | NA | NA | Water leakage in Control Panel, Service Of Reefer Unit, need External Alarming & Mantrap system | Service needed | Mantrap system with 2nos. switch, External temp. alarm system and servicing material | Yes | Servicing of unit | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY057%2F25 | Carrier-Primeline | CARRIER-PRIMLINE | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | 0 | RAJ KUMAR | Yes | REPAIRS & REPLACEMENT | 2025-07-04 11:21 | operation@crystalgroup.in | NO | [9 empty] | 2025-07-04 11:22 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-04 11:25 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-04 22:43 | 2025-06-28 |  |  |  |  | SUDU6218004 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/10br | 9.9/9.8/9.8 | 406/407/406 | Short | Water entering electrical panel . resolved and fixed shade. and unit pm due. | PM Complited and required fixed mantrap | No | https://drive.google.com/open?id=1oJO3zQFHvX2p0qTVRw7-EUWqBleUYKRy | https://drive.google.com/open?id=1lLOSR8YNNzKTVihldbkFQF3hEw6-fMFG |  | 101/HYD | Yes | No | Can be done on next PM | man trap & extra te.p. Sensors from hetro | NA | technician@crystalgroup.in | REEFER
MAY058/25 | 2025-05-28 17:22 | crm@crystalgroup.in | Qwik Supply Bhiwadi | Ganesh Minde | +91 95107 75974 | NA | CICU1799161 |  |  | NA | Bhiwandi | Preventive Maintenance |  |  |  | 2025-05-29 11:34 | service@crystalgroup.in | Qwik Supply Bhiwadi | CICU1799161 | 10 FT BLAST | Thermoking MP-4000 | SERVICE-AT SITE | NA | NA | Temperature not archive to set temperature, temperature fluctuation. | Site check. |  | No | Temperature not archive to set temperature, temperature fluctuation. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY058%2F25 | Thermoking MP-4000 | TK-MP4000 | 0 | LSM60198823 | 0 | BRand NEW | 0 | SHAHBUDDIN | Yes | [30 empty] | 2025-06-14 13:42 | 2025-06-11 |  |  |  |  | CICU1799161 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 10.1/10/10 .1 | 400/401/400 | Short | PM servicev Due | PM service completed & run unit observation found as satisfactory | No | https://drive.google.com/open?id=1VVEx4M8mZTLJ3VALFLoyAvR4Di7g_oyy | https://drive.google.com/open?id=1GKqDs0THSBqAKujKiSP5zXQLUyoJQNm5 |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY059/25 | 2025-05-28 17:28 | crm@crystalgroup.in | Qwik Supply Bhiwadi | Ganesh Minde | 9510775974 | NA | CICU2094031 |  |  | NA | Bhiwandi | Preventive Maintenance |  |  |  | 2025-05-29 11:37 | service@crystalgroup.in | Qwik Supply Bhiwadi | CICU2094031 | 10 ft reefer | Thermoking | SERVICE-AT SITE | NA | NA | Temperature not archive to set temperature, temperature fluctuation. | site check |  | No | Temperature not archive to set temperature, temperature fluctuation. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY059%2F25 | Thermoking | Magnum Plus | E0GM029789 | ABC782800321480264 | 0 | BrandNew | 0 | SHAHBUDDIN | Yes | [30 empty] | 2025-06-14 13:46 | 2025-06-11 |  |  |  |  | CICU2094031 |  |  |  | Thermo king | -35c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/21br | 9.9/10/9.9 | 402/405/403 | Short | PM service Due | PM servicecompleted with observation& found unit working fine | No | https://drive.google.com/open?id=1mLJ0pKJdZt6kicFZiDqkgVfCrc7IEcAD | https://drive.google.com/open?id=1n7qiCXlg3iHujhUtUtkRqT_Mt98EuxbQ |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
MAY060/25 | 2025-05-30 12:19 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | +91 6307 373 723 | NA | MYRU4518356 |  |  | NA | Lucknow | Preventive Maintenance | [57 empty] | 2025-06-08 18:32 | 2025-05-31 |  |  |  |  | MYRU4518356 |  |  |  | Daikin | +4'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S-77. D-1561 | R-10.1. B-10.3. Y-10.3 | L1-401. L2-400. L3-402 | Not done | We have attende tha unit found condenser coil havy durty and keypad (set key) not working alarm E-406. section gas temperature sensor | We have work condenser coil wash with normal water after unit running good condition | Yes | https://drive.google.com/open?id=1-KdIkphJtLzFjGyXOn6I4h5IUADNboxN | https://drive.google.com/open?id=1KkP2-jsuV6hx5t1tAu6PUOH4Q5SCYxK4 |  | Trip095 | Yes | No | Can be done on next PM | Key pad and section gas temperature sensor | Keypad and section gas temperature sensor | rajreefertech@gmail.com | REEFER
MAY061/25 | 2025-05-30 16:02 | crm@crystalgroup.in | DHL Supply Chain pvt Ltd | Ajay Solanki | 9157904500‬ | NA | TCLU1912270 | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | Sushma | NA | Ahmedabad | Running with issues | Temperature Fluctuation, Ice formation on Compressor | Call | Lina | 2025-06-04 15:44 | crm@crystalgroup.in | DHL | TCLU1912270 | 20 Feet | Daikin | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | NEED TO SET TEMPERATURE |  |  | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY061%2F25 | 20 Feet | TK-MP3000 | NA | NA | NA | NA | NA | RAJ KUMAR | Yes | FLUCTUATIONS IN TEMEPRATURE, ICE FORMATION | 2025-07-02 16:12 | operation@crystalgroup.in | NO | [9 empty] | 2025-07-02 16:12 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-02 16:13 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-10 17:58 | 2025-06-14 |  |  |  |  | TCLU1912270 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | NA | Issue resolved on call. | No | https://drive.google.com/open?id=16rG3jPSt3y8Akvk_w0ceRVP5171jL4pS | https://drive.google.com/open?id=1LSDHAAGp6rSpOEUJkQqMn-bQ0r-4HK3I |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
MAY062/25 | 2025-05-31 15:52 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | PRGU4958724 |  |  | NA | Vishakapatnam | Running with issues |  | Call | Ramiz | 2025-06-04 16:27 | crm@crystalgroup.in | Lauras Lab Unit 2 | PRGU4958724 | 40 Feet | Carrier | SERVICE-AT SITE | LEASE | FOC | Controller Panel | HTT Sensor, Defrost Sensor & Keypad | HTT Sensor, Defrost Sensor & Keypad - Qty 01 Nos | Yes | Controlller Panel | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=MAY062%2F25 | 40 Feet | CARRIER-THINLINE | NA | NA | NA | NA | NA | RAMIZ | Yes |  | 2025-06-04 17:13 | crm@crystalgroup.in | YES | IN050 | 2025-06-04 | Spares | LAURUS SYNTHESIS UNIT 2 | Vishakapatnam | PRGU4958724 | SITE | FOC | CARRIER-THINLINE | 2025-06-07 15:29 | operation@crystalgroup.in | YES | IN050 | YES | https://drive.google.com/open?id=1329d4FFGHZ-PZZF9obWUR4KbTY5IYqsG | Vendor | 2025-06-26 17:26 | crm@crystalgroup.in | YES | IN050 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-08-20 11:04 | 2025-07-28 |  |  |  |  | PRGU4958724 |  |  |  | Carrier | 5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 10B | 12.4A 12.4A 12.4A | 410V 410V 410V | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1FG61r883O-VeTmSBc5A1mmk0b5Erw_Zd | https://drive.google.com/open?id=1D2WhsTN9QlBUa4pPRCz9qebDmrEeQhkv |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
MAY063/25 | 2025-05-31 15:57 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | CXRU1031845 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 17:03 | 2025-05-30 |  |  |  |  | CXRU1031854 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3/11.4b | 9.8 | 407 | Not done | Found Condenser coil very dirty, inlet sensor & outlet sensor & Suction sensor & supply & return need to replace | Clean condenser coil with fresh water.all temperature sensors need to replace soon | Yes | https://drive.google.com/open?id=1CUgrXVVCRF1mzlbM2Cth4OdfDTWVpiyz | https://drive.google.com/open?id=19i0xhd2sxCR53MYifhNMe8Kgmr6EfE5t |  | Na | No | No | Can be done on next PM | Need to replace all temperature sensors | Inlet sensor -1 Outlet sensor -1 Suction sensor -1 Return sensor -2 Supply sensor- 2 | technician@crystalgroup.in | REEFER
MAY064/25 | 2025-05-31 16:10 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | BMOU9782197 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-02 23:25 | 2025-05-30 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2&11.5 | 10.1 | 407 | Not done | Found Condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=19g4bGreabTBugF5ULLMWnlNTGB301QiJ | https://drive.google.com/open?id=1pMm_KLpTh5s-MX_GTGKYfdpG0Htt6aES |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
MAY065/25 | 2025-05-31 16:27 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharges | CXRU1036533 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-02 23:19 | 2025-05-30 |  |  |  |  | CXRU1036533 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3&12.5 | 9.9 | 407 | Not done | Found Condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=1eLH0u8rk8O6jlQKVLK01VuRI5QZEx_SP | https://drive.google.com/open?id=1eudBLFo1cEwOZYmTOE6Y05NA9Jkl_DXt |  | NA | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
MAY066/25 | 2025-05-31 16:32 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | GESU9529290 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 17:08 | 2025-05-30 |  |  |  |  | GESU9529290 |  |  |  | Carrier | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/114b | 9.8 | 408 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked all parameters are good. | No | https://drive.google.com/open?id=1SbOofpODTvgDsPdSaljSAv5L8lQMRRVC | https://drive.google.com/open?id=1Gf75Cd6HPTtAkt1RaGG28CVIiDyAee0D |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
MAY067/25 | 2025-05-31 16:38 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | HDMU5584444 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Email | Ramiz | [54 empty] | 2025-06-02 23:30 | 2025-05-30 |  |  |  |  | HDMU5584444 |  |  |  | Thermo king | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.6&16.8b | 8.7 | 407 | Not done | Found Condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=1il1P35LHopeG4ofAQ8ZR5IaimpivSd-s | https://drive.google.com/open?id=1AwdQJi4xSRiwV9ZFRVFdr04EWikvzykj |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
MAY068/25 | 2025-05-31 16:46 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | CRSU6101910 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-02 23:35 | 2025-05-30 |  |  |  |  | CRSU6101910 |  |  |  | Carrier | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7&13.b | 12.1 | 407 | Not done | Found Condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=1ITdh9LMa8RzkTypdz-IDYffKV-vhmPZe | https://drive.google.com/open?id=1oYoa-QKRfBiQh3B7UwB34yt_WqOOLIUs |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
JUN001/25 | 2025-06-02 11:04 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 916307373723 | NA | CICU3876605 |  |  | NA | Lucknow | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-06 13:23 | 2025-05-31 |  |  |  |  | CICU3876605 |  |  |  | Thermo king | -40'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S---- D-22.3bar | R-11.9. B11.9. Y11.8 | L1-405v. L2-403v. L3-404v | Short | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=16RHyc1biyFr-HKCJf68DtG7r71a8_IL8 | https://drive.google.com/open?id=1w1-yB2oCQQqvHtIp7w7KPq2oOV15N4Ry |  | Trip095 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN002/25 | 2025-06-02 11:08 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 916307373723 | Manager | TDRU7151675 |  |  | NA | Lucknow | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-08 18:46 | 2025-05-31 |  |  |  |  | TDRU7151675 |  |  |  | Daikin | -5'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S-152. D1331 | R-9.8. B-10.1. Y-9.9 | L1-405. L2-403. L3-404 | Not done | We have attende tha unit found condenser coil havy durty and alarm E-402 data recorder supply sensor, E-411 ambient temperature sensor | We have work condenser coil wash with normal water after unit running good condition | Yes | https://drive.google.com/open?id=12-ZwaqWnT17Oq0jvbctEL9QoLVQmL16n | https://drive.google.com/open?id=17je3sAn_7cgO9b--QhmhZJT6PjoFQVzA |  | Trip095 | Yes | No | Can be done on next PM | Sensor | Supply recorder and ambient temperature sensor | rajreefertech@gmail.com | REEFER
JUN003/25 | 2025-06-02 11:12 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 916307373723 | Manager | TCLU1903088 |  |  | NA | Lucknow | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-02 23:07 | 2025-05-30 |  |  |  |  | HDMU5586473 |  |  |  | Thermo king | +22'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.8& 16.5b | 8.7 | 407 | Not done | Found Condenser coil dirty. | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=1ERXdyv2zObNHADlUz_KljdT4D-9vlOLc | https://drive.google.com/open?id=1Hlpwx241n3sGocNMJK0PmVSZkaoBXYq6 |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
JUN004/25 | 2025-06-02 12:22 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | MYRU4505847 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-03 00:08 | 2025-05-31 |  |  |  |  | MYRU4505847 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/11.5b | 9.8 | 405 | Not done | Found Condenser coil dirty | Clean the condenser coil with fresh water. Checked all parameters are good. | No | https://drive.google.com/open?id=1mzzXpsmo4msjzMKLqAw8ca6gaJ03cSBG | https://drive.google.com/open?id=1xUp9Ex_hNhp_0qoHw9P-W6qxnbX-CuYV |  | Na | No | No | Can be done on next PM | Na | Na | rrmondal.786@gmail.com | REEFER
JUN005/25 | 2025-06-02 12:33 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site Incharge | HDMU5586473 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 16:52 | 2025-05-30 |  |  |  |  | HDMU5586473 |  |  |  | Thermo king | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.8/16.5b | 8.5 | 407 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked all parameters are good. | No | https://drive.google.com/open?id=1XkB6IUoOEg9ATCsbQ4BkIUvDT68g2mB8 | https://drive.google.com/open?id=1Zc1ObPFNyqMKnEenW_vZS5UTENEYqDPc |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN006/25 | 2025-06-02 12:37 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | SUDU6257274 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-07-25 17:52 | 2025-06-11 |  |  |  |  | SUDU6257274 |  |  |  | Carrier | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | NA | NA | No | https://drive.google.com/open?id=1yKhmVgtE9oF1oe8uKbPrN8Isi-RXgEmN | https://drive.google.com/open?id=1895OB9poc9Y61MiV0M74lZwOn7npB_NQ |  | NA | No | No | Can be done on next PM | CONTAINER TO BE OFFLEASED- AS PER DISCUSSION WITH PUSHPA MAM | NA | crm@crystalgroup.in | REEFER
JUN007/25 | 2025-06-02 14:45 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | GESU9460634 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Email | Shabuddin | [54 empty] | 2025-06-02 23:57 | 2025-06-01 |  |  |  |  | GESU9460634 |  |  |  | Carrier | 3.6c | Clean | Need to replace |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/13.6br | 11.4/11 5/11.4 | 407/408/407 | Short | Unit condenser coil oil trace suspected with Minar leakage and Evaprator Heater coil need to replaced unit FAIL Auti PTI - P-1 | Adding Refrigerant Gas 2kg R134A & PM COMPLITED.. UNIT MAINTAIN SET TEMP. | No | https://drive.google.com/open?id=1j9WRRILUfL-6tTn4NYK9h-neXiayWuqZ | https://drive.google.com/open?id=1lGvCSLPB0QwKFxoaWctRikVcY8DWYFe6 |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN008/25 | 2025-06-02 14:47 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6008328 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Email | Shabuddin | [54 empty] | 2025-06-02 23:41 | 2025-05-31 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | +4.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/180psig | 9.9/9.8/9.8 | 407/406/407 | Short | PM Complited | Unit working as satisfactory and clean controller panel and secured damaged wiring and covered plastic to out side electrical panel for rain proof in Rainey season. | No | https://drive.google.com/open?id=1ALrNSYL-AZiJfadQSYWvuVtGOkhXzVfH | https://drive.google.com/open?id=1s2Mp-8tt6f9G9zSy2SseaYmsIDv341wj |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN009/25 | 2025-06-02 14:59 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | HDMU5542114 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 23:33 | 2025-05-31 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .3/14br | 12.6/12.5/12.6 | 414/415/414 | Short | PM Complited | Unit working as satisfactory and after mapping Unit handed over for cargo operation | No | https://drive.google.com/open?id=1gPWTnee7IQNbqVkJAOpT6G-A-qwnfAps | https://drive.google.com/open?id=1pEH1lf6JuKshzxvo_dxWOFJf0KMYr0Qp |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN010/25 | 2025-06-02 15:10 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6031328 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-02 23:23 | 2025-05-31 |  |  |  |  | PCIU6031328 |  |  |  | Daikin | 22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/180psig | 9.9/9.8/9.8 | 406/407/406 | Short | PM Complited | Unit working as satisfactory | No | https://drive.google.com/open?id=1fLyIz_A1aNF81DrueJPc2oojZoL1YgSW | https://drive.google.com/open?id=11H91d869qINuDLYg7sW9bqIIhlDtRHb4 |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN011/25 | 2025-06-02 15:12 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6032622 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 22:58 | 2025-06-02 |  |  |  |  | PCIU6032622 |  |  |  | Daikin | 22.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/195 psig | 9.8/9.9/9.9 | 407/406/407 | Short | Mapping complted with pm service | Unit working as satisfactory | No | https://drive.google.com/open?id=1fNGLndfp0Pdh8_TIuvlQNYcy63_u-sVD | https://drive.google.com/open?id=1fy5VQlpShN2zXHsJnyvTruFjv3fRR3IM |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN012/25 | 2025-06-02 15:14 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6034374 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-04 21:58 | 2025-05-31 |  |  |  |  | PCIU6034374 |  |  |  | Daikin | +22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/195 psig | 9.9/9.8/9.8 | 407/408/408 | Short | PM Complited | Unit working as satisfactory | No | https://drive.google.com/open?id=15WHLLyACuxfJjRkfME0yWU-KkaKiqGJr | https://drive.google.com/open?id=1l1Dm99RMzfP42FPYfkGEZRdOjkTfYFJU |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN013/25 | 2025-06-02 15:16 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | NYKU7931149 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 22:37 | 2025-06-01 |  |  |  |  | NYKU7931149 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .5/14br | 11.4/11.5/11.5 | 408/409/408 | Short | Unit pm service completed with secured Dispaly harness & controller Harness proper | Unit working as satisfactory.& recomnded for inter cleaning time to time. | No | https://drive.google.com/open?id=1hJknlUvwp5Lu1K_9YTS4LLFhFh0zu4vt | https://drive.google.com/open?id=1j2JAZJjglt4oAVAQezb7iZp2zdqi5D_z |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN014/25 | 2025-06-02 15:29 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | MYRU4507120 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 22:22 | 2025-06-01 |  |  |  |  | MYRU4507120 |  |  |  | Carrier | +4.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .3/24br | 10.2/10.3/10.2 | 406/407/406 | Short | PM service completed/ repaired old damaged controller wiring & secured. | Unit working as satisfactory & recomnded for internal cleaning time to time. | No | https://drive.google.com/open?id=1AXRZHcczh2KZ57uF5DepQ6z5pco7rQfb | https://drive.google.com/open?id=1Aq_nqS6BcHw1sQwtXq5W9ycRt4kmq0db |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN015/25 | 2025-06-02 15:32 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | CRLU3604920 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 22:12 | 2025-06-02 |  |  |  |  | CRLU3604920 |  |  |  | Daikin | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/190 psig | 9.9/9.8/9.8 | 414/415/414 | Short | PM service complited | Unit working as satisfactory, Recomnded internal need to clean time to time | No | https://drive.google.com/open?id=1gUhKczeO5IZnVNxp9AWA2dvdggpjx-Xp | https://drive.google.com/open?id=1iBx65KSClAvTML_672qFnrmwQhfduzzM |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN016/25 | 2025-06-02 15:35 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | MYRU4518042 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Shahbuddin | [54 empty] | 2025-06-02 21:38 | 2025-06-01 |  |  |  |  | MYRU4518042 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | ,4/185 psig | 9.8/9.9/9.8 | 407/408/407 | Short | PM complited attached job order& recomnded for internal house keeping to improve and need cleaning time to time | Unit working as satisfactory | Yes | https://drive.google.com/open?id=1E64jZPDnUdFwTeWCN9pvKVJKNl7sxFkr | https://drive.google.com/open?id=1t3I20R0W6qe_LC52m99wNaobd6CGy3aP |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN017/25 | 2025-06-02 17:00 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | TITU9930032 | Unit Installation | Puhpa Mam | Madhusoodhana.k@sailife.com | Bidar | Installation |  | Email | Shahbuddin | [54 empty] | 2025-06-04 10:36 | 2025-06-03 |  |  |  |  | TITU9930032 |  |  |  | Carrier | 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 5/190 psig | 12.5/12.4/12.5 | 416/417/416 | Short | Removed Defective Thermoking unit & Complit reefer unit Instalation done . | After reefer unit Instalation complited run carrier unit & observation & handed over to clints duty person | No | https://drive.google.com/open?id=1_PIVBtbYTDYIni2_U2veDzBkDvoygnaU | https://drive.google.com/open?id=14JwDthcF8XPdiJMfwFfb7iBHl_Xyz4zl |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN018/25 | 2025-06-02 17:34 | crm@crystalgroup.in | Lucknow International Airport | Vivek Chauhan | 9161113399 | NA | TRIU6618581 |  |  | vivek.Chauhan@adani.com | Lucknow | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-06 13:07 | 2025-06-02 |  |  |  |  | TRIU6618581 |  |  |  | Carrier | -3'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S --- d-17.9bar | R17.7. Y18.1. B17.6 | L1-391v. L2-395. L3-393 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1fW4sv2siimmFj-YyJ5clUwHfEOJgbkBI | https://drive.google.com/open?id=1QW-hGpJtXpYt76aXYn1jDSltVmRbLD3p |  | Trip095 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN019/25 | 2025-06-03 14:42 | crm@crystalgroup.in | LAURUS UNIT -1 | Ramakrishna | 8916601403 | NA | CXRU1037308 |  |  | ramakrishna.chvvs@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Email | Ramiz | [54 empty] | 2025-06-05 16:19 | 2025-06-01 |  |  |  |  | CXRU1037308 |  |  |  | Carrier | +1.5'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/13.1b | 9.1 | 407 | Not done | Found Condenser coil very dirty | Checked allparameters are good. | No | https://drive.google.com/open?id=14a-nPt2aFuEfiaUEBAZl9NMOJ1GZmrHw | https://drive.google.com/open?id=14wPsVCSpz1-_ddLCFMLlkYYAftGH3rDV |  | Na | Yes | Yes | Can be done on next PM | Need to clean condenser coil | Na | technician@crystalgroup.in | REEFER
JUN020/25 | 2025-06-03 14:44 | crm@crystalgroup.in | LAURUS UNIT -1 | Ramakrishna | 8916601403 | NA | PCIU6006639 |  |  | ramakrishna.chvvs@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 16:24 | 2025-06-01 |  |  |  |  | PCIU6006639 |  |  |  | Daikin | + | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1/13.2b | 9.1 | 407 | Not done | Found Condenser coil very dirty | Checked all parameters are good. | No | https://drive.google.com/open?id=1Pcc3Uoaok0pJnUexEUcLOMcvnljRbFNn | https://drive.google.com/open?id=1naLafFHN9AdAWqkzQ8Yyg7i_h3Pn6k8S |  | Na | Yes | Yes | Can be done on next PM | Need to clean Condenser coil | Na | technician@crystalgroup.in | REEFER
JUN021/25 | 2025-06-04 11:44 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | MYRU4519115 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 15:46 | 2025-06-03 |  |  |  |  | MYRU4519115 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4/105b | 9.4 | 407 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked allparameters are good. | No | https://drive.google.com/open?id=1zHGIQ1il5Dmnxf0vjAEBK2l2JCZauq1z | https://drive.google.com/open?id=1l1_bu0LN-9he-Ens7zKsbGc8MZG11O_Q |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN022/25 | 2025-06-04 11:55 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | TDRU7153256 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 15:53 | 2025-06-03 |  |  |  |  | TDRU7153256 |  |  |  | Daikin | +22'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/118b | 9.1 | 407 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked all parameters are good. | No | https://drive.google.com/open?id=1bmGodV3v3FWf61gDRQcbcKI3gvjXIbs- | https://drive.google.com/open?id=1Yh9JyWE6CFW-vND4YITjJBSdVCWq_lZQ |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN023/25 | 2025-06-04 12:06 | crm@crystalgroup.in | Laurus Unit 3 | Mr. Ajay | 9985369677 | NA | KKFU6711724 |  |  | na | Vishakapatnam | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-05 15:59 | 2025-06-03 |  |  |  |  | KKFU6711724 |  |  |  | Carrier | +20'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3/ 12.1b | 407 | 12.1 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water.Checked all parameters are good. | No | https://drive.google.com/open?id=1058vW8AiyyYnWtxDk6sYC0EZTfa1u2JS | https://drive.google.com/open?id=1gftpwen2Gvn4kzIe6bWUpmcZpUjg2Wc_ |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN024/25 | 2025-06-04 17:43 | crm@crystalgroup.in | Qwik Supply | Mangesh Vannere | 7020374749 | IFMS Team | PCIU6015055 | DOOR NOT CLOSING | Lina | Mangesh.Vannere@ril.com | Pune | Running with issues | Facing door damage issue | Email | Lina | 2025-06-07 16:37 | crm@crystalgroup.in | Qwik Supply | PCIU6015055 | 40 FEET | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DOOR STRUCTURE DAMAGE | ARRANGING A STRUCTURE PERSON | NA | No | DOOR DAMAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN024%2F25 | DAIKIN | DAIKIN LXE10E | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | DOOR NOT CLOSING | 2025-09-30 17:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-30 17:05 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-30 17:05 | crm@crystalgroup.in | NO
JUN025/25 | 2025-06-05 15:22 | crm@crystalgroup.in | BEJAPURI DAIRY | LAKHWINDER SINGH | 99876772453 | MAINTAINENCE MANAGER | MYRU4503459 |  |  | lakhwindersingh@countrydelight.in | Patanchuru | Preventive Maintenance |  | Call | Shahbuddin Sir | [54 empty] | 2025-06-09 19:41 | 2025-06-04 |  |  |  |  | MYRU4503459 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/185psig | 10.1/10.2/10 1 | 410/411/410 | Short | PM servicecompleted | Run unit observation operation& working as satisfactory | No | https://drive.google.com/open?id=17yNbKvgg431LlJLIZlLwtbwTnbDt37JI | https://drive.google.com/open?id=17va_p4lfKICSGP7jfC31sJoKa6vDnGdA |  | 94 | No | No | Can be done on next PM | N@ | NA | technician@crystalgroup.in | REEFER
JUN026/25 | 2025-06-05 17:20 | crm@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | SJKU4000104 |  |  | dharmender.tiwari@dsv.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-09 19:58 | 2025-06-04 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | +2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 10.1/10.2/10.1 | 409/410/409 | Short | PM service & General Instalation after repair by vandor | Unit working as satisfactory | No | https://drive.google.com/open?id=1qCuFY3lVfLVJpwIUuZpqAumY9Vwh4KI2 | https://drive.google.com/open?id=1eZsYnkEoTd68pfkoZkRWH8GkYa7J8tTb |  | 94 | No | No | Can be done on next PM | NA | a | technician@crystalgroup.in | REEFER
JUN027/25 | 2025-06-05 17:21 | crm@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | TITU9930096 |  |  | dharmender.tiwari@dsv.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-09 20:06 | 2025-06-04 |  |  |  |  | TITU9930096 |  |  |  | Thermo king | +2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 06/19br | 10.2/10 3/10.2 | 410/411/410 | Short | PM service &General Inspection after repaired by vandor | Found unit Working as satisfactory | No | https://drive.google.com/open?id=1kyY1Lr1FcuPzPKZKwbhd7tTXAt7FpmlQ | https://drive.google.com/open?id=1P4o7s1r8FsME5FNDuRoYfxz1VxVFUXKl |  | 94 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN028/25 | 2025-06-06 13:00 | crm@crystalgroup.in | NSR TRADER | KAMESH | 99039 99266 | NA | TCLU1112683 | Compressor Contactor Issue | Pushpa Mam | NA | Vishakapatnam | Running with issues | Capacitor Burned, Compressor Contactor | Call | Shabuddin | 2025-06-07 16:43 | crm@crystalgroup.in | NSR TRADER | TCLU1112683 | 40 FEET | THERMOKING | SERVICE-AT SITE | LEASE | FOC | COMPRESSOR CONTACTOR BURNED | TEMPERARLY RUN WITH ONE CONTACTOR BYPASS | TK MP 3000 COMPRESSOR CONTACTOR | Yes | COMPRESSOR CONTACTOR BURNED, FOR TIME BEING RUNNING WITH ONE CONTACTOR BYPASS | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN028%2F25 | THERMOKING | TK-MP3000 | NA | NA | NA | USED | NA | RAMIZ | Yes | Compressor Contactor Issue | 2025-07-28 18:48 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-28 19:37 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-28 19:38 | crm@crystalgroup.in | NO
JUN029/25 | 2025-06-06 13:21 | crm@crystalgroup.in | Cipla | Vikas | 8669917201 | NA | CXRU1033787 | SERVICING, REPAIRS & REPLACEMENT | Pushpa Mam | NA | Goa | Running with issues | Water Leakage | Call | Pushpa Mam | 2025-06-07 16:47 | crm@crystalgroup.in | Cipla | CXRU1033787 | 40FT STD RF - Dual Machine Daikin with Anti Room + Heater | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | ARRANGING THIRD PARTY VENDOR OR TECHNICIAN |  | No | SUSPECTED TOP ROOF LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN029%2F25 | DAIKIN | DAIKIN LXE10E | M001107 | K31412141829 | DECOS 3F 2557 / 1 | used | NA | SHAHBUDDIN | Yes | SERVICING, REPAIRS & REPLACEMENT | 2025-06-16 10:35 | operation@crystalgroup.in | NO | [9 empty] | 2025-06-16 10:37 | operation@crystalgroup.in | NO |  |  |  |  | 2025-06-16 17:28 | crm@crystalgroup.in | NO | [7 empty] | 2025-06-13 22:18 | 2025-06-13 |  |  |  |  | CXRU1033787 |  |  |  | Daikin | +30c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/185 PSIG | 9.9/9.8/9.9 | 411/410/411 | Short | Water leaking from top roof..Rusty | First suggest to top roof shade required for permanent soulation. And at present container top roof covering with Tarpullin ..and stop leakage. Water entering from ventilation cover.& that close with fill sealicon sealant. And perform short PTI & PASS WITH NO AL. | No | https://drive.google.com/open?id=1s3GkllXR6rz_tSixHCvUsnT7ko7i-9Gr | https://drive.google.com/open?id=16La5Y6QGftHnfQcMrM0mfh_yOpOXCJIb |  | NA | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN030/25 | 2025-06-06 13:36 | crm@crystalgroup.in | Cipla | Vikas | 8669917201 | NA | CXRU1033344 | SERVICING, REPAIRS & REPLACEMENT | Pushpa Mam | NA | Goa | Running with issues | Water Leakage | Call | Pushpa Mam | 2025-06-07 16:49 | crm@crystalgroup.in | Cipla | CXRU1033344 | 40FT STD RF - Dual Machine Daikin with Anti Room | DAIKIN | SERVICE-AT SITE | LEASE | FOC | WATER LEAKAGE | ARRANGING VENDOR OR TECHNICIAN O SITE |  | No | WATER LEAKAGE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN030%2F25 | DAIKIN | DAIKIN LXE10E | M001118 | K31411114078 | DECOS 3F 2609 / 1 | Used | NA | SHAHBUDDIN | Yes | SERVICING, REPAIRS & REPLACEMENT | 2025-06-16 10:36 | operation@crystalgroup.in | NO | [9 empty] | 2025-06-16 10:36 | operation@crystalgroup.in | NO |  |  |  |  | 2025-06-16 17:29 | crm@crystalgroup.in | NO | [7 empty] | 2025-06-17 17:40 | 2025-06-14 |  |  |  |  | CXRU1033344 |  |  |  | Daikin | +22 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/180psig | 9.9/9.9/9.8 | 410/411/410 | Short | Unit working as satisfactory & temperley on top roof fixed Tarpollin . For permanent need shade . | Checked unit operation and completeed pm service | No | https://drive.google.com/open?id=1LVTIWli8NwZlqHnLMHww0WwYj8FcEi3j | https://drive.google.com/open?id=1l225d-uGzCimq_Ut7szhMgfbC7CzMtCb |  | 099 Goa | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN031/25 | 2025-06-06 13:39 | crm@crystalgroup.in | Crystal | Khirod | 82609 72816 | NA | BMOU9788370 | FABRICATION, REPAIRS & REPLACEMENT | Pushpa Mam | NA | JNPT | Running with issues | Machine Installation | Call | Pushpa Mam | 2025-06-16 16:56 | operation@crystalgroup.in | Crystal Yard | BMOU9788370 | 40FT STD RF | Daikin | REPAIR | STOCK | FOC | Machine Installation | NA |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN031%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No | FABRICATION, REPAIRS & REPLACEMENT | 2025-06-11 15:04 | operation@crystalgroup.in | YES | IN053 | 2025-06-06 | FOC | CRYSTAL YARD | JNPT | BMOU9788370 | DEPOT | FOC | DAIKIN | 2025-06-11 15:06 | operation@crystalgroup.in | YES | IN053 | YES | https://drive.google.com/open?id=1OtlsA9PsXmFOpF_lhYAIUKRl3ECEQL8- | Vendor | 2025-06-12 17:06 | qualitycontrol@crystalgroup.in | NO | [7 empty] | 2025-06-16 17:42 | 2025-06-11 |  |  |  |  | BMOU9788370 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.6 TO 19 b | 9.8 AMP/9.7AMP/9.8 AMP | 12 AMP/11 AMP/ 12 AMP | Full | Unit 1& 2 working ok, All spare clean & ok, Run tested ok | PTI Done | No | https://drive.google.com/open?id=1Z-7faBZ7fTKC3AD9ElzHGP8ShV8yjke2 | https://drive.google.com/open?id=1R-IWxrFXaIwMwuYTf1TZIqOXUTKJ4je3 |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUN032/25 | 2025-06-06 16:44 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | Mukul Mukharjee | 9831737646 | Client Head | CXRU1036019 | SERVICING, REPAIRS & REPLACEMENT | Pushpa Mam | mukul.in77@gmail.com | Dhulagarh, Kolkata | Complete Breakdown | Container Breakdown | Call | Pushpa Mam | 2025-06-07 16:53 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | CXRU1036019 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | BREAKDOWN - ALARM E1O1 | ARRANGING TECHNICIAN |  | No | ALARM E1O1 HIGH PRESSURE TRIPPING OFF | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN032%2F25 | DAIKIN | DAIKIN LXE10E | M001044 | K31511115441 | DECOS 3F 2513 / 1 | used | NA | RAMIZ | Yes | SERVICING, REPAIRS & REPLACEMENT | 2025-06-12 16:53 | crm@crystalgroup.in | NO | [9 empty] | 2025-06-12 16:53 | crm@crystalgroup.in | NO |  |  |  |  | 2025-06-12 16:54 | crm@crystalgroup.in | NO | [7 empty] | 2025-06-10 22:15 | 2025-06-10 |  |  |  |  | CXRU1036019 |  |  |  | Daikin | +6'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7/10.1 | 10.5/10.3/10.1 | 402/402/401 | Not done | Found fues blown due to phese contactor stack | Replaced Fuse with spare one.Fix the contactor.After working the Reefer unit running good . Still under observation | Yes | https://drive.google.com/open?id=1GuvP29lARbGE5dxdaboeG0Wm_ESn84GA | https://drive.google.com/open?id=1Pabk5aquOsC26ZfFJ56GDWqLeFhTbxPS |  | Na | Yes | Yes | Can be done on next PM | Fues | Fues 10 amps | technician@crystalgroup.in | REEFER
JUN033/25 | 2025-06-06 16:58 | crm@crystalgroup.in | Crystal | NA | NA | NA | CICU1442256 | REPAIRS & REPLACEMENT |  | NA | JNPT | Repair |  | Call | Khirod | 2025-06-09 13:08 | crm@crystalgroup.in | Crystal Yard | CICU1442256 | 40' Blast | NA | REPAIR | STOCK | NA | Internal Panel Delaminatd to Laminted Patch with foamQty 04 Nos | Internal Panel Delaminatd to Laminted Patch with foamQty 04 Nos |  | No | Foaming Work fo Internal Panel | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN033%2F25 | Thermoking | TK-MP4000 | EOG5003933 | 220916, 3.29.00 | NA | brand New | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-06-09 13:20 | crm@crystalgroup.in | YES | IN054 | 2025-06-06 | FOC | CRYSTAL YARD | JNPT | CICU1442256 | DEPOT | FOC | TK-MP4000 | 2025-08-08 12:10 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 12:10 | crm@crystalgroup.in | NO
JUN034/25 | 2025-06-06 17:00 | crm@crystalgroup.in | Crystal | NA | NA | NA | MWCU5709930 | SERVICING, REPAIRS & REPLACEMENT |  | NA | JNPT | Running with issues |  | Call | Khirod | 2025-06-09 13:11 | crm@crystalgroup.in | Crystal Yard | MWCU5709930 | 20FT STD RF | Carrier | REPAIR | STOCK | NA | External Panel Welding | WELDING WORK |  | No | EXTERNAL PANEL CUT AND WELD TO THE PATCH | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN034%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | SERVICING, REPAIRS & REPLACEMENT | 2025-06-09 13:22 | crm@crystalgroup.in | YES | IN055 | 2025-06-06 | FOC | CRYSTAL YARD | JNPT | MWCU5709930 | DEPOT | FOC | CARRIER-THINLINE | 2025-08-08 12:17 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 12:18 | crm@crystalgroup.in | NO
JUN035/25 | 2025-06-07 16:59 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | Atul Tyagi | 9717318538 | NA | GRMU3607418 |  |  | NA | Noida | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-09 22:47 | 2025-06-07 |  |  |  |  | GRMU3607418 |  |  |  | Daikin | -25.c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S- -21psi. D-1438psi | R-9.8. B-9.6. Y-9.9 | L2-410. L2-411. L3-410 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running good condition | No | https://drive.google.com/open?id=1naB-sG9P0djXFFtrIdi6D5jaNEVmI2_m | https://drive.google.com/open?id=1V6SWX-D_L9kJZcVcpk1K_lXzQkRsmAVC |  | Trip095 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN036/25 | 2025-06-07 17:01 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | Atul Tyagi | 9717318538 | NA | TRIU6687350 |  |  | NA | Noida | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-08 08:10 | 2025-06-07 |  |  |  |  | TRIU6687350 |  |  |  | Carrier | -25'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S- 0.9 bar. D-14.6bar | R-9.9. B-10.0. Y-9.7. | L1-400. L2-399. L3 - 402 | Not done | We have attende tha unit found condenser coil havy durty and kick plate havy iecing | We have work condenser coil wash with normal water and ice clean after unit running good condition | Yes | https://drive.google.com/open?id=1MyvWAe0TCXE3ApYnMnPPXKqYEenWrN5d | https://drive.google.com/open?id=16zRa89xzO63OI5dvjqUq7WcJlUoR1yFe |  | Trip095 | No | No | Can be done on next PM | No | Supply air sensor 2 nose | rajreefertech@gmail.com | REEFER
JUN037/25 | 2025-06-09 17:27 | crm@crystalgroup.in | lands flavour | Ananth Prabhu | 8105012718 | NA | CXRU1043337 | DISPLAY NOT VISIBLE, Excessive sweating in ODU | Lina | landsflavour.services@gmail.com | Mangalore | Running with issues | Return sensor error E404 Excessive sweating in ODU | Email | Pushpa Mam | 2025-06-13 12:31 | technician@crystalgroup.in | Land Flavor Gonda Factory | CXRU1043337 | 40" | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Temp. Not received at set point. | Suggest to replaced Reefer unit bu verendra | NA | No | Compressor faulty | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN037%2F25 | Carr | CARRIER-THINLINE | NA | NA | NA | Used | NA | VIRENDRA | Yes | DISPLAY NOT VISIBLE, Excessive sweating in ODU | 2025-07-04 12:32 | operation@crystalgroup.in | YES | IN091 | 2025-07-04 | Spares | Lands Flavour / Bonda Factory | Mangalore | CXRU1043337 | SITE | FOC | DAIKIN | 2025-09-30 17:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-30 17:36 | crm@crystalgroup.in | YES | IN204 | TECHNICIAN |  |  | Sitaram |  |  | 2025-09-04 09:16 | 2025-09-03 |  |  |  |  | CXRU1043337 |  |  |  | Daikin | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On ca | On call | Not done | On call guide | Unit not working due to return sensor out of calibration, guide to factory technician to install return sensor, he replaced under my supervision and done, unit working fine | No | https://drive.google.com/open?id=1XQhzqIzoBq3yko3hq45Itu5WtmpiyRhN | https://drive.google.com/open?id=17Icb27gyzZqTVQ_9VJ3CrmpIleFYKGst |  | 117 | No | No | Can be done on next PM | Na | Nan | technician@crystalgroup.in | REEFER
JUN038/25 | 2025-06-11 15:33 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | SJKU4000022 |  |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-19 06:07 | 2025-06-11 |  |  |  |  | SJKU4000022 |  |  |  | Carrier | +2'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | S-2.3bar. D13.7bar | 10.9/10.7/10.8 | 392/389/390 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1-RXvgHgJJe4KJb70QeAM-j1cdWR8Y38Q | https://drive.google.com/open?id=1Qut_wboEZDMWFn4BSGjC60QeBZs23TSs |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN039/25 | 2025-06-11 15:36 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | CICU8118130 |  |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-19 08:34 | 2025-06-11 |  |  |  |  | CICU8118130 |  |  |  | Thermo king | +2'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | ----/22.3bar | 12.2/12/11.9 | 390/389/391 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1S2MOD8NzY_VJh5W0TeNWJV_UhVol8ugP | https://drive.google.com/open?id=1hHFDXBmZrCIPFC30101niMfdT1dqlyyM |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN040/25 | 2025-06-11 15:37 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | CICU3876631 |  |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-19 08:25 | 2025-06-10 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | ---/21.6bar | 11.8/12.4/11.7 | 401/400/401 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=15oxN9ONtVX-4HVNi3nuJT2m9abLFV991 | https://drive.google.com/open?id=1JQ6qLYWmg3obPySNjgEMpuoy284SbDWD |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN041/25 | 2025-06-11 15:40 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | CXRU1045453 |  |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-19 07:58 | 2025-06-11 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -20'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 47/1719 | 10.4/10.3/10.4 | 391/393/392 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1k7w2Hw2rDvYe4kglpQou-Tapw62lPqYh | https://drive.google.com/open?id=1Awj6dnXgFPwlFz7wRGOkzr_MWTmOcBdS |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN042/25 | 2025-06-11 15:42 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | TCLU1130265 |  |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Preventive Maintenance |  | Call | Rajkumar | [54 empty] | 2025-06-19 08:06 | 2025-06-11 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | -20'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | ----/26.3bar | 14.5/14.2/14.0 | 391/391/391 | Not done | We have attende tha unit found condenser coil havy durty | We have work condenser coil wash with normal water after unit running sound condition | No | https://drive.google.com/open?id=1pNgCkdFq9s5ECm1EHAf2Z4zTxut_SCUl | https://drive.google.com/open?id=1OBRH6A40qvUbghWPsx8YLLWqjMc-YbSB |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN043/25 | 2025-06-11 16:22 | crm@crystalgroup.in | Crystal | Sachin Jayswar | 919136599610 | NA | MYRU4509035 |  |  | qualitycontrol@crystalgroup.in | JNPT | Preventive Maintenance |  | Call | Ajay Thakur | 2025-06-26 14:27 | operation@crystalgroup.in | Crystal Yard | MYRU4509035 | 40FT STD RF | NA | PREVENTIVE MAINTENANCE | STOCK | FOC | PTI Test | PTI | NA | No | PTI to be carried out | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN043%2F25 | Daikin | DAIKIN | 802602 | LXE10E136A | NA | Used | NA | Thakur | Yes |  | 2025-06-26 14:30 | operation@crystalgroup.in | NO | [9 empty] | 2025-06-26 14:33 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-04 12:13 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-04 12:25 | 2025-05-31 |  |  |  |  | MYRU4509035 |  |  |  | Daikin | -18C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5BAR 1.8BAR | NA | NA | Full | FULL PTI OK | PTI DONE | No | https://drive.google.com/open?id=19WtX0PVmWqcEz0o8U1_M7W8DLolUELYc | https://drive.google.com/open?id=1DKgVC0MGZExgPRzyFav-VOK0xrHdvLQe |  | NA | No | No | Can be done on next PM | NA | NA | operation@crystalgroup.in | REEFER
JUN044/25 | 2025-06-11 17:01 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal | 9836800040 | commercial head | CXRU1033370 |  |  | agarwal.dilip1@gmail.com | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-12 08:52 | 2025-06-11 |  |  |  |  | CXRU1033370 |  |  |  | Daikin | -15'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4/141 | 9.5 | 404 | Not done | Found Condenser coil very dirty & al e407 | Clean condenser coil with fresh water & EIS sensor need to replace | Yes | https://drive.google.com/open?id=1HejUeNdeqFguje0LuFxNy-OR_m4AbNKt | https://drive.google.com/open?id=1eDFwXcqaIR9oceKCezbLk7QvdQu2siQt |  | Na | Yes | Yes | Urgent | Sensor fix | EIS sensor | technician@crystalgroup.in | REEFER
JUN045/25 | 2025-06-11 17:02 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal | 9836800040 | Commercial Head | GRMU3707525 |  |  | agarwal.dilip1@gmail.com | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-12 09:17 | 2025-06-11 |  |  |  |  | GRMU3707525 |  |  |  | Daikin | -18 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/10.3b | 9.8 | 304 | Not done | Found unit 1 condenser coil dirty, Unit 3 AL 407 Unit 2 Need AL ,407 Key pad defective | Clean condenser coil with fresh water & for checkin unit need empty | Yes | https://drive.google.com/open?id=1Sdt7hD9JCDfQ5vTKoxpHKYpvakMj1Dam | https://drive.google.com/open?id=1Zupg26R4R2cBwVN8w-5aqSRDGjW8oztC |  | Na | Yes | Yes | Urgent | EIS sensor -2 Eis sponsor -2 Key pad -1 Expansion coil -1 Expansion valve -1 | EIS sensor -2 Eis sponsor -2 Key pad -1 Expansion coil -1 Expansion valve -1 | technician@crystalgroup.in | REEFER
JUN046/25 | 2025-06-11 17:04 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal | 9836800040 | Commercial Head | MYRU4515260 |  |  | agarwal.dilip1@gmail.com | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-12 08:34 | 2025-06-11 |  |  |  |  | MYRU4515260 |  |  |  | Daikin | -18'C | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.6/14.1b | 10.5/10.4/10.5 | 404/ | Not done | Found both EVP Motor noise & Display defective & key pad defective. | Need to replace display & Key pad & for Moto r need to replace due to have noise | Yes | https://drive.google.com/open?id=1YwGUhfH8cpsXjU4iIppWcvF1OIomtwwr | https://drive.google.com/open?id=1YDN5aIT71XVlfdefQgmHRO9c_JKBrQ8t |  | Na | Yes | Yes | Urgent | Need to fix display, key pad, motor | Display -1 Key pad -1 EVP motor -2 | technician@crystalgroup.in | REEFER
JUN047/25 | 2025-06-11 17:05 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal |  | Commercial Head | MYRU4516306 |  |  | agarwal.dilip1@gmail.com | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-12 08:43 | 2025-06-11 |  |  |  |  | MYRU4516306 |  |  |  | Daikin | -15'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5/11.4b | 9.8/ | 404 | Not done | Found Condenser coil very dirty | Clean condenser coil with fresh water & Check all parameters are good | No | https://drive.google.com/open?id=18pcWJqlHC1MzKIPDV26iZV3YoyKvDqk0 | https://drive.google.com/open?id=1N98-gDZSOPtD709h1KOVIv1arjMHk8RJ |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN048/25 | 2025-06-11 17:31 | crm@crystalgroup.in | Devyani Food Industries Ltd | Ravi Kumar Singh | 9088047482 | NA | KKFU6712675 |  |  | ravikumar.singh@creambell.com | Burdhman | Preventive Maintenance |  | Email | Tushar More | [54 empty] | 2025-06-20 10:16 | 2025-06-19 |  |  |  |  | KKFU6712675 |  |  |  | Carrier | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Na | Na | 407 | Not done | Found leaked from compressor bady & liquid charging value | Try to fix but not done need Valve plate gasket gasket | Yes | https://drive.google.com/open?id=1Mo4PgGmHNG0cPLMt40DPBbLTsABdVTJt | https://drive.google.com/open?id=1W5_YtdqR-97mkMAKN1is5B6jdzS0dJHu |  | 100 | Yes | Yes | Urgent | All pending | Gasket 4 nos, liquid charging value | technician@crystalgroup.in | REEFER
JUN049/25 | 2025-06-12 14:50 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal | 9836800040 | Commercial Head | MYRU4516306 | REPAIRS & REPLACEMENT | Ramiz | agarwal.dilip1@gmail.com | Kolkata | Running with issues | As per the job order JUN047/25 - EVP Inlet & Outlet Sensor requirred - Qty 01 No Each | Call | Ramiz | 2025-06-12 16:23 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | MYRU4515260 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | Sensor are not working | EVP INLET SENSOR & EVP OUTLET SENSOR | EVP INLET SENSOR & EVP OUTLET SENSOR QTY 1 EACH | Yes | PM Service complete & sensor Required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN049%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | NA | RAMIZ | Yes | REPAIRS & REPLACEMENT | 2025-06-16 10:01 | operation@crystalgroup.in | YES | IN065 | 2025-06-13 | Spares | Mochan Food Processors Pvt Ltd | Kolkata | MYRU4516306 | SITE | PAID | DAIKIN | 2025-06-16 17:55 | operation@crystalgroup.in | YES | IN065 | YES | https://drive.google.com/open?id=1qlp_DsNVz8YXjyvGQHcT1J9KKcq_I_IA | Vendor | 2025-06-19 17:24 | qualitycontrol@crystalgroup.in | YES | JUN049/25 | COURIER | 51620475815 | blue dart |  | https://drive.google.com/open?id=1W-T1EFQ0bRnVLF0U0vq-z_BXYT-IwM5S |  | 2025-07-25 17:36 | 2025-06-18 |  |  |  |  | MYRU4516306 |  |  |  | Thermo king | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | - | - | - | Short | NA | NA | No | https://drive.google.com/open?id=1qdFqX57-Ei7vX7p5LUvNExGzpeNLXcPX | https://drive.google.com/open?id=1VaN8cZObyM1FbI0-iIqkDLbpIfsDV9Cl |  | NA | No | No | Can be done on next PM | CONTAINER TO BE OFFLEASED- CLOSED AS PER DISCUSSION WITH PUSHPA MAM | NA | crm@crystalgroup.in | REEFER
JUN050/25 | 2025-06-12 15:25 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agawal | 9836800040 | Commercial Head | MYRU4515260 | REPAIRS & REPLACEMENT | Ramiz | agarwal.dilip1@gmail.com | Kolkata | Running with issues | As per the last job order JUN046/25 - require spares of Keypad, Display qty 1 each & EVP motor - Qty 2 Nos | Call | Ramiz | 2025-06-12 16:37 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | MYRU4515260 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | PM Service Complete & Some spares required | Spares Required | KEYPAD 1 NO Display 1 NO EVP Motor 2 Nos | Yes | PM Service done | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN050%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | NA | RAMIZ | Yes | REPAIRS & REPLACEMENT | 2025-06-16 10:00 | operation@crystalgroup.in | YES | IN066 | 2025-06-14 | Spares | Mochan Food Processors Pvt Ltd | Kolkata | MYRU4515260 | SITE | FOC | DAIKIN | 2025-06-16 17:56 | operation@crystalgroup.in | YES | IN066 | YES |  | Stock | 2025-06-19 17:28 | qualitycontrol@crystalgroup.in | YES | JUN050/25 | COURIER | 51620475815 | blue dart |  | https://drive.google.com/open?id=18lYbPQ3G16dt5WiT5HEj3IhgOlzFdoqo |  | 2025-06-25 22:00 | 2025-06-25 |  |  |  |  | MYRU4515260 |  |  |  | Daikin | -18'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/13.2b | 10.1 | 395 | Not done | Found PT& CT board defective/alFE07. & Ab normal cooling due to this | Replace Pt& CT board with good one, Replace keypad with new one, replace display with New one, The unit under observation | No | https://drive.google.com/open?id=1wLLxE38M1VS2CMp4Qb9rEhgOtZQlScyc | https://drive.google.com/open?id=1qWIbv8ZZY6pvx04zmy4_z48er97LbkUf |  | 100 | Yes | No | Can be done on next PM | PT CT board for GRMU3707525 container unit's 2 | Replace PT& CT BOARD from Container no GRMU3707525 unit 2 | technician@crystalgroup.in | REEFER
JUN051/25 | 2025-06-12 15:29 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | Dilip Agarwal | 9836800040 | Commercial Head | GRMU3707525 | REPAIRS & REPLACEMENT | Ramiz Sir | agarwal.dilip1@gmail.com | Kolkata | Running with issues | As per the job order JUN045/25 - spares required - KEYPAD 1 EIS SENSOR 2 FOS SENSOR 2 EXPANSION COIL 1 EXPANSION VALVE 1 FILTER DRIER 1 Brizing Set inclu Nitrogen & Vaccum 1 | Call | Ramiz | 2025-06-12 16:34 | crm@crystalgroup.in | Mochan Food Processors Pvt Ltd | GRMU3707525 | 20FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | PM Service done & spares required | Spares required | KEYPAD 1 EIS SENSOR 2 FOS SENSOR 2 EXPANSION COIL 1 EXPANSION VALVE 1 FILTER DRIER 1 Brizing Set inclu Nitrogen & Vaccum 1 | Yes | PM Service Completed & spares required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN051%2F25 | Daikin | DAIKIN | NA | NA | NA | used | NA | RAMIZ | Yes | REPAIRS & REPLACEMENT | 2025-06-16 10:03 | operation@crystalgroup.in | YES | IN064 | 2025-06-13 | Spares | Mochan Food Processors Pvt Ltd | Kolkata | GRMU3707525 | SITE | PAID | DAIKIN | 2025-06-16 18:03 | operation@crystalgroup.in | YES | IN064 | YES | https://drive.google.com/open?id=1xYUyCyrKcS3GzWcn_9dP9WG1GKpGuFe0, https://drive.google.com/open?id=1Dyrx-eK99qtN9nq3LmMDLO09y4AgxUKw | Vendor | 2025-06-19 17:27 | qualitycontrol@crystalgroup.in | YES | JUN051/25 | COURIER | 51620475815 | blue dart |  | https://drive.google.com/open?id=13UfsChDWbqxESWCha99BnQJ8G5DqYFrE |  | 2025-06-25 22:39 | 2025-06-25 |  |  |  |  | GRMU3707525 |  |  |  | Daikin | -18'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/13.8 | 10.1 | 395 | Not done | Replaced key pad with new one, replace ios & EOS with new , Replace filter drier with i | The unit under observation | No | https://drive.google.com/open?id=1235jrN3V_OU7twa3Px8XWJTEG70YZuNT | https://drive.google.com/open?id=1nP2iYk2kVeMBKjssJzeUr809xgca9ZtP |  | 100 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN052/25 | 2025-06-12 17:45 | crm@crystalgroup.in | Lupin Limited | "Prasanna Kumar | 9676999956 | Manager | CCLU1036859 |  |  | prasannakota@lupin.com | Bhiwandi | Preventive Maintenance |  | Call | Shabuddin Sir | [54 empty] | 2025-06-13 12:13 | 2025-06-11 |  |  |  |  | CCLU1036859 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/10br | 12.4/12.5/12.4 | 389/390389 | Short | PM due | PM servicev complit and unit working as satisfactory | No | https://drive.google.com/open?id=1Rb_UnwW8-9XeM4fLyuE5VYUbOUXA5uOq | https://drive.google.com/open?id=1j9eNjFlbVDAO7QsYE6tWdJu3m3S7SKqM |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN053/25 | 2025-06-12 17:47 | crm@crystalgroup.in | Lupin Limited | Prasanna Kumar | 9676999956 | Manager | TRIU6681882 |  |  | prasannakota@lupin.com | Bhiwandi | Preventive Maintenance |  | Call | Shabuddin Sir | [54 empty] | 2025-06-13 12:18 | 2025-06-11 |  |  |  |  | TRIU6681882 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/14br | 12.4/12.5/12.4 | 388/389/389 | Short | PM service Due | PM service completed & found unit working fine. | No | https://drive.google.com/open?id=1r7heFD585U6ocYmZRyKy92zwohfiOgEo | https://drive.google.com/open?id=1YQpgiLAfcTecg7AvFQNBm3867O_kBCwZ |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN054/25 | 2025-06-13 16:22 | crm@crystalgroup.in | LAURUS UNIT -1 | Somy Readdy | 9963198979 | NA | TITU9930011 | REPAIRS & REPLACEMENT | Pushpa Mam | NA | Vishakapatnam | Running with issues | Compressor contactor burned. Need to replace. | Call | Pushpa Mam | 2025-06-13 16:57 | crm@crystalgroup.in | Lauras Lab Unit 1 | TITU9930011 | 40FT Spl RF | Thermoking TK 4000 | SERVICE-AT SITE | LEASE | FOC | Compressor Contactor Burned | Contactor burned, Transformer Not Working | Contactor 01 nos | Yes | Contactor burned, Transformer Not Working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN054%2F25 | Thermoking MP-4000 | TK-MP4000 | 14D8568HT | EOG1000566 | NA | Used | NA | RAMIZ | Yes | REPAIRS & REPLACEMENT | 2025-07-09 10:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-08 12:22 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 12:22 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-20 10:54 | 2025-07-24 |  |  |  |  | TITU9930011 |  |  |  | Thermo king | 15.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | Na | 410V 410V 410V | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=167td6MmpaGndf_XwQs0mla_F3NzNPUZ6 | https://drive.google.com/open?id=1w5sbpad6jzkdbZiRcajG0JpSvVOqDQKY |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN055/25 | 2025-06-13 16:37 | crm@crystalgroup.in | ITC Limited - Adya Dairy | Raju Bhunia | 9230676077 | NA | CXRU1033719 |  |  | NA | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-14 00:01 | 2025-06-12 |  |  |  |  | CXRU1033719 |  |  |  | Daikin | 3 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 07/13.7 | 10.1 | 407 | Not done | Found Condenser coil dirty | Clean condenser coil with fresh water & checked all parameters are good | No | https://drive.google.com/open?id=1a33nhIoqgtN_vAYAcWaFJ55YHX4TsFCt | https://drive.google.com/open?id=1NblQoGSNb6yNl2ApuyvS4Ckj91398uoE |  | 96 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN056/25 | 2025-06-13 16:39 | crm@crystalgroup.in | ITC Limited - Adya Dairy | Raju Bhunia | 9230676077 | NA | BMOU9729398 |  |  | NA | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-14 00:10 | 2025-06-12 |  |  |  |  | BMOU9729398 |  |  |  | Daikin | -18'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | Na | Na | Not done | Found Condenser coil dirty & display defective & 10 amps fues | Clean condenser coil with fresh y& | Yes | https://drive.google.com/open?id=1IgIEhnc_U9HWdlNsGhEXHeKg0w98d1Dc | https://drive.google.com/open?id=149gVVwD_DZMAbl2JKQWqhgKqtoYRBGFi |  | 96 | Yes | Yes | Urgent | Need to replace & Fues 10 amps | Display 10amp fues | technician@crystalgroup.in | REEFER
JUN057/25 | 2025-06-13 16:41 | crm@crystalgroup.in | ITC Limited - Adya Dairy | Raju Bhunia | 9230676077 | NA | KKFU6706142 |  |  | NA | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-17 18:04 | 2025-06-12 |  |  |  |  | KKFU6706142 |  |  |  | Carrier | +0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 05/13.1B | 12.5 | 407 | Not done | Found Condenser coil normal dirty | Clean condenser coil with fresh water | No | https://drive.google.com/open?id=1v6-4Py9QPv5SHmrA_ppR-QMUaR_9ugBS | https://drive.google.com/open?id=1NyxtoiK-dZYjiOF0aJWAmOtEWS8J2xO5 |  | 96 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN058/25 | 2025-06-14 17:16 | operation@crystalgroup.in | BIOCON | Manjunath Kelur | +91 90081 76576 | NA | TRIU6681542 | REPAIRS & REPLACEMENT | Pushpa Ma'am | NA | Bangalore | Running with issues | EVP Motor to be replaced | Call | Pushpa ma'am | 2025-06-14 21:20 | technician@crystalgroup.in | Biocon | TRIU6681542 | 20FT STD RF With Ante Room | Carrier | SERVICE-AT SITE | LEASE | FOC | Evp. Motor break down no.1NA | Need to replaced | Evaprator motor single phase carrier thin line | Yes | Found old model motor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN058%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-06-23 16:15 | operation@crystalgroup.in | YES | IN071 | 2025-06-17 | Spares | Biocon | Bangalore | TRIU6681542 | SITE | PAID | CARRIER-THINLINE | 2025-06-30 17:38 | operation@crystalgroup.in | YES | IN071 | NO |  | Stock | 2025-07-21 12:01 | qualitycontrol@crystalgroup.in | YES | NA | COURIER | 51601400933 | blue dart |  | https://drive.google.com/open?id=1P761dAMd2OY96BhIdgN8KyRY-jAM0yBt |  | 2025-10-16 14:52 | 23/07/0025 |  |  |  |  | TRIU6681542 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/210psig | 12.8/12.9/12.8 | 412/411/411 | Short | On video call checked by shahabuddin & found Evaprator motor no.2 not working / burnout ... Next visit motor not reached site only pm due. | Pm completed & attached job order. Next visit as per Nemichand his replaced Evaprator motor. A nd test done. | No | https://drive.google.com/open?id=16elUsqfRbm9LxJbe1KF4fkYrEmURWo-m | https://drive.google.com/open?id=1ZzZ1k-F_s0aSeN2QTQroXYYhWpTmVJlq |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN059/25 | 2025-06-14 17:21 | operation@crystalgroup.in | Tata Advanced Systems Ltd | Mr. Sachin | 7337832756 | NA | CZZU6009100 | REPAIRS & REPLACEMENT | Pushpa Ma'am | NA | Bangalore | Preventive Maintenance |  | Call | Pushpa ma'am | 2025-06-14 21:17 | technician@crystalgroup.in | Tata Advanced Systems Ltd | CZZU6009100 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | FOC | Key pad Al E 406 | Need to replaced | Daikin key pad set | Yes | Key pad Defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN059%2F25 | Daikin | DAIKIN LXE10E | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-06-23 16:08 | operation@crystalgroup.in | YES | IN077 | 2025-06-21 | Spares | Tata Advanced Systems Ltd | Bangalore | CZZU6009100 | SITE | PAID | DAIKIN | 2025-06-26 17:13 | crm@crystalgroup.in | YES | IN077 | YES |  | Stock | 2025-06-26 17:15 | crm@crystalgroup.in | YES | IN077 | TECHNICIAN |  |  | SHAHBUDDIN |  |  | 2025-07-17 13:15 | 2025-05-11 |  |  |  |  | CZZU6009100 |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/185 psig | 9.9/9.8/9.8 | 412/411/411 | Short | PM | PM Complited & need to replaced sheet key not function | Yes | https://drive.google.com/open?id=1MMI_A3aEiO2J3jE3HEByWBpac0kJbaKS | https://drive.google.com/open?id=1K7jC4NWk6YcEJ9m20weO1G6tf4jcbHIi |  | 89 | Yes | No | Can be done on next PM | need replaced sheet key | Dakin sheet key | technician@crystalgroup.in | REEFER
JUN060/25 | 2025-06-16 11:45 | crm@crystalgroup.in | Qwik Supply | Deepak Singh | 9254012557 | NA | TITU9927240 | ALARM CODE VISIBLE, Tripping off |  | Deepak91.Singh@ril.com | Sonipat, Haryana | Complete Breakdown |  | Email | Lina | 2025-06-17 17:32 | technician@crystalgroup.in | Quick supply Ril Haryana | TITU9927240 | 10"" | Thermoking mp 4000 | SERVICE-AT SITE | LEASE | FOC | Unit not working due to Power MOUDULE Defective | On the way spare | Tk mp 4000 power MOUDULE | Yes | Piwer issue fluctuations | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN060%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | RAJ KUMAR | Yes | ALARM CODE VISIBLE, Tripping off | 2025-06-18 12:01 | operation@crystalgroup.in | YES | IN070 | 2025-06-17 | Spares | Qwik Supply | Rai, Sonipat, Haryana | TITU9927240 | SITE | FOC | TK-MP4000 | 2025-06-18 12:32 | operation@crystalgroup.in | YES | IN070 | YES | https://drive.google.com/open?id=1XsXDKmtHbShwsh_0CyB_r_SVWfYUdDHg | Vendor | 2025-06-21 11:24 | qualitycontrol@crystalgroup.in | YES | JUN060/25 | COURIER | 34498853093 | Blue dart |  | https://drive.google.com/open?id=1gEh8o20AhbaLzPh1c3qB2OIcsZzs3HUj |  | 2025-06-27 16:57 | 2025-06-24 |  |  |  |  | TITU9927240 |  |  |  | Thermo king | +3.2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 3.4 - 16.3 | NA | 408/408/410 | Not done | Unit was displaying an alarm of Power Moduler Error | Replaced the Power Moduler & cleared the Alarm. After attending the unit started working fine without any alarm | No | https://drive.google.com/open?id=1kVsEH8nJFc1l4E7Mf2pFrHcMY5A5PQOt | https://drive.google.com/open?id=1flS9yKmUycdGl3vGTwy3qK2PoyNt1ade |  | NA | No | No | Can be done on next PM | na | Power Moduler installed | crm@crystalgroup.in | REEFER
JUN061/25 | 2025-06-16 12:30 | crm@crystalgroup.in | Cipla | Vikas | 8669917201 | NA | CICU2094073 |  |  | vikas.navage@cipla.com | Goa | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-16 21:49 | 2025-06-15 |  |  |  |  | CICU2094073 |  |  |  | Thermo king | 20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/18br | 9.9/9 .9/9.8 | 410/410/409 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1l-8-56eolTA7TRYZ0diho_5qt86ybt-1 | https://drive.google.com/open?id=1L6s4467dGax2DrZ-qbB7-mldFvRizcY5 |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN062/25 | 2025-06-16 12:32 | crm@crystalgroup.in | Cipla | Kiran Naik | 9822394474 | NA | TITU9230980 |  |  | Kiran.Naik@cipla.com | Goa | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-16 21:31 | 2025-06-16 |  |  |  |  | TITU9230980 |  |  |  | Daikin | +4.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 12/190psig | 9.9/10/10 | 399/400/399 | Short | PM due | PM Complited & observation unit found workinking as satisfactory | No | https://drive.google.com/open?id=19tR9yP7Qci9ugKKUAZXjnjL_4l8flXGi | https://drive.google.com/open?id=1rolgOmDB-c80YVv8y5bjCs3VSe1Z-OfL |  | NA | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN063/25 | 2025-06-16 12:34 | crm@crystalgroup.in | Cipla | Kiran Naik | 9822394474 | NA | TITU9231009 |  |  | Kiran.Naik@cipla.com | Goa | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-06-16 21:37 | 2025-06-16 |  |  |  |  | TITU9231009 |  |  |  | Daikin | +4.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/190psig | 9.9/9.8/9.9 | 399/398/399 | Short | PM due | PM Complited | Yes | https://drive.google.com/open?id=18YXivmBsWz95a9i9S8i_RxygXxsTQUO7 | https://drive.google.com/open?id=19TUPuF5KHSBdzp5Tat5IIOgg-HTf4qV2 |  | NA | No | No | Can be done on next PM | NA | Daikin Display & sheet key complit set | technician@crystalgroup.in | REEFER
JUN064/25 | 2025-06-17 16:41 | crm@crystalgroup.in | CIPLA UNIT - VI | Ajinkya | 7030921315 | NA | CRIU4024012 |  |  | Ajinkya.Murkute@cipla.com | Goa | Preventive Maintenance |  | Call | SHABUDDIN | 2025-06-17 17:19 | technician@crystalgroup.in | CIPLA UNIT - VI | CRIU4024012 | 40FT 2BAY RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | P M Due | Arrange tech. | NA | No | Due pm service | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN064%2F25 | Thermoking | TK-MP4000 | CIM1048772 | NA | NA | New | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-06-18 19:00 | 2025-06-17 |  |  |  |  | CRIU4024012 |  |  |  | Thermo king | 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/19br | 9.9/9.8/9.9 | 412/413/412 | Short | Reefer unit pm due | PM Complited with unit working as satisfactory | Yes | https://drive.google.com/open?id=1VcRDtOTK8IK5KwPf_WqX43hqm_0WIwpN | https://drive.google.com/open?id=1-Y6e23nqZDisdW6jLiePUcyYHFQcRseS |  | 99 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN065/25 | 2025-06-17 16:45 | crm@crystalgroup.in | CIPLA UNIT - VI | Ajinkya | 7030921315 | NA | CRIU4024028 |  |  | Ajinkya.Murkute@cipla.com | Goa | Preventive Maintenance |  | Call | Shabuddin | 2025-06-17 17:13 | technician@crystalgroup.in | CIPLA UNIT - VI | CRIU4024028 | 40FT 2BAY RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | PM Due | Arrange pm & on the way tech. | NA | No | P. M Due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN065%2F25 | Thermoking | TK-MP4000 | CIM1051752 | NA | NA | New | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-06-18 18:55 | 2025-06-17 |  |  |  |  | CRIU4024028 |  |  |  | Thermo king | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/20br | 9.9/9.9/9.8 | 413/413/412 | Short | Two way unit pm due....Water leak inside & top roof cipla will arranging pain leak proof coving... | Unit working as satisfactory no issue with & no alram.. | No | https://drive.google.com/open?id=19rEzqEdH3FR0vmV7jr7GxHev3hQ-Ai-p | https://drive.google.com/open?id=1KStEYfjhq3UrIiK_zRC0QOrOW9jB2aif |  | 99 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN066/25 | 2025-06-17 17:46 | crm@crystalgroup.in | Qwik Supply | Surav Kundu CPC | 7812067317 | NA | CICU2094068 |  |  | NA | Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-17 18:12 | 2025-06-17 |  |  |  |  | CICU2094068 |  |  |  | Thermo king | -40'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.8/19.4 b | 9.4 | 404 | Not done | Found Condenser coil normal dirty & Ice foundation on internal floor & controller door damaged | Need to replace controller with Key | Yes | https://drive.google.com/open?id=1Y5w42zI218YYYKmXNo-QgcFxF1TEbHHI | https://drive.google.com/open?id=1FNGaIcsRX0C3oLb2eKy4PdfRtaMb6Fhf |  | 96 | Yes | Yes | Urgent | Controller door & Key pad need to fix | Controller door Key pad | technician@crystalgroup.in | REEFER
JUN067/25 | 2025-06-19 14:47 | crm@crystalgroup.in | Crystal | Khirod | +91 82609 72816 | NA | MSCU5621100 | REPAIRS & REPLACEMENT |  | NA | JNPT | Repair Work |  | Call | Kunal | 2025-06-27 14:26 | crm@crystalgroup.in | Crystal Yard | MSCU5621100 | 40 GP Dry | NA | REPAIR | STOCK | NA | NA | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN067%2F25 | NA | DRY | NA | NA | NA | Used | NA | Thakur | No | REPAIRS & REPLACEMENT | 2025-06-19 18:58 | operation@crystalgroup.in | YES | IN074 | 2025-06-19 | FOC | CRYSTAL YARD | JNPT | MSCU5621100 | DEPOT | FOC | DRY | 2025-06-27 14:35 | crm@crystalgroup.in | NO |  |  |  |  | 2025-06-27 14:36 | crm@crystalgroup.in | NO
JUN068/25 | 2025-06-21 12:15 | crm@crystalgroup.in | Swadesh Milk | Rakesh Sharma | 916377926037 | NA | GESU9290991 | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Barabanki- UP | Running with issues |  | Call | Pushpa Mam | 2025-06-23 22:04 | technician@crystalgroup.in | Swadesh milk barabanki UP | GESU9290991 | 40" | Carrier | SERVICE-AT SITE | SALE | CHARGEABLE | No cooling | Temperley advise to check leak | R134a Gas/ N2/ Filter Drier ...if leak need brazing set& vacum pump | Yes | Suspected leak or Filter Drier choked | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN068%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | RAJ KUMAR | Yes | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-09-30 17:25 | crm@crystalgroup.in | YES | IN204 | 2025-09-30 | Spares | Swadesh Milk |  | GESU9290991 | SITE | PAID |  | 2025-10-15 10:40 | crm@crystalgroup.in | YES | IN204 | YES | https://drive.google.com/open?id=1GKB2ekQ4zuofmfBC_XLK1yB7bOVefM3D | Vendor | 2025-10-20 14:34 | crm@crystalgroup.in | YES | IN204 | COURIER | NA | NA |  |  |  | 2025-11-14 16:16 | 2025-11-10 |  |  |  |  | GESU9290991 |  |  |  | Carrier | -24C Ret.-23.4C Sup.-30.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.5bar 12.4bar | 12.3A 12.3A 12.3A | 414 | Not done | Breakdown | After observation of 36 hours, unit working fine , evaporator coil and filter drier has been changed, unit maintain -24'c . Heat termination thermostat and defrost sensor defective need to be replaced | Yes | https://drive.google.com/open?id=1fjkAqUTQkSSwJeT2LdmlTJ82TAISQww6 | https://drive.google.com/open?id=1Vy1LEbGRhi7Jae8UZ3P96M2Fwc6hGAAW |  | 127 | Yes | Yes | Urgent | Heat termination thermostat Defrost sensor Compressor contactor | Heat termination thermostat Defrost sensor Compressor contactor | technician@crystalgroup.in | REEFER
JUN070/25 | 2025-06-21 16:49 | crm@crystalgroup.in | ITC Ltd/M/s Bengal Nestor Industries | Suman | 918906415426 | NA | HDMU5221979 |  |  | NA | Bardhaman, Kolkata | Preventive Maintenance |  | Call | RAMIZ | [54 empty] | 2025-06-21 20:43 | 2025-06-21 |  |  |  |  | HDMU5221979 |  |  |  | Daikin | +1'C | Clean | Clean |  | Noisy | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7/14.1b | 10.3 | 195 | Not done | Found Condenser coil very dirty & Insufficient air circulation in condenser coil | Clean condenser coil with fresh water, need to keep space 2 meter for batter performance | No | https://drive.google.com/open?id=16HN77LA4Bv9AFRRI3vTvZF-of4u8LevG | https://drive.google.com/open?id=1neM1R52n8PsaY5YukFudYUWq_hS9vE2M |  | 100 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN071/25 | 2025-06-21 16:52 | crm@crystalgroup.in | ITC Ltd/M/s Bengal Nestor Industries | Suman | 918906415426 | NA | CGMU2990461 |  |  | NA | Bardhaman, Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-21 18:04 | 2025-06-21 |  |  |  |  | CGMU2990461 |  |  |  | Carrier | +0'C | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.8 | 12.2 | 395 | Not done | Found Condenser coil very dirty & R/S Evaporator Motor defective, Very less space for condenser air flow ( up to 2ft). Compressor Contactor 30 amps partial damage | In sufficient Air circulation due to less space condenser area.evp motor R/S in bypass. | Yes | https://drive.google.com/open?id=1te07V8iCmtV6JuBonzTcbG2sNaKKDiiy | https://drive.google.com/open?id=1k2dpGMtKdlJB5e_6f_kxq0X9B1jQa5G- |  | 100 | Yes | Yes | Urgent | Evp motor singh please complete 1nos Contactor 30 amps | Evp motor singh please complete 1nos Contactor 30 amps | technician@crystalgroup.in | REEFER
JUN072/25 | 2025-06-21 16:53 | crm@crystalgroup.in | ITC Ltd/M/s Bengal Nestor Industries | Suman | 918906415426 | NA | TCLU1910472 |  |  | NA | Bardhaman, Kolkata | Preventive Maintenance |  | Call | Ramiz | [54 empty] | 2025-06-21 20:49 | 2025-06-21 |  |  |  |  | TCLU1910472 |  |  |  | Daikin | +1'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8/13.5b | 10.1 | 396 | Not done | Found Condenser coil very dirty & Insufficient air circulation in condenser coil | Clean condenser coil with fresh water, need to keep space 2 meter for batter performance | No | https://drive.google.com/open?id=1EwjxeYbNp_JbA0CHgXVqCmi1meBxijE2 | https://drive.google.com/open?id=1sH9BXFZG255RkdToeKjxm5vbDHU6CJHl |  | 100 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN073/25 | 2025-06-21 17:30 | crm@crystalgroup.in | Dr Reddy | Suresh Kasam | 9908125456 | Plant Engineer | TITU9930074 |  |  | sureshkasam@drredddys.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin Sir | [54 empty] | 2025-07-01 16:54 | 2025-07-23 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -30 c | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 0.9 Suction 19 Discharge | R 10.2 B 10.3 B 10.3 | L1- 416 , L2- 415, L3- 410 | Not done | General Inspection and Cooling Issue with the compressor | Compressor test and fail in back, For compressor saftey traning and medical fitness complit with Dr. Reddy. | No | https://drive.google.com/open?id=1Tl8AsrfH5__iptWE3Al4azki_xsOvSGL | https://drive.google.com/open?id=1a3dDCaKyVB53u6KRij6Ken0OFAHczM8S |  | 101 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUN074/25 | 2025-06-21 17:33 | crm@crystalgroup.in | Dr Reddy | Suresh Kasam | 9908125456 | Plant Engineer | TITU9930114 |  |  | sureshkasam@drredddys.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin Sir | 2025-07-11 10:45 | crm@crystalgroup.in | Dr Reddy | TITU9930114 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | TKMP-4000 | PREVENTIVE MAINTENANCE | LEASE | FOC | Complaint attended | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN074%2F25 | Thermoking | TK-MP4000 | 14E219055 | EOG1000667 | NA | USED | NA | SHAHBUDDIN | Yes |  | 2025-07-11 11:31 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-11 11:36 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-11 11:38 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-11 12:08 | 2025-06-23 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -30C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9/19 | 10.2/ 10.3/10.3 | 416/415/410 | Short | General Inspection and Cooling Issue with compressor leaked | Compressor Test and fail in back leake, For compressor Saftey traning, Fitness complit with DR. REDDY. | No | https://drive.google.com/open?id=1TOb77ZT6DdzUUvlbmqPLqfmQArKtAJpg | https://drive.google.com/open?id=1GwjYpmFATFIDzt08CDlKDngBGW3U8dim |  | 101 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUN075/25 | 2025-06-21 17:34 | operation@crystalgroup.in | Tata Advance System | Raghu Ramesh | 8904971079 | NA | BMOU9788370 | Additional Spares | Sushma | NA | Bangalore | Additional Spares | Additional Spares | Call | Sushma | 2025-06-27 11:15 | crm@crystalgroup.in | Tata Advance System | BM0U9788370 | 40 FT Reefer | Daikin | REFURBISHMENT OF CONTAINER | LEASE | FOC | Data Logger and Genset Installation | NA | Data Logger, Genset | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN075%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | SHAHBUDDIN | No | Additional Spares | 2025-07-04 11:59 | operation@crystalgroup.in | YES | IN081 & IN082 | 2025-06-25 | Spares | Tata Advance System | Bangalore | BMOU9788370 | SITE | FOC |  | 2025-07-04 12:04 | operation@crystalgroup.in | YES | IN081 & IN082 | YES | https://drive.google.com/open?id=1CZug3KEZuGaXJBv95aUstV8q4RTLWcbK, https://drive.google.com/open?id=1hrSxPYzCp5b2uLp-Fq2lKj_IYkOCQ8cK | Vendor | 2025-07-10 14:45 | crm@crystalgroup.in | YES | IN081 & IN082 | COURIER | 25436200006089 | Shree Maruti |  | https://drive.google.com/open?id=1yNmar3WWn4BVmhQoW5VIjEm3YSXt6v0G |  | 2025-07-10 15:13 | 2025-07-05 |  |  |  |  | BMOU9788370 |  |  |  | Carrier | -26C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | 11/11.5/10.7 | 425/430/427 | Short | Check the cooling cabinate working fine. | Deffrost working in auto mode now changed to manual 6 hours once defrost | No | https://drive.google.com/open?id=1zJWf2jJ1n63aQG-Q_Mms6fStwZhZ4Lvu | https://drive.google.com/open?id=1Sjr32rHlYcy5oO66-uqQqCvR-iZZFRsi |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUN076/25 | 2025-06-24 12:18 | operation@crystalgroup.in | Dr. Reddy's Laboratories Ltd. | Sushma | NA | NA | SJKU4000038 | Additional Spares required | Sushma | NA | Vishakapatnam | Reimburesment | Additional Spares required | Call | NA | 2025-06-24 12:32 | operation@crystalgroup.in | Crystal Yard (Dr. Reddy's Laboratories Ltd.) | SJKU4000038 | 40FT STD RF | NA | REFURBISHMENT OF CONTAINER | SALE | FOC | Container to be ready | - | LED Light, Strip Curtains, Anti-Room Internal, Man Trap, Crystal Paint & logo | Yes | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN076%2F25 | - | CARRIER-PRIMLINE | - | - | - | Brand new | - | Thakur | No | Additional Spares required | 2025-06-30 10:32 | crm@crystalgroup.in | YES | IN085 | 2025-06-26 | Spares | Dr. Reddy's Laboratories Ltd. | Visakhapatnam | SJKU4000038 | DEPOT | FOC | CARRIER-PRIMLINE | 2025-08-08 14:47 | crm@crystalgroup.in | YES | IN085 | YES | https://drive.google.com/open?id=1CIXTSPBVQ5YoAER0rXAhf5io7cNcKox2, https://drive.google.com/open?id=1LPGg95wMxbnHKH4nVclD89vuj72xLlie | Stock and Vendor | 2025-08-08 14:49 | crm@crystalgroup.in | YES | IN085 | TECHNICIAN |  |  | SHAHBUDDIN
JUN078/25 | 2025-06-25 17:31 | operation@crystalgroup.in | Crystal Yard (HQIDS) | Pushpa Ma'am |  | DGM Sales | CICU3780951 | Logo Paint | Pushpa Ma'am | NA | JNPT | Refurbishment | Logo ANC_ 5.5ft x 2.5ft | Call | Kunal | 2025-06-25 17:40 | operation@crystalgroup.in | Crystal Yard (HQIDS) | CICU3780951 | 20GP | DRY CONTAINER | REFURBISHMENT OF CONTAINER | SALE | FOC | Logo ANC_ 5.5ft x 2.5ft | NA | Logo ANC_ 5.5ft x 2.5ft |  | Logo ANC_ 5.5ft x 2.5ft | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN078%2F25 | NA | DRY | NA | NA | NA | NA | NA | Thakur | No | Logo Paint | 2025-06-25 18:16 | operation@crystalgroup.in | YES | IN083 | 2025-06-25 | Consumables | Crystal Yard (HQIDS) | JNPT | CICU3780951 | DEPOT | FOC | DRY | 2025-06-25 18:18 | operation@crystalgroup.in | YES | IN083 | YES |  | Stock | 2025-07-04 11:46 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-09 10:39 | [54 empty] | operation@crystalgroup.in | DRY/Others
JUN079/25 | 2025-06-25 17:35 | operation@crystalgroup.in | Crystal Yard (HQIDS) | Pushpa Ma'am |  | DGM Sales | FWRU0324937 | Logo Paint | Pushpa Ma'am | NA | JNPT | Refurbishment | Logo ANC_ 5.5ft x 2.5ft | Call | Kunal | 2025-06-25 17:45 | operation@crystalgroup.in | Crystal Yard (HQIDS) | FWRU0324937 | 20GP | NA | REFURBISHMENT OF CONTAINER | SALE | NA | Logo ANC_ 5.5ft x 2.5ft | NA | Logo ANC_ 5.5ft x 2.5ft | Yes | Logo ANC_ 5.5ft x 2.5ft | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN079%2F25 | NA | DRY | NA | NA | NA | NA | NA | Thakur | No | Logo Paint | 2025-06-25 18:17 | operation@crystalgroup.in | YES | IN084 | 2025-06-25 | Consumables | Crystal Yard (HQIDS) | JNPT | FWRU0324937 | DEPOT | FOC | DRY | 2025-06-25 18:18 | operation@crystalgroup.in | YES | IN084 | YES |  | Stock | 2025-07-04 11:46 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-09 10:40 | [54 empty] | operation@crystalgroup.in | DRY/Others
JUN080/25 | 2025-06-25 17:36 | crm@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | CPC Manager | CXRU1043912 | FABRICATION, REPAIRS & REPLACEMENT |  | kuldeep18.yadav@qwik.co.in | Hapur | Running with issues | ceiling bulging and support ripped broken issue | Email | Pushpa Mam | 2025-07-01 15:23 | crm@crystalgroup.in | Qwik Supply | CXRU1043912 | 40FT STD RF | Daikin | SERVICE-ON CALL | LEASE | FOC | PT and CT board Defective, Suspected - Controller and current transformer | NA |  | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN080%2F25 | Daikin | DAIKIN | M001970 | K31404118374 | DECOS 3F / 2553 / 1 | Used | NA | RAMIZ | Yes | FABRICATION, REPAIRS & REPLACEMENT | 2025-07-09 10:23 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-09 15:46 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-09 15:46 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-12 09:32 | 2025-07-04 |  |  |  |  | CXRU1043912 |  |  |  | Daikin | -22'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -18.9psi/1340psi | 10.2A/10.1A/10.0A | 398V/399V/398V | Not done | We have attende tha unit found condenser coil durty and eveporetor coil havy iecing | We have work condenser coil wash with normal water and eveporetor coil ice clean after unit running sound condition | No | https://drive.google.com/open?id=1mkkWdMOoJ3n4_Jl1pYMSISlizzy16R0y | https://drive.google.com/open?id=1QOUSy9aHBJWTfCzzst2fG_mWo7R4Rp42 |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUN081/25 | 2025-06-25 17:41 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | TITU9930032 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | Madhusoodhana.k@sailife.com | Bidar | Running with issues | abnormality in achieving the temperature of the cold container | Email | Pushpa Mam | 2025-06-27 17:27 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | TITU9930032 | 40FT Spl RF | Carrier | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | EVP Motor Noisy Bearing issue | BEARING TO BE REPLACED | BEARING | Yes | EVP MOTOR NOISY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN081%2F25 | Carrier Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-06-30 17:48 | operation@crystalgroup.in | YES | IN087 | 2025-06-27 | Spares | Sai Life Science Pvt Ltd | Bidar | TITU9930032 | SITE | PAID | CARRIER-THINLINE | 2025-06-30 17:48 | operation@crystalgroup.in | YES | IN087 | YES |  | Stock | 2025-07-04 10:58 | qualitycontrol@crystalgroup.in | YES | IN087 | COURIER | 34498854445 | BLUE DART |  | https://drive.google.com/open?id=17MLq_r4UkRBiojvgQDUSxey2Ka6nmiAR |  | 2025-07-17 11:40 | 2025-07-12 |  |  |  |  | TITU9930032 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/12 br | 13.2/13.3/12.2 | 412/413/412 | Short | Evaprator motor Noisy | Replaced bearing for Evaprator motor | No | https://drive.google.com/open?id=1QLmwVs1XT6fD_InMhVegdvsCKWJaKZvC | https://drive.google.com/open?id=1XbwZxcxZLeMVwrzOGuquJ4HrDNmb0hgQ |  | 101 | No | No | Can be done on next PM | a | na | technician@crystalgroup.in | REEFER
JUN082/25 | 2025-06-25 18:04 | crm@crystalgroup.in | DIVIS LAB | Prasanna CH | 040-66966380 | NA | CONT 4 | leakages in the condenser coil |  | cprasanna@divislabs.com | Hyderabad | Running with issues | leakages in the condenser coil | Email | Pushpa Mam | 2025-06-26 21:49 | technician@crystalgroup.in | DEVIS LAB | DC SEZ NO:4 | 40" | Carrier Thin Line | SERVICE-AT SITE | SALE | CHARGEABLE | Condenser coil Gas leak | Unit under N2 test | Condenser coil new | Yes | Gas leakage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN082%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | leakages in the condenser coil | 2025-06-30 10:28 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-02 16:08 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-02 16:10 | operation@crystalgroup.in | NO | [7 empty] | 2025-06-30 23:31 | 2025-06-27 |  |  |  |  | DC-SEZ-04 |  |  |  | Carrier | +3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/10 br | 13.2/13.3/13.2 | 406/407/406 | Short | Unit Complan no cooling | leak test & found Condenser coil leak with Nitrogen. pull out leaking coil through brazing set used replaced new coil . brazing two pipes & vacum system and Gas charged. unit run observation & working as normal and handed over for operation. | No | https://drive.google.com/open?id=1EbTEzitSN5li881I5_hdGqdYVn4-ZINm | https://drive.google.com/open?id=1PgB0Ozcvn1qJNaTcCA8DtKd22mmYin0K |  | 101 | No | No | Can be done on next PM | NA | NA | technician@crystalgroup.in | REEFER
JUN083/25 | 2025-06-26 10:43 | crm@crystalgroup.in | ITC LIMITED, FOODS DIVISION | Shahrukh Khan | 7451877796 | NA | TRUL5253890 | Dry Container- Leakage problem | Jyostna | Shahrukh.Khan@itc.in | Munger, Bihar | Running with issues | Dry Container- Leakage problem | Email | Harshali | 2025-06-27 15:24 | crm@crystalgroup.in | ITC LIMITED, FOODS DIVISION | TRUL5253890 | 40 HC Dry | NA | SERVICE-AT SITE | LEASE | FOC | LEAKAGE FOUND | NA | NA | No | LEAKAGE FROM TOP | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN083%2F25 | NA | DRY | NA | NA | NA | USED | NA | RAJ KUMAR | No | Dry Container- Leakage problem | 2025-06-27 15:26 | crm@crystalgroup.in | NO | [9 empty] | 2025-06-27 15:26 | crm@crystalgroup.in | NO |  |  |  |  | 2025-06-27 15:26 | crm@crystalgroup.in | NO
JUN084/25 | 2025-06-26 15:43 | crm@crystalgroup.in | Qwik Supply | Mohit Rai | 9023419864 | NA | CICU2779935 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NA | Tejinder5.Singh@ril.com | Ahmedabad | Running with issues | Again our both 10ft blast freezer is unable to freeze PCM within the specified timeframe (8-11hrs.) and even after 23 hours of charging it found in liquid form, hence affecting our daily operations. This issue poses a risk of potential operational disruptions during high indent days, | Email | Pushpa Mam | 2025-07-01 18:22 | operation@crystalgroup.in | Qwik Supply | CICU2779935 | 10 ft reefer | TK-MP-4000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Sensor nor working | Container under warranty |  | Yes | Sensor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN084%2F25 | Thermoking | TK-MP4000 | E0GM030274 | ABC782800322010476 | NA | BrandNew | NA | RAMIZ | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-07-09 10:06 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-11 10:13 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-11 10:17 | crm@crystalgroup.in | YES | NA | COURIER | 34498856265 | Blue Dart |  | https://drive.google.com/open?id=1YHwONSMn3G29bDLMsRdxTFeJu6XUsGPD |  | 2025-07-30 14:38 | 2025-07-21 |  |  |  |  | CICU2779935 |  |  |  | Thermo king | -40C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 1.6 bar discharge 19.2 bar | R 11.1A B 10.2A Y 10.6A | 415V 415V 415V | Not done | Defective Supply and evp temp sensor | Supply and evp temp sensor | No | https://drive.google.com/open?id=10bPQ_Gksi4fobXA6YhtpUtU6yy8EuvdX | https://drive.google.com/open?id=1EXlR_0m2KmSIvrWQtQtNsyeYOmXGbIBR |  | N/A | No | No | Can be done on next PM | N/A | N/A | technician@crystalgroup.in | REEFER
JUN085/25 | 2025-06-26 16:06 | crm@crystalgroup.in | Qwik Supply | Mohit Rai | 9023419864 | NA | CICU2779909 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | mohit2.rai@qwik.co.in | Ahmedabad | Running with issues | Again our both 10ft blast freezer is unable to freeze PCM within the specified timeframe (8-11hrs.) and even after 23 hours of charging it found in liquid form, hence affecting our daily operations. This issue poses a risk of potential operational disruptions during high indent days. | Email | Pushpa Mam | 2025-07-01 18:21 | crm@crystalgroup.in | Qwik Supply | CICU2779909 | 10 ft reefer | TK MP 4000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | Sensor not working | NA | Sensors required | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN085%2F25 | Thermoking | TK-MP4000 | E0GM030263 | ABC782800322010201 | NA | BrandNew | NA | RAMIZ | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-07-08 15:48 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-11 10:12 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-11 10:18 | crm@crystalgroup.in | YES | NA | COURIER | 34498856265 | Blue dart |  | https://drive.google.com/open?id=1fbvXbiuLpXXQww8y3XN4rvQEi5OvBUW4 |  | 2025-07-18 18:09 | 2025-06-05 |  |  |  |  | CICU2779909 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/12br | 13.2/13.4/13.2 | 412/413/413 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1NXRzTfnz29rc4dn9BeYAf0vIz4U06hS2 | https://drive.google.com/open?id=1d5EaR6zUJnLycseBhszd0VKD8HW0STDu |  | 99 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUN086/25 | 2025-06-27 12:44 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | TCLU1130265 | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | ajit.sisodiya@qwik.co.in | Rajpura, Punjab | Running with issues | Temperature error showig | Call | Linaa | 2025-07-01 10:06 | crm@crystalgroup.in | Qwik Supply | TCLU1130265 | 40FT STD RF | TK MP 3000 | CONTAINER RUNNING BUT REPAIR REQUIRED | LEASE | FOC | EVP coil sensor and TK-MP-3000 return temp sensor | NA | EVP coil sensor and TK-MP-3000 return temp sensor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN086%2F25 | Thermoking | TK-MP3000 | NA | NA | NA | Refurbished | NA | RAMIZ | Yes | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-07-01 10:03 | operation@crystalgroup.in | YES | IN088 | 2025-06-30 | Spares | Qwik Supply | Rajpura | TCLU1130265 | SITE | FOC | TK-MP3000 | 2025-07-01 10:05 | operation@crystalgroup.in | YES | IN088 | YES |  | Stock | 2025-07-16 12:31 | operation@crystalgroup.in | YES | IN088 | COURIER | 34498854806 | Blue Dart |  | https://drive.google.com/open?id=1qdFI8airyUcdUIsMS9Fxq-xFELAq2cGN |  | 2025-09-16 14:13 | 2025-09-16 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | 3.0'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 16.2B | 7.2A 7.2A 7.2A | 404V 404V 404V | Short | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=18QyaTpAMDkredy8UKQAUD_9U7DAdsU3- | https://drive.google.com/open?id=17H00uFKe4XZYx6n5opWtNZbQWJqHFj_e |  | 118 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN087/25 | 2025-06-30 10:50 | crm@crystalgroup.in | Hetero Unit 5 | Ramesh | 9099033689 | NA | CXRU1186467 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Pushpa | 2025-07-02 10:46 | technician@crystalgroup.in | HETRO 5 | CXRU1186467 | 40" | DKN | SERVICE-AT SITE | SALE | FOC | PM service & Man trap & Hetro own sensor Instalation | PM & Instalation job under progress | .an trap light/switch/buttan/ silicon sealant/ Ins.tape/ nut bolts etc. | Yes | PM DUE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN087%2F25 | DKN | DAIKIN LXE10E | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-07-17 12:40 | 2025-07-08 |  |  |  |  | CXRU1186467 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/175 psig | 9.8/9.9/9.8 | 395//394/394 | Short | PM due & clints required to fixed Mantrap & temp. sensor Instalation | PM Complited with fixed Man trap and Instalation temp. sensor. | No | https://drive.google.com/open?id=19HGzC3VHm98UFAeZ-4SclLMZpZWX4Xdk | https://drive.google.com/open?id=1FrErikVNYjk_Y2CXPS6HYPAFS9nvOyEH |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUN088/25 | 2025-06-30 11:04 | crm@crystalgroup.in | Hetero Unit 5 | Ramesh | 9099033689 | NA | CXRU1186425 |  |  | NA | Hyderabad | Preventive Maintenance |  | Email | Pushpa Mam | [54 empty] | 2025-07-03 00:06 | 2025-06-30 |  |  |  |  | CXRU1186425 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/180 psig | 9.9/9.9/9.8 | 395/394/394 | Short | unit working as satisfactory | PM service completed | Yes | https://drive.google.com/open?id=1LDtXx14GH6igPAm_cLFrQF4ByvOFlY0m | https://drive.google.com/open?id=12ovOYPDMkfwV4ZMATjOywhgkaZGY52oO |  | 101 | No | No | Can be done on next PM | na | Mantrap and switch / cable/ silicon | technician@crystalgroup.in | REEFER
JUN089/25 | 2025-06-30 11:21 | crm@crystalgroup.in | HETERO UNIT 3 | B. Mahendranath | 6309652982 | NA | CXRU1550769 | Water lekage at back side of reefer container. |  | NA | Hyderabad | Running with issues | Water lekage at back side of reefer container. | Email | Pushpa mam | [54 empty] | 2025-08-02 16:41 | 2025-07-24 |  |  |  |  | CXRU1550769 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 11.2 bar | 7.2 7.2 7.2 | 415 415 415 | Short | Pm service and general inspection done | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1Zggwn0wMFBeOI2WqCUDbXhMtCO39kn5G | https://drive.google.com/open?id=13Xh1UsyNQDd6-Dq4ON3eVeIys_TXyPWY |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUN090/25 | 2025-06-30 11:23 | crm@crystalgroup.in | HETERO UNIT 3 | B. Mahendranath | 6309652982 | NA | CXRU1326276 | water lekage at back side of reefer container. |  | NA | Hyderabad | water lekage at back side of reefer container. | water lekage at back side of reefer container. | Email | Pushpa mam | 2025-07-05 15:30 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1326276 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | CHARGEABLE | Water lekage at back side of reefer container | NA |  | No | Water lekage at back side of reefer container | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN090%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | water lekage at back side of reefer container. | [29 empty] | 2025-07-17 16:50 | 2025-07-11 |  |  |  |  | CXRU1326276 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/12br | 9.8/9.9/9.8 | 406/407/407 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1F5DVW0lahJGoBWGKLrSMgi6gCk1Lz5IG | https://drive.google.com/open?id=1SjBGmar4472C-ZWqZTU4O__Azls-tFzH |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUN091/25 | 2025-06-30 15:45 | crm@crystalgroup.in | Soft Box | Satish | 8977711235 | NA | TITU8257288 | Need to check |  | NA | Hyderabad | Running with issues | Need to check | Call | Pushpa mam | 2025-07-02 10:41 | technician@crystalgroup.in | soft box | TITU8257288 | 40" | Thermoking mp 4000 | SERVICE-AT SITE | SALE | FOC | low Gas in system | Required Gas adding to system | R404A Gas- 3 KG | Yes | minar leak system need to chech | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN091%2F25 | TK MP 4000 | TK-MP4000 | NA | NA | NA | NA | NA | SHAHBUDDIN | Yes | Need to check | 2025-07-16 11:35 | operation@crystalgroup.in | YES | IN096 | 2025-07-11 | Consumables | Soft Box | Hyderabad | TITU8257288 | SITE | PAID | TK-MP4000 | 2025-07-02 17:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-16 11:37 | operation@crystalgroup.in | YES | IN096 | ARRENGING AT SITE | [5 empty] | 2025-07-16 12:03 | 2025-07-04 |  |  |  |  | TITU8257288 |  |  |  | Thermo king | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.7/21 | 10.0/ 10.1/ 70.0 | 417/ 416/410 | Short | Found Compressor contractor burned and Noisy | Run unit observe and found compressor contactor burned and noisy, Replaced contactor and unit run, it was working. | No | https://drive.google.com/open?id=1oJw7zgL2OF5TBS70M7VUG14Da1rWvand | https://drive.google.com/open?id=1su10iLPpvRWGd-zdH91PVyXK3hwlSSHX |  | 101 | No | No | Can be done on next PM | NA | Arranged on site | crm@crystalgroup.in | REEFER
JUN092/25 | 2025-06-30 16:35 | crm@crystalgroup.in | Tata Advance | Raghu Ramesh | 8904971079 | NA | BMOU9788370 | Machine not working. | Machine not working. | NA | Bangalore | Running with issues | Machine not working. | Call | PUSHPA MAM | 2025-07-05 16:23 | crm@crystalgroup.in | Tata Advance | BMOU9788370 | 40FT STD RF | Daikin | SERVICE-AT SITE | LEASE | CHARGEABLE | Container is on Auto defrosting mode | NA | No | No | Container is on Auto defrosting mode | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUN092%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | Machine not working. | 2025-07-05 17:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-05 17:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-05 17:04 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-07 17:45 | 2025-07-05 |  |  |  |  | BMOU9788370 |  |  |  | Carrier | -26c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | 11/11.5/10.7 | 425/430/427 | Not done | Check the cooling cabinate working fine diffrost issue | Deffrost working In auto mode, Now changed to manual 6 hours once on the defrost | No | https://drive.google.com/open?id=1VZFC7sFK1wm4B1ty7MuLe0tVPkMWf4q0 | https://drive.google.com/open?id=1l2Yu2lq-Delottd6pDyAGUmPAGjqZTFl |  | TRIP104 | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUL001/25 | 2025-07-02 10:39 | operation@crystalgroup.in | Avenue Supermarts LTD-Dmart | Mr. Rajesh Hatankar | 9920892255 | NA | HDMU4698329 | REPAIRS & REPLACEMENT | Door Gasket Issue | NA | Thane | Running with issues | Door Gasket Issue | Email | Jyotsna | 2025-07-02 10:52 | operation@crystalgroup.in | Avenue Supermarts LTD-Dmart | HDMU4698329 | 40FT | NA | REPAIR | LEASE | FOC | Door Gasket Issue | NA | Rubber Gasket | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL001%2F25 | NA | DRY | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-09-30 11:07 | crm@crystalgroup.in | YES | IN098 | 2025-07-12 | Spares | Avenue Supermarts LTD-Dmart |  | HDMU4698329 | SITE | FOC |  | 2025-09-30 11:15 | crm@crystalgroup.in | YES | IN098 | NA | https://drive.google.com/open?id=1wtUltvzDzrg1fz_hSLqteU8GwQSvZd9O, https://drive.google.com/open?id=1dnpLUijB1jWc1DJV1yjFmQrnvvfLjLtx | Vendor | 2025-09-30 11:16 | crm@crystalgroup.in | YES | IN098 | ARRENGING AT SITE | [5 empty] | 2025-09-30 11:22 | [54 empty] | crm@crystalgroup.in | DRY/Others
JUL002/25 | 2025-07-03 16:15 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Saleem | 9108924032 | NA | MYRU4507120 | Machine not working |  | saleem.t@sailife.com | Bidar | Complete Breakdown | Machine not working | Call | Harshali | 2025-07-08 18:34 | crm@crystalgroup.in | Sai Life Science | MYRU4507120 | 40 FT | Daikin | SERVICE-AT SITE | SALE | AMC | Comprassor chowk, Gas needs to refill | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL002%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No | Machine not working | 2025-07-30 17:52 | crm@crystalgroup.in | YES | IN119 | 2025-07-24 | Spares | Sai Life Science | Bidar | MYRU4507120 | SITE | FOC | CARRIER-THINLINE | 2025-07-30 17:53 | crm@crystalgroup.in | YES | IN119 | YES | https://drive.google.com/open?id=1st8rz_TQGmnORHkGjYEdZS5k57gonqvB | Vendor | 2025-07-31 20:26 | crm@crystalgroup.in | YES | IN119 | COURIER | NA | Dolphin |  | https://drive.google.com/open?id=1s5k7k8BnK3Is-7xkqyCPYcnuodDfykrY |  | 2025-08-18 11:41 | 2025-08-16 |  |  |  |  | MYRU4507120 |  |  |  | Carrier | +5'c | Clean | Clean |  | Okay | Clean | Noisy | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9b 11.9b | 7.2A 7.2A 7.2A | 416v 416v 416v | Short | Service call | Suction transducer and Suction sensor has been replaced. Unit running in good condition. | Yes | https://drive.google.com/open?id=1_5y-bmTADjTD4-HZG-hMvqTFy7Q7igVo | https://drive.google.com/open?id=161lUn5Pd91hicCRwX5pUEV_T3aZfwCNr |  | TRIP106 | No | Yes | Can be done on next PM | Nil | Evaporator motor | technician@crystalgroup.in | REEFER
JUL003/25 | 2025-07-03 17:30 | crm@crystalgroup.in | Tianish | 7799045848 | Ravi kumar | 7799045848 | TRLU1741601 | Leakage problem |  | NA | Vizianagaram | Preventive Maintenance | Leakage problem | Call | Pushpa mam | 2025-07-24 12:24 | operation@crystalgroup.in | Tianish | TRLU174160 | 40FT | Thermoking | SERVICE-AT SITE | SALE | FOC | Compressor making abnormal sound, found burn relay connection pin melt | Compressor to be replaced, Relay board to be replaced | 1)Compressor - 1 2)Relay Board -1 3) R404A 4 kg 4) Display -1 | Yes | Compressor making abnormal sound, found burn relay connection pin melt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL003%2F25 | Thermoking | TK-MP3000 | NA | NA | NA | USED | NA | SITARAM | Yes | Leakage problem | [29 empty] | 2025-07-31 15:42 | 2025-07-22 |  |  |  |  | TRLU1741601 |  |  |  | Thermo king | 18 | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 1.8b 18.6b | 12.A 12A 12A | 398v 398v 398v | Not done | Customer request to visit found relay bord found burnt, relay connection pim foundation melt, compressor not found groud. Compressor making abnormal voice qnd vibration due to internal mechanical problem. | Relay bord need to replace due due to burnt out. Compressor need to replace due to internal mechanical problem causing abnormal noise/bed noise and vibration | Yes | https://drive.google.com/open?id=1mPQd-rBv5UKi1rh0_kIQb7Xszp-luGHr | https://drive.google.com/open?id=1NJxn-iBOFokGpEzDAmHsuO6qHTCfC5cw |  | TRIP106 | Yes | Yes | Urgent | Same as above | Compressor Relay bord Gas 404 4kg Display | technician@crystalgroup.in | REEFER
JUL004/25 | 2025-07-04 18:14 | crm@crystalgroup.in | DR. Reddy's Unit III | Srinivasa Reddy | 9391378300 | NA | GSOU6384240 |  |  | srinivasre@drreddys.com | BOLLARAM IND. AREA | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-06 10:18 | 2025-09-04 |  |  |  |  | GSOU6384240 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/200 psig | 12 4/12.5/12.4 | 412/411/412 | Short | Pm completed with replaced reefer unit new Instalation done. | Reefer unit Instalation done | No | https://drive.google.com/open?id=1vJ4clanoQTF1UsxXdgOhaVZ7w8itufCz | https://drive.google.com/open?id=1k2jlEBJBVc3oDabMznSfEl5xGZVz09Bo |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL005/25 | 2025-07-04 18:59 | operation@crystalgroup.in | Qwik Supply | Kuldeep Yadav | 9990063655 | NA | CXRU1040322 | REPAIRS & REPLACEMENT |  | NA | Hapur | Running with issues | Contactor burn | Call | Rajkumar | 2025-07-08 17:53 | operation@crystalgroup.in | Qwik Supply | CXRU1040322 | 40FT | Daikin | SERVICE-ON CALL | LEASE | FOC | Contactor connection burn | New Connection refix | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL005%2F25 | Daikin | DAIKIN | M001862 | K31403112957 | DECOS 3F / 2609 / 1 | Used | NA | RAJ KUMAR | Yes | REPAIRS & REPLACEMENT | 2025-07-08 17:56 | operation@crystalgroup.in | NO | [9 empty] | 2025-07-08 17:56 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-08 17:57 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-12 09:20 | 2025-07-05 |  |  |  |  | CXRU1040322 |  |  |  | Daikin | -22'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -19psi/1345psi | 10.0/10.1/10.0 | 393/394/393 | Short | We have attende tha unit found condenser coil durty and eveporetor coil havy iecing and compressor contacter connection burnt 1 nose | We have work condenser coil wash with normal water and eveporetor coil ice clean and compressor contacter connection replace and exepaintion Valve body moisture clean with Hot water after unit running sound condition | No | https://drive.google.com/open?id=1Wlw6XHUkVqnxGTsaLyhXVGH4M-UOwDLL | https://drive.google.com/open?id=1LoAPGfrYa71Kcmnk4gNKDnsDBCXkw8NA |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUL006/25 | 2025-07-07 16:49 | crm@crystalgroup.in | Kirloskar Corrocoat | Ashutosh Kumar | 6204240137 | Deputy Manager– Application Department | PCIU5822411 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NA | pundlik.dhope@kicopl.com | Ghatampur | Running with issues | The internal temperature has reached 21°C and the cooling unit is not functioning. | Email | Pushpa | 2025-07-07 17:12 | crm@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20FT STD RF | Daikin | SERVICE-AT SITE | SALE | FOC | The internal temperature has reached 21°C and the cooling unit is not functioning. | Call alined with Ajay Technician at our Yard |  | No | The internal temperature has reached 21°C and the cooling unit is not functioning. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL006%2F25 | Daikin | DAIKIN | LXIDEA33A | NA | NA | Used | NA | Thakur | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-07-12 10:45 | operation@crystalgroup.in | NO | [9 empty] | 2025-07-12 13:07 | operation@crystalgroup.in | NO |  |  |  |  | 2025-07-12 13:08 | operation@crystalgroup.in | NO | [7 empty] | 2025-07-12 09:45 | 2025-07-10 |  |  |  |  | PCIU5822411 |  |  |  | Daikin | +12'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 68psi/1135psi | 9.1A/9.0A/9.0A | 401V/400V/402V | Not done | We have attende tha unit found condenser coil havy durty and R134a gas low 1.5kg | We have work condenser coil wash with normal water and R134a gas top up 1.5kg after unit running sound condition | No | https://drive.google.com/open?id=1gwImF2WkJRkMdPNECJYNMnM_tDiJvy1c | https://drive.google.com/open?id=1krrR50aItODaBR31BqrkSOFrlJoUFpVQ |  | Trip097 | No | No | Can be done on next PM | No | No | rajreefertech@gmail.com | REEFER
JUL007/25 | 2025-07-09 16:49 | crm@crystalgroup.in | HETERO UNIT 3 | M.V.Subrahmanyam | 8121002374 | NA | CXRU1550769 | Facing Power Shut down issue |  | Subrahmanyam.M@hetero.com | Hyderabad | Running with issues | Facing Power Shut down issue | Email | Gauri | 2025-07-12 12:21 | crm@crystalgroup.in | Hetero Labs Unit 3 | CXRU1550769 | 40FT STD RF | Carrier | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor Grounded. | NA | Carrier Primeline comprassor | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL007%2F25 | Carrier | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | Facing Power Shut down issue | 2025-07-23 16:31 | crm@crystalgroup.in | YES | IN106 | 2025-07-16 | Consumables, Spares | Hetero Labs Unit 3 | HYDERABAD | CXRU1550769 | SITE | PAID | CARRIER-PRIMLINE | 2025-07-23 16:34 | crm@crystalgroup.in | YES | IN106 | YES | https://drive.google.com/open?id=1hybQp_bUdjlMebWaYlwumjURBQ2zlK8Q | Stock and Vendor | 2025-07-24 12:15 | qualitycontrol@crystalgroup.in | YES | JUL007/25 | COURIER | NA | DOLPHINE TRAVEL VASHI |  | https://drive.google.com/open?id=1hjr8dDTgQFbCgtsV_I84S_1ECBj_39ZU |  | 2025-08-02 16:11 | 2025-07-24 |  |  |  |  | CXRU1550769 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 13.5 bar | 6.9 6.9 6.9 | 415 415 415 | Short | Pm service and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1IbepCMWMboRfLZlEC8UQY2uc3jwwKWue | https://drive.google.com/open?id=1QoT7ILrWdTGl3d-GFXepP-__OiOWmbIo |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL008/25 | 2025-07-14 15:16 | crm@crystalgroup.in | OLD MUMBAI ICECREAM DAIRY | NEERAV | 9833174697 | NA | CCLU1030531 | DISPLAY NOT VISIBLE |  | NA | ICHALKARANJI | Complete Breakdown |  | Email | PUSHPA MAM | 2025-07-16 10:24 | crm@crystalgroup.in | OLD MUMBAI ICECREAM DAIRY | CCLU1030531 | 20FT | Daikin | INSTALLATION | SALE | CHARGEABLE | Display not working. | NA | Display | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL008%2F25 | Daikin | DAIKIN | NA | NA | NA | New | NA | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE | 2025-07-30 11:51 | crm@crystalgroup.in | YES | IN114 | 2025-07-22 | Spares | OLD MUMBAI ICECREAM DAIRY | ICHALKARANJI | CCLU1030531 | SITE | PAID | DAIKIN | 2025-07-30 11:52 | crm@crystalgroup.in | YES | IN114 | YES | https://drive.google.com/open?id=1pMLjHUnrjHJXismHw5rezJqKJot43oCW | Vendor | 2025-07-30 11:53 | crm@crystalgroup.in | YES | IN114 | TECHNICIAN |  |  | NEMICHAND |  |  | 2025-07-30 15:12 | 2025-07-25 |  |  |  |  | CCLU1030531 |  |  |  | Carrier | N/A | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay | https://drive.google.com/open?id=18Zc2SlE83zyc_XHmNVKqv72Bb7WhihZb | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | N/A | N/A | 413V 413V 413V | Not done | Display checked and fixed also inspected the compressor | Compressor found to be grounded needs to be replaced and display has been properly set. | Yes | https://drive.google.com/open?id=1OWpcxcN3J-5WL2xXXYP48iK2udlUv4rM | https://drive.google.com/open?id=1ZFM4XxfzkQDc_KDudK6IAjCUOvGI7zoe |  | N/A | Yes | Yes | Urgent | Compressor grounded need to be replaced | 1) compressor 2) 4kg gas R134a 3) Filter driver | technician@crystalgroup.in | REEFER
JUL009/25 | 2025-07-14 16:37 | crm@crystalgroup.in | Orbittal Electromech Engg. Projects Pvt. Ltd | Bhivaji/mobilization@orbittal.com | 7774076748 | NA | Site Cabin 59 | Leakage issue |  | Bhivaji/mobilization@orbittal.com | Taloja | Water leakage |  | Call | Gauri | 2025-07-30 12:36 | crm@crystalgroup.in | Orbittal Electromech Engg. Projects Pvt. Ltd | Site Cabin 59 | NA | NA | REPAIR | LEASE | FOC | LEAKAGE ISSUE FROM TOP | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL009%2F25 | NA | DRY | NA | NA | NA | NA | NA | THAKUR | No | Leakage issue | [12 empty] | 2025-10-15 10:52 | crm@crystalgroup.in | NO
JUL010/25 | 2025-07-15 10:19 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhana | 72593 66532 | NA | PCIU6008328 | REPAIRS & REPLACEMENT |  | madhusoodhana.k@sailife.com | Bidar | Complete Breakdown | This reefer container is shifted from unit 6 to unit 4 in unit 4 Instalation done by sai lab staff. at the Instalation time wrong power supply connection with wrong harness PT/ CT Board fixed by sai Lab. Due to this reason PT/CT Board & container got damaged/ or malfunction... Requried spares PT/CT BOARD CONTROLLER DECOS III D ( OLD MODEL) I/O BOARD- SUSPECTED | Call | PUSHPA MAM | 2025-07-15 10:29 | crm@crystalgroup.in | Sai Life Science | PCIU6008328 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | PTCT Board, IO Board and Controller not working. | NA | PT/CT BOARD CONTROLLER DECOS III D ( OLD MODEL) I/O BOARD- SUSPECTED | Yes | Instalation time wrong power supply connection with wrong harness PT/ CT Board fixed by sai Lab. Due to this reason PT/CT Board & container got damaged/ | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL010%2F25 | Daikin | DAIKIN | NA | NA | NA | used | JSGA622340291 | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | 2025-07-21 10:40 | crm@crystalgroup.in | YES | IN102 | 2025-07-15 | Spares | Sai Life Science | BIDAR | PCIU6008328 | SITE | PAID | DAIKIN | 2025-07-21 11:01 | crm@crystalgroup.in | YES | IN102 | YES | https://drive.google.com/open?id=1FJ0FDPhBVxx1D6E-drgBb5guXg9tx-7U | Stock and Vendor | 2025-07-21 11:48 | crm@crystalgroup.in | YES | IN102 | TECHNICIAN |  |  | Ramesh |  |  | 2025-07-30 10:30 | 2025-07-11 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | Unit not working with AL 707 | NA | Yes | https://drive.google.com/open?id=10EV-Hhf-L5dzufHNbfdjLmybJX5V1F0K | https://drive.google.com/open?id=1uOMCuJ5H0lGpw7PfH2L3jJPcepczzvFr |  | TRIP101 | No | No | Can be done on next PM | NA | PTCT board IO Board Daikin Controller 3D | crm@crystalgroup.in | REEFER
JUL011/25 | 2025-07-15 11:36 | crm@crystalgroup.in | Qwik Supply | Lalit Saini | 9928034131 | NA | TRIU6680335 | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | lalit.saini@qwik.co.in | Jaipur | Running with issues | The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze | Email | PUSHPA MAM | 2025-07-15 12:21 | crm@crystalgroup.in | Qwik Supply | TRIU6680335 | 20FT STD RF - Dual Machine Carrier unit | Daikin | SERVICE-AT SITE | LEASE | FOC | The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze. | NA |  | No | The current observed temperature is between -12 to -14, This is the reason why the PCM pad is taking a long time to freeze. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL011%2F25 | Daikin | DAIKIN | NA | NA | NA | Used | NA | AKSHAY | Yes | COMPRESSOR MAKING NOISE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-09-30 11:39 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-30 11:40 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-30 11:41 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-04 17:56 | 31/10/0025 |  |  |  |  | TRIU6680335 |  |  |  | Daikin | -30C Ret. -25C Sup. -23.6C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | Suction LPT-23 Discharge HPT1278 | 12.7A 10.5A | 408A 408A 48A | Not done | I visited the site and thoroughly checked the entire unit. Everything is fine, including the wiring. However, the ambient sensor and supply sensor readings are out of range and need to be replaced. The compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | The ambient sensor and supply sensor readings are out of range and need to be replaced. The compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | Yes | https://drive.google.com/open?id=12ImdaL8oryGDR8qkESBaebIL5oRxTk-G | https://drive.google.com/open?id=1ApCc3y9HV45TnpDqDqgPiRdZu9dtAb-A |  | 127 | Yes | Yes | Urgent | Compressor daikin Gas 5kg Filter drier Vacuum pump Ambent sensor Supply sensor 2 nos | Compressor daikin Gas 5kg Filter drier Vacuum pump Ambent sensor Supply sensor 2 nos | technician@crystalgroup.in | REEFER
JUL012/25 | 2025-07-15 15:41 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd,Kothur | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering, | CXRU1030387 | 1 unit is not working, Stand by unit is on and not achieving said Temp |  | brahmaiah.g@hetero.com | Hyderabad | Running with issues | 1 unit is not working, Stand by unit is on and not achieving said Temp. Asked to share video and photos | Email | Pushpa Mam | 2025-07-16 10:44 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd, | CXRU1030387 | 40FT STD RF with Anteroom | Carrier Primeline | SERVICE-AT SITE | LEASE | CHARGEABLE | Compressor not working | NA | Compressor- Carrier Primeline Filter Drier Compressor Gasket Compressor Oil Gas- 134a- 5kg's Vaccum pump | Yes | Need to change compressor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL012%2F25 | DAikin | CARRIER-PRIMLINE | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | NA | SHAHBUDDIN | Yes | 1 unit is not working, Stand by unit is on and not achieving said Temp | 2025-08-08 11:43 | crm@crystalgroup.in | YES | IN118 | 2025-07-23 | Consumables, Spares | Hetero Plasma Sciences Pvt Ltd,Kothur | Hyderabad | CXRU1030387 | SITE | PAID | DAIKIN | 2025-08-08 11:46 | crm@crystalgroup.in | YES | IN118 | YES | https://drive.google.com/open?id=1SQT7t767cjqqMIMqCX_ECivL5LcZoHW9, https://drive.google.com/open?id=1cKnJkKXdq_rhlWkErqXXij7nyb3k0n3r | Stock and Vendor | 2025-08-08 11:50 | crm@crystalgroup.in | YES | IN118 | COURIER | 1445 | Dolphin travels Vashi |  | https://drive.google.com/open?id=18fMW3rFom5hS0_bUh84gNmtDnkHQp9Yr |  | 2025-08-11 11:10 | 2025-08-05 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 1200 | 7.9 7.9 7.9 | 395 395 395 | Not done | Unit breakdown | New compressor replace Vacuum system Drive filter replace R134a gas charge Has been done Unit running good condition. | No | https://drive.google.com/open?id=1cDcoxDvLBpNBxiZt90uouE3J5wz69F47 | https://drive.google.com/open?id=1ts2y26Q4wAR3YUNeT7D-Hl5Qt_g2XVzR |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL013/25 | 2025-07-17 15:30 | crm@crystalgroup.in | Qwik Supply | Deepak Singh | 9254012557 | NA | CICU277991 | Lights Not working |  | Deepak91.Singh@ril.com | Sonipat, Haryana | Running with issues | Lights not working | Email | Pushpa Mam | 2025-07-18 16:54 | technician@crystalgroup.in | Quick supply Ril | CICU277991 | 10" | TK | SERVICE-AT SITE | LEASE | FOC | Internal Light not working. | repair will done by clints | Tube light / cable 10mt.( 2.5 two core) casing pati-1 & 16 A single pole MCB. ETC..... | Yes | Light wiring shirtage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL013%2F25 | TK | TK-MP4000 | na | na | na | New | na | RAJ KUMAR | No | Lights Not working | 2025-08-01 16:31 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-01 16:31 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-01 16:32 | crm@crystalgroup.in | NO | [7 empty] | 2025-09-13 14:52 | 2025-09-03 |  |  |  |  | CICU277991 |  |  |  | Thermo king | -40'c , | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 16.5B | 11.4A 11.4A 11.4A | 404V 404V 404V | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1344mDLXbDc9M1WvyUt949iXsganoK_h6 | https://drive.google.com/open?id=1LH9tSNNtHkJRma01QJ6j8P2TG90MDGfq |  | 117 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL014/25 | 2025-07-17 18:42 | operation@crystalgroup.in | Hetero Unit 5 | Ramesh | 9099033689 | NA | CXRU1030746 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-18 17:04 | 2025-07-02 |  |  |  |  | CXRU1030746 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/170psig | 9.9/9.8/9.8 | 402/403/402 | Short | PM due | PM service completed | No | https://drive.google.com/open?id=1osoTBEB75qyXaGnE_CKz-cYUHpjVBcfZ | https://drive.google.com/open?id=1wZiYTKnWHI6psC0QLs4voQKb6_sI0fiX |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL015/25 | 2025-07-17 18:46 | operation@crystalgroup.in | DR. REDDY LAB CTO-5 | T.Sreeram Naik | 7036305829 | NA | CXRU1045896 |  |  | sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-18 17:22 | 2025-07-04 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/170 PSIG | 9.9/10/9.9 | 412/413/413 | Short | PM due | PM service completed | No | https://drive.google.com/open?id=1fq0DQpJyL8IWGyaG650Yc2iHhDskuwwQ | https://drive.google.com/open?id=1EyqwRDNAdfWSsUrCYlnU_mGxn6CYP1dm |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL016/25 | 2025-07-18 10:31 | crm@crystalgroup.in | Dr Reddy | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | NA | CXRU1032564 |  |  | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  | Email | Aparna | [54 empty] | 2025-07-18 17:43 | 2025-07-04 |  |  |  |  | CXRU1032654 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/175 psig | 9.9/10/10 | 391/392/391 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1CCWQizB_AVVwskwJtWuQjbIvmBhJ7YrS | https://drive.google.com/open?id=1V3Aah1VgsgPrdRCKlfn1PNJ-rjkHsiTA |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL017/25 | 2025-07-18 10:38 | crm@crystalgroup.in | Dr Reddy | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | NA | GSOU6384153 |  |  | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Nalgonda | Preventive Maintenance |  | Email | Aparna | [54 empty] | 2025-07-18 17:31 | 2025-07-04 |  |  |  |  | GSOU6384153 |  |  |  | Carrier | +18.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/200 psig | 13.2/13.3/13 2 | 397/396/396 | Short | PM due | na | No | https://drive.google.com/open?id=1GsnIVVF-cW5bBt6xGF1rc1ykExvl5I3s | https://drive.google.com/open?id=1Cr9_xdv6h9STsyqFj7jYuZivUUTq9kPa |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL018/25 | 2025-07-18 11:28 | crm@crystalgroup.in | HETERO UNIT 3 | B. Mahendranath | 6309652982 | NA | CXRU1026520 |  |  | NA | Jadmetala | Complete Breakdown |  | Email | Aparna | 2025-07-23 16:45 | crm@crystalgroup.in | Hetero Unit 3 | CXRU1026520 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | GAS NEEDS TO BE REFILED | NA | ONLY GAS REQURIED | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL018%2F25 | Daikin | DAIKIN | M000785 | K31405122858 | DECOS 3F 2553 / 1 | Used | JSGA623040278 | RAMESH | Yes |  | 2025-07-30 10:59 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-30 11:00 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-30 11:01 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-30 11:43 | 2025-07-25 |  |  |  |  | CXRU1026520 |  |  |  | Daikin | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4/17.3B | 8.9/9.6/9.3 | 394/395/415 | Short | PM and General Inspection Done | PM services and unit operation and all sensor reading checked. Unit working fine | No | https://drive.google.com/open?id=1AocgnFiWLycCOPL6PSLgOktUWMk8CyIH | https://drive.google.com/open?id=1u9P5kXuSXky8bwOjEqpRtkpM63jMy92h |  | NA | No | No | Can be done on next PM | NA | na | crm@crystalgroup.in | REEFER
JUL019/25 | 2025-07-19 12:46 | operation@crystalgroup.in | Kirloskar Corrocoat | pundlik.dhope | 9881003659 / 9890385995 | NA | PCIU5822411 | not getting alarm | not getting alarm-connected with rajkumar and customer-Container under observation | pundlik.dhope@kicopl.com /shailendra.patil@kicopl.com | Ghatampur | Running with issues | not getting alarm | Email | Pushpa | 2025-07-22 18:09 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | Unit temp not maintaining | We've top-up 0.5kg gas by cleaning the condenser coil. | R-134a Gas 0.5Kg | Yes | Unit has condenser coil dusty & gas less | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL019%2F25 | DAIKIN | DAIKIN | LXIDEA33A | NA | NA | USED | JSGA623040170 | RAJ KUMAR | Yes | not getting alarm | 2025-08-08 11:56 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-08 12:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 12:02 | crm@crystalgroup.in | NO | [7 empty] | 2025-09-22 17:48 | 2025-09-22 |  |  |  |  | PCIU5822411 |  |  |  | Daikin | 12'C, supply 11.9'C, Return 12.2'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | 0.1B, 11.4B | 7.9A 7.9A 7.9A | 404V 404V 404V | Short | During inspection, it was observed that the main power supply wire from the PCTC board was not connected and the RPP connection was loose. After rectifying these issues, the unit started functioning. | After 24 hours of observation, the discharge temperature was found to be high, which caused the unit to shut down repeatedly. This may be due to contaminated refrigerant, in which case the system should be vacuumed and recharged with fresh gas. Will observation and check, If the problem continues, compressor replacement will be necessary. | Yes | https://drive.google.com/open?id=1chU1By9yjGKDVRt33AHaoKUdhcs9Ekz_ | https://drive.google.com/open?id=1oQB39oDgkSyEtAEsjGI5KAVE0C7x5N87 |  | 117 | Yes | Yes | Urgent | Same | Display R134A 5kg Filter drier | technician@crystalgroup.in | REEFER
JUL020/25 | 2025-07-21 15:05 | operation@crystalgroup.in | Transy Global | Venkat | 9703736718 | Manager | TITU8259378 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-21 16:09 | 2025-07-05 |  |  |  |  | TITU8259378 |  |  |  | Thermo king | -22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18 br | 9.9/9.9/10 | 402/403/402 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1lnb1ZTSNgy2ttkf7eAvMoEhyYux9Eo_H | https://drive.google.com/open?id=1nlPABn1bJHxcQpd292z8f82jDu-9S-e2 |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL021/25 | 2025-07-21 15:11 | operation@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | PCIU6016370 |  |  | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-22 11:18 | 2025-07-11 |  |  |  |  | PCIU6016370 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/170 psig | 9.9/9.8/9.8 | 407/406/407 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1KjHnVsc68Jk0i7orkOWZJzhWdXWrGQvl | https://drive.google.com/open?id=1UkLuVRUB3zWG___TNr5nBTRcku7UPlQh |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL022/25 | 2025-07-21 15:19 | operation@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | APRU5091041 |  |  | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-21 16:18 | 2025-07-11 |  |  |  |  | APRU5091041 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/12 br | 13.3/13.4/13.3 | 428/428/428 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1zmyzN5yUWOfFq6aChU9IYdBAKOSXcFSi | https://drive.google.com/open?id=1zHLJbsPACtoY4NOObX-62zSbsi27Avh8 |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL023/25 | 2025-07-21 15:24 | operation@crystalgroup.in | HETERO UNIT 3 | YUGANDHAR REDDY | 9100071906 | NA | CXRU1030427 |  |  | yugandhar.s@hetro.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-07-21 16:25 | 11/07/0025 |  |  |  |  | CXRU1030427 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/178 | 9.9/9.9/9.9 | 407/408/407 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=19J1zpwNdjuuXbxJ6xEHGqhdXm_upnzDu | https://drive.google.com/open?id=1a_XORBXBVvR6Nc4_3wSsUEu9GKToWjBx |  | 101 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL024/25 | 2025-07-21 15:32 | crm@crystalgroup.in | Royal Bhutan Army | Lt Col Kuenzang | +975 17677064 | NA | CICU1799860 | Motherboard not working |  | NA | Bhutan | Complete Breakdown | Motherboard not working | Call | PUSHPA MAM | 2025-07-22 18:13 | service@crystalgroup.in | Royal Bhutan Army | CICU1799860 | 20RF | THERMOKING MP4000 | SERVICE-ON CALL | SALE | CHARGEABLE | Unit not working | Temporary runned in bypass mode, currently under observation | after observation | will confirm after observation. | Unit Not working due to power issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL024%2F25 | TK MP4000 | TK-MP4000 | NA | NA | NA | NEW | NA | SHAHBUDDIN | No | Motherboard not working | 2025-07-23 09:26 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-23 09:26 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-23 09:28 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-23 12:24 | 2025-07-23 |  |  |  |  | CICU1799860 |  |  |  | Thermo king | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18 br | 10.2/10 3/10.3 | 388/387/387 | Not done | call from client unit not working | secured loose harness and checked main power voltage....parameters .. | Yes | https://drive.google.com/open?id=15zy7tfrvs3k15opexs9ZnFanWdyeqfL- | https://drive.google.com/open?id=1aN4sSrFOH2vwsgzj_LoyFNWsfHkiTdOJ |  | NA | No | No | Can be done on next PM | na | Power module for stand by . Old Power module some times current draw like increase or decrease | technician@crystalgroup.in | REEFER
JUL025/25 | 2025-07-21 18:47 | crm@crystalgroup.in | ISKON | Ambadas | 7021659217 | NA | Site Cabin 64 | REPAIRS & REPLACEMENT |  | NA | Mumbai | Running with issues | Repair requried | Call | Pushpa Mam | 2025-07-22 17:49 | service@crystalgroup.in | ISKON | Site Cabin 64 | Customised Cabin | NA | REPAIR | SALE | CHARGEABLE | Floor Damage | Need to inspect the unit | NA | will confirm after inspection | Floor Damage | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL025%2F25 | NO | NA | NA | NA | NA | NEW | NA | AKSHAY | Yes | REPAIRS & REPLACEMENT | 2025-07-28 14:10 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-28 14:17 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-28 14:18 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-28 14:20 | [54 empty] | crm@crystalgroup.in | DRY/Others
JUL026/25 | 2025-07-22 17:14 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | 7259366532 | Madhusoodhana | NA | PCIU6008328 | Need to arrange spares. |  | NA | Bidar | Complete Breakdown | Controller, Transformer ,Display needs to arranged | Email | Harshali | 2025-07-23 10:37 | service@crystalgroup.in | Sai Life Science | PCIU6008328 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Unit not working. | need to replace controller, display, also have to check the transformer. | Controller Decos 3d, Transformer & display | Yes | Unit not working due to controller & display defective. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL026%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | JSGA622340291 | RAMESH | Yes | Need to arrange spares. | 2025-07-23 17:07 | crm@crystalgroup.in | YES | IN115 | 2025-07-22 | Spares, Paid | Sai Life Science | BIDAR | PCIU6008328 | SITE | PAID | DAIKIN | 2025-07-30 17:55 | crm@crystalgroup.in | YES | IN115 | YES | https://drive.google.com/open?id=1gMQqq9b8pbyDPdu7IvyqbPC6AyGLCECk | Vendor | 2025-07-30 17:58 | crm@crystalgroup.in | YES | IN115 | COURIER | NA | Dolphin |  | https://drive.google.com/open?id=1PTqgaN0VRe50ZEP3yIliRWOiH3c1MOkK |  | 2025-08-02 09:19 | 2025-07-30 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 1200 | 8.4 8.4 8.4 | 395 395 395 | Not done | This unit controller and display on was not getting on. | Controller, display, transfarmar replace | No | https://drive.google.com/open?id=1oJ4Kl-0080DM8NWAuxUH3Ra7HRtQQjmx | https://drive.google.com/open?id=1M2YPQNHPQZ-NiUSXJlrwBuu0HgIryAmy |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL027/25 | 2025-07-22 18:03 | crm@crystalgroup.in | Earl Corvus Habitat | Pramod Kumar | NA | NA | CICU1938143 | FLUCTUATIONS IN TEMEPRATURE |  | Pramod.Kumar@emcure.com | Jammu | Running with issues | Our limit is 2-8 Degree c Spikes has highlighted as mentioned . Max Temp =9.8 degree c Min. temp = - 40 degree c the attached report of data logger from 11.07.2025 to 15.07.2025 . Spikes has highlighted as mentioned . Max Temp = 13.8 degree c Min. temp = 1.9 degree c Please help to resolve the issue on priority. | Email | Pushpa Mam | 2025-07-30 12:57 | service@crystalgroup.in | EmCure | CICU1938143 | 20RF | THERMOKING MP3000 | SERVICE-AT SITE | SALE | CHARGEABLE | set point changing automatically | controller already sent with configuration | software version | software required | set point changing automatically | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL027%2F25 | THERMOKING MP-3000 | TK-MP3000 | NA | NA | NA | NEW | NA | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE | 2025-10-20 10:35 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 10:35 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 10:36 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-03 14:40 | 2025-11-03 |  |  |  |  | Cicu1938143 |  |  |  | Thermo king | On call | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | Na | Not done | Na | Unit working fine | No | https://drive.google.com/open?id=1gNT06T1FT_VkDeqrmLocBC1f_t8HCB8n | https://drive.google.com/open?id=1x36szE9r0cEUjy_fTgY9TntCBxYU9Vum |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL028/25 | 2025-07-23 15:21 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusudhan | 72593 66532 | NA | PICU6032622 |  |  | madhusudhan.k@sailife.com | Bidar | Preventive Maintenance |  | Email | PUSHPA MAM | [54 empty] | 2025-08-02 16:32 | 2025-07-22 |  |  |  |  | PICU6032622 |  |  |  | Daikin | 22.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 1200 | 8.6 8.6 8.6 | 415 415 415 | Short | Pm due and general inspection done | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1xiI8b0V8DXYEN-_B9tEwc_6FxAC-uJ-M | https://drive.google.com/open?id=1P8GXaETgbL-fxvHiucAPNoBoL5Rar9ad |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL029/25 | 2025-07-23 15:23 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | MADHUSUDHAN | 7259366532 | NA | TITU9930032 |  |  | madhusudhan.k@sailife.com | Bidar | Preventive Maintenance |  | Email | PUSHPA MAM | [54 empty] | 2025-08-02 16:22 | 2025-07-22 |  |  |  |  | TITU9930032 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1100 | 8.6 8.6 8.6 | 415 415 415 | Short | Pm due and general inspection done | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1zouq4RjdJEysUnJQzVacYlO2Kia_vbWt | https://drive.google.com/open?id=1J2k-ebl1cbVt7WQGoh4ygb-ifsrO0dR5 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL030/25 | 2025-07-24 15:17 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Arun Bhand | 7709240073 | Manager-Formulation / Packing | CICU2093992 | SERVICING |  | Arun.Bhand@gennova.bio | Pune | AMC |  | Email | Pushpa Mam | [54 empty] | 2025-07-27 15:42 | 2025-07-25 |  |  |  |  | CICU2093992 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/20br | 9.9/9.8/9.9 | 416/415/415 | Short | PM due | PM completed | No | https://drive.google.com/open?id=1stxoHucCqiOpI0jBFCurlb8MutrKo-ZF | https://drive.google.com/open?id=1wYHjUxhEfCxv3n_1vSle0NtKrx9e3ukC |  | pune | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL031/25 | 2025-07-24 15:34 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | saleem | 8217399465 | Executive | PCIU-6032622 |  |  | NA | Bidar | Preventive Maintenance |  | Call | Rameez | [54 empty] | 2025-08-02 15:48 | 2025-07-22 |  |  |  |  | PCIU-6032622 |  |  |  | Daikin | 22.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 1100 | 7.9 7.9 7.9 | 415 415 415 | Short | Pm due and general inspection | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1Ua3XITRJ4Dif53edPn_BcfQMZUhPaa5p | https://drive.google.com/open?id=1NxBV5V-TaP0nmuD3lyb4m7rFpBX1Dj4v |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL032/25 | 2025-07-24 15:35 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Arun Bhand | 7709240073 | Manager-Formulation / Packing | CICU2094005 | SERVICING |  | Arun.Bhand@gennova.bio | Pune | AMC |  | Email | Pushpa Mam | [54 empty] | 2025-07-27 15:38 | 2025-07-25 |  |  |  |  | CICU2094005 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19br | 9.8/9.9/9.8 | 415/416/415 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1U1aMFeu2HALCq31n0MC3FGsyYRftL_3_ | https://drive.google.com/open?id=1gYviZsopbwC8Uay_JjEn1IOQ7m0WJi39 |  | pune | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL033/25 | 2025-07-24 15:40 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | saleem | 8217399165 | 8217399165 | PCIU6034374 |  |  | na | Bidar | Preventive Maintenance |  | Call | Rameez | 2025-07-25 10:39 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6034374 | 40FT STD RF | Daikin | SERVICE-AT SITE | SALE | CHARGEABLE | General Inspection done | NA |  | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL033%2F25 | Daikin | DAIKIN | NA | NA | NA | USED | NA | RAMESH | No | [30 empty] | 2025-07-25 11:08 | 2025-07-21 |  |  |  |  | PICU6034374 |  |  |  | Daikin | -15 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2.8/ 17.2 | 7.9/8.2/8.5 | 415/419/423 | Short | PM DONE AND GENERAL INSPECTION. | PM SERVICE AND ELECTRICAL AUDIT COMPLETE WITH CHECKED UNIT OPREATION ETC. ALL UNIT WORKING FINE. | No | https://drive.google.com/open?id=17604L2JNsVvYHbTVd5saxxxhbmeTR2fv | https://drive.google.com/open?id=156CL9dzicxx1Wy46Zs8c6lzc-R2Rebs3 |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUL034/25 | 2025-07-24 15:49 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | HDMU5542114 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | RAMEEZ | [54 empty] | 2025-07-25 11:44 | 2025-07-22 |  |  |  |  | HDMU552114 |  |  |  | Carrier | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4 | 17.6 | 395/398/401 | Short | PM DONE | PM SERVICE COMPLETE AND UNIT CHECK OPREATION. ALL UNIT WORKING FINE | No | https://drive.google.com/open?id=14x96CYNG2uiixADeUVqkTy_dleMCSkyj | https://drive.google.com/open?id=1fQ_NIt6wqSFYJny7az2JgixePeNBiBsV |  | NA | No | No | Can be done on next PM | NA | NA | crm@crystalgroup.in | REEFER
JUL035/25 | 2025-07-24 15:59 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | 7709240073 | 7709240073 | Manager-Formulation / Packing | CICU2094010 | SERVICING |  | Arun.Bhand@gennova.bio | Pune | AMC |  | Email | PUSHPA MAM | [54 empty] | 2025-07-27 15:32 | 2025-07-25 |  |  |  |  | CICU2094010 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/21br | 9.9/9.9/9.8 | 424/415/414 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1Jm40Mmh3vTvPmAIW3T6VLVbR4cSqim8F | https://drive.google.com/open?id=1M-f1uLVrA2_6UMZgf_0_U1ppiNvydA2S |  | pune | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL036/25 | 2025-07-24 16:03 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Arun Bhand | 7709240073 | Manager-Formulation / Packing | CICU2094026 | SERVICING |  | Arun.Bhand@gennova.bio | Pune | AMC |  | Email | PUSHPA MAM | [54 empty] | 2025-07-27 15:27 | 2025-07-25 |  |  |  |  | CICU2094026 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19br | 9.9/9.8/9.8 | 415/416/415 | Short | PM due | PM Complited | No | https://drive.google.com/open?id=1q446XoMzpGmAmRQKLBjabhneGZpK0Znu | https://drive.google.com/open?id=1tWqIOLBSjKRuPdvJlfvByOT_BSEA1RgG |  | pune | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL037/25 | 2025-07-24 16:17 | crm@crystalgroup.in | Gennova Biopharmaceuticals Ltd | Arun Bhand | 7709240073 | Manager-Formulation / Packing | CICU1937152 | SERVICING |  | Arun.Bhand@gennova.bio | Pune | AMC |  | Email | PUSHPA MAM | [54 empty] | 2025-07-27 15:16 | 2025-07-25 |  |  |  |  | CICU1938565 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/.9/220/220 | 9.9/10.3/9.8/10.4/9.7/10.5 | 415/416/416 | Short | PM due | PM servicec ompleted | No | https://drive.google.com/open?id=1OQ0tcFQJuyeZPcCWN5D2w8ZIeyVE5dhR | https://drive.google.com/open?id=1NYXAujQf0d9ykUCouoqlY6WyMiF3SMa- |  | pune | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
JUL038/25 | 2025-07-24 16:23 | crm@crystalgroup.in | Dr. Reddy's FTO-9 | Pathivada Krishnarao | 94925 45452 | NA | TRIU6616969 | Defrosting Continuously |  | NA | Vishakapatnam | Running with issues |  | Call | HARSHALI | 2025-07-30 14:25 | service@crystalgroup.in | Dr. Reddy's FTO-9 | TRIU6616969 | 20RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | temp not maintaining | need to visit | - | will confirm after inspection | temp not maintaining | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL038%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA622340507 | SITARAM | Yes | Defrosting Continuously | 2025-09-30 11:31 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-30 11:32 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-30 11:33 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-30 11:45 | 2025-07-25 |  |  |  |  | TRIU6616969 |  |  |  | Carrier | 5.0'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 2.5b, 14.5B | Not applicable | 405405405 | Not done | performed PM service. Initial check showed the unit was within normal range, but the customer reported occasional temperature spikes and slow pull-down times. | After detailed inspection, the supply recorder sensor was found to be defective need to replace. The unit is functioning correctly and pulling temperature properly during the -18°C test. The unit is operating normally. | Yes | https://drive.google.com/open?id=1BraZsgCI9ZEGkG8uQPTzFjTcOtSiccSK | https://drive.google.com/open?id=12LaZvspFnHHMonDijZ_hfEuKkJF8ZU-q |  | TRIP106 | No | Yes | Urgent | Na | Supply recoder sensor | technician@crystalgroup.in | REEFER
JUL039/25 | 2025-07-24 16:26 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | GESU9460634 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | rameez | [54 empty] | 2025-08-02 15:37 | 2025-07-22 |  |  |  |  | GESU9460634 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 11.6 bar | 6.3 6.3 6.3 | 415 415 415 | Short | Pm due and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1HP7O22-BpR0joQFkuQlot5tc9gBrYAPG | https://drive.google.com/open?id=1SxSTRbC4TPmHuDNFyyo7ttfmHqYpxGrd |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL040/25 | 2025-07-25 12:05 | crm@crystalgroup.in | Qwik Supply | Mohit Rai | 9023419864 | NA | TDRU5815332 |  |  | mohit2.rai@qwik.co.in | Ahmedabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 14:49 | 2025-07-21 |  |  |  |  | TDRU5815332 |  |  |  | Carrier | -21C | Clean | Clean | https://drive.google.com/open?id=1j21CEu0Tg6qErF9LIi-W5XL-uOVcsLCo | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 1.2 bar discharge 14.6 bar | R 13.8A B 13.8A Y 13.6A | 408 V 408V 408V | Not done | PM | Washed the condenser coil | No | https://drive.google.com/open?id=1N0YqgHH9vuD9n39qn9HSnt4YTFChIVGE | https://drive.google.com/open?id=1AChPZsMuehdxv-LnDhz4jacTp59cYtdP |  | N/A | No | No | Can be done on next PM | N/A | N/A | technician@crystalgroup.in | REEFER
JUL041/25 | 2025-07-25 14:50 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | NA | GESU9460634 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 15:20 | 2025-07-21 |  |  |  |  | GESU9460634 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 12.6 bar | 6.3 6.3 6.3 | 415 415 415 | Short | Pm due and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running,, | No | https://drive.google.com/open?id=1XvZuoNqZKy_P7k9LWZrrQzskExrOKf5i | https://drive.google.com/open?id=189FuCa2uykS-EWCcK3VDk7V_d0ojD7WZ |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL042/25 | 2025-07-25 15:27 | operation@crystalgroup.in | Zepto | Paras | 918882625720 | NA | KKFU6711832 | REPAIRS & REPLACEMENT |  | NA | Delhi | Running with issues | Contactor burnt | Call | Harshali | 2025-07-30 17:47 | service@crystalgroup.in | Zepto | KKFU6711832 | 40RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | unit has evp contactor burnt | client will replace the contactor | - | No | unit has evp contactor burnt | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL042%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA623040288 | SHAHBUDDIN | No | REPAIRS & REPLACEMENT | 2025-07-31 12:48 | crm@crystalgroup.in | NO | [9 empty] | 2025-07-31 12:48 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-31 12:49 | crm@crystalgroup.in | NO | [7 empty] | 2025-07-31 14:57 | 2025-07-25 |  |  |  |  | KKFU6711832 |  |  |  | Carrier | NA | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Short | Contactor was burned which was observed on Video call | Asked client to arrange contator at site | Yes | https://drive.google.com/open?id=1XZ0KrHNUwUewdEB0DQXDUWY4eiKkkm0S | https://drive.google.com/open?id=1QEVjEohCS1Jjv5KhrOI3DJfpRqtRvZcn |  | NA | No | No | Can be done on next PM | NA | Contator | crm@crystalgroup.in | REEFER
JUL043/25 | 2025-07-25 16:07 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusudhan | 72593 66532 | NA | GESU9460634 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 15:28 | 2025-07-22 |  |  |  |  | GESU9460634 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 11.6 bar | 6.3 6.3 6.3 | 415 415 415 | Short | Pm due and general inspection. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1TlBJG2R2_zoJ2r8Xm_tWpUDh0fCwQ2Uy | https://drive.google.com/open?id=184TiSMWWhfHnWg3OZEsg8wtZRb1EtlqU |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL044/25 | 2025-07-25 16:18 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | NA | TITU9930032 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 15:06 | 2025-07-22 |  |  |  |  | TITU9930032 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1200 | 8.2 8.2 8.2 | 412 412 412 | Not done | Pm service and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1IvArMK2RWBKairglKc2hvTumpkzOvJon | https://drive.google.com/open?id=1MKC_GC0drOtSi0FijJDCtKKSp73E7Gn8 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL045/25 | 2025-07-25 16:20 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | NA | PCIU6008328 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 14:51 | 2025-08-30 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10 1300 | 9.1 9.1 9.1 | 391 395 399 | Not done | Pm service and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running, | No | https://drive.google.com/open?id=1FUo_Kgq4wTFIFcEcCiNcUzP4nomg4tbG | https://drive.google.com/open?id=1cIWb4M9SKqMw8REICfGLom5KV6QVgWZ7 |  | TRIP110 | No | No | Can be done on next PM | Na | 0 | technician@crystalgroup.in | REEFER
JUL046/25 | 2025-07-25 16:28 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusudhan | 72593 66532 | NA | PCIU6031328 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 14:35 | 2025-07-22 |  |  |  |  | PCIU6031328 |  |  |  | Daikin | 22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1200 | 7.6 7.6 7.6 | 412 412 412 | Short | Pm due and general inspection done. | Pm service complete with unit operation and internal check, this unit power check , cricket breaker input and output voltage check, all contractor resistance check, all sensor reading,gas leval check, evo motor and condenser motor voltage, condenser coil clean,all found ok unit properly running,, | No | https://drive.google.com/open?id=1Lg17oUC2TuE7Q41lBq-ON7Q0DZC1J__A | https://drive.google.com/open?id=1SQTMr-kpBBhc613y3i3mqU84oID3Bo7k |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL047/25 | 2025-07-25 18:14 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | 9963198979 | NA | PCIU6006639 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:54 | 2025-07-24 |  |  |  |  | PCIU6006639 |  |  |  | Daikin | -2.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9psi 98ppsi | 8.9A 8.9A 8.9A | 410V 410V 410V | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | Yes | https://drive.google.com/open?id=1dqWbWB2ciyXBBQ6y_LYCVXC54bn79lqX | https://drive.google.com/open?id=1ykBWwd8bZKfcAKscoEearxask438eNWF |  | TRIP106 | No | No | Can be done on next PM | Na | SHEET KEY (KEYPAD) | technician@crystalgroup.in | REEFER
JUL048/25 | 2025-07-25 18:18 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | 9963198979 | NA | APRU5000210 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:50 | 2025-07-24 |  |  |  |  | APRU5000210 |  |  |  | Carrier | 27.7C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | In range | In range | 410v 410v 410v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | Yes | https://drive.google.com/open?id=1_t0TmNHT1rgxfsnMwoCrjFTTVhJx5h78 | https://drive.google.com/open?id=10vszW4DaCbHU3TLyNWTBUdKRoHqIeUlt |  | TRIP106 | No | No | Can be done on next PM | Na | KEYPAD | technician@crystalgroup.in | REEFER
JUL049/25 | 2025-07-25 18:23 | crm@crystalgroup.in | LAURAS UNIT 06 | SOMA | 9963198979 | NA | CICU1937445 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:47 | 2025-07-24 |  |  |  |  | CICU1937445 |  |  |  | Thermo king | -20.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 46 psi 1650 psi | 12.4A 12.4A 12.4A | 405v 405v 405v | Not done | Unit inspected, no issues found. Request raise by client | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1BXmPaLczcfukNOZ6Cw_wos191fuQkTxU | https://drive.google.com/open?id=1lRq1jWUgPX4EKdi2Zla6rjKYh0G5a5_Q |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL050/25 | 2025-07-25 18:25 | crm@crystalgroup.in | LAURUS UNIT -1 | NA | 9963198979 | NA | TITU9930011 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:42 | 2025-07-24 |  |  |  |  | TITU9930011 |  |  |  | Thermo king | 15.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | In range | In range | 410V 410V 410V | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=18YI7hp7jYtuGp4Nk_MaNuPZlXcHRoiDC | https://drive.google.com/open?id=1FeUHCYiGcni7uaKhlxth4dhBwm_C8T3u |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL051/25 | 2025-07-25 18:27 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | NA | 9963198979 | NA | CXRU1037308 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:38 | 2025-07-24 |  |  |  |  | CXRU1037308 |  |  |  | Daikin | 4.3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | In range | In range | 410V 410V 410V | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=10MrAbRq1qXGYwb-Hu3gHmOocwWyBGoSX | https://drive.google.com/open?id=1YofsDPmaqZnFk5ediW1P4BWgGEzPB8T6 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL052/25 | 2025-07-26 19:28 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | PCIU6016370 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 11:24 | 2025-07-24 |  |  |  |  | PCIU6016370 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1200 | 7.6 7.6 7.6 | 415 415 415 | Short | Pm service and general inspection done. | Power supply check, input output voltage check,all sensor reading check,gas leval,all contractor resistance check amp check evp motor condenser motor voltage check, condenser coil clean all found ok unit running properly . | No | https://drive.google.com/open?id=1rHi-NoNiC-99KAPz4Yb42R0zN4Y_KaHy | https://drive.google.com/open?id=1GFdkgub3OLxkW5hIeHtDMv146_Zly0UA |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL053/25 | 2025-07-26 19:31 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | APRU5091041 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 11:16 | 2025-07-24 |  |  |  |  | APRU5091041 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 13.2 bar | 12.3 12.4 12.3 | 415 415 415 | Short | Pm due and general inspection done. | Power supply check, input output voltage check,all sensor reading check,gas leval,all contractor resistance check amp check evp motor condenser motor voltage check, condenser coil clean all found ok unit running properly . | No | https://drive.google.com/open?id=12_XdSxkWTvkoTuzD6-n_n6kr8Hj2ARPX | https://drive.google.com/open?id=1ftG3Na4m9sthdIwuLpBM9yYZ-c1gEo70 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL054/25 | 2025-07-26 19:32 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1026520 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 11:03 | 2025-07-25 |  |  |  |  | CXRU1026520 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1200 | 8.1 8.1 8.1 | 415 415 415 | Short | Pm due and general inspection done | Power supply check, input output voltage check,all sensor reading check,gas leval,all contractor resistance check amp check evp motor condenser motor voltage check, condenser coil clean all found ok unit running properly | No | https://drive.google.com/open?id=1VIQoch8ddVocgM9I3YbKbwoO_PAfSMEv | https://drive.google.com/open?id=1cw-sNVUGnsUAicONj-7H8uKLpKq6NvEb |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL055/25 | 2025-07-26 19:34 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1030427 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 10:55 | 2025-07-24 |  |  |  |  | CXRU1030427 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 08 1200 | 7.9 7.9 7.9 | 415 415 415 | Short | Pm due and general inspection. | Power supply check, input output voltage check,all sensor reading check,gas leval,all contractor resistance check amp check evp motor condenser motor voltage check, condenser coil clean all found ok unit running properly | No | https://drive.google.com/open?id=19R0i4gsJvBfJMyGB8HnIzYh4vUxEAvhH | https://drive.google.com/open?id=11C59ildGxEF6Kpb27RBNj-8rxyli4UY6 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL056/25 | 2025-07-26 19:36 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1326276 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 10:12 | 2025-07-24 |  |  |  |  | CXRU1326276 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 14.5 bar | 6.8 6.8 6.8 | 415 415 415 | Short | Pm service and general inspection done | Power supply check, input output voltage check,all sensor reading check,gas leval,all contractor resistance check amp check evp motor condenser motor voltage check, condenser coil clean all found ok unit running properly . | No | https://drive.google.com/open?id=1lEhzjAZMyIS3NmMIxseD14560xhoQRSa | https://drive.google.com/open?id=1XJ7gavP062zdtjdpv0zorEJVjavDmPP9 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL057/25 | 2025-07-26 19:37 | crm@crystalgroup.in | Hetero Labs Ltd - unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1550769 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 09:52 | 2025-07-24 |  |  |  |  | CXRU1550769 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4 16.5 bar | 6.9 6.9 6.9 | 415 415 415 | Short | This unit compressor defective not working | Compressor replace R134a gas charge Drier filter replace | No | https://drive.google.com/open?id=1TPgPBwxkIIowpLtVu_mm6YbhVRYLGBi4 | https://drive.google.com/open?id=1nZplGm8W_c6P9BzK7x-lkuO__IZk2m88 |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL058/25 | 2025-07-28 11:04 | crm@crystalgroup.in | Jubliant Consumer Pvt Ltd | JAYANT | 7827984949 | NA | GRMU3607418 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Delhi | Running with issues | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Call | PUSHPA MAM | 2025-07-30 17:55 | service@crystalgroup.in | JUBILANT | GRMU3607418 | 20RF | DAIKIN | SERVICE-ON CALL | LEASE | FOC | as per customer temperature isn't falling | during observation on-call unit found working fine | na | No | during observation on-call unit found working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL058%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-08-01 16:33 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-01 16:34 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-01 16:35 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-08 15:48 | 2025-07-25 |  |  |  |  | GRMU3607418 |  |  |  | Daikin | -25.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | Unit is working fine without any alarms or any other issues. | NAT | No | https://drive.google.com/open?id=1Lx7N-8nCsHoAyqtN89cXU353NASmJ4D7 | https://drive.google.com/open?id=1PL31GZHDyEmljAtaWicx-BYqJNTFIYBC |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JUL059/25 | 2025-07-28 11:13 | crm@crystalgroup.in | ITC Ltd | Khaja | 9493514469 | NA | MYRU4519748 | FLUCTUATIONS IN TEMEPRATURE |  | Tadikonda.Sivakumar@itc.in | Bapatla | Running with issues | Container got malfunctioning | Email | HARSHALI | 2025-08-04 15:11 | service@crystalgroup.in | ITC Ltd | MYRU4519748 | 40RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | temperature not falling | NEED TO ARRANGE TECHNICIAN AT SITE | NA | WILL CONFIRM AFTER ATTENDANCE | TEMP NOT FALLING & WHITE DISPLAY NOT VISIBLE PROPERLY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL059%2F25 | DAIKIN | DAIKIN | M003143 | NA | NA | NA | JSGA623040176 | RAMESH | Yes | FLUCTUATIONS IN TEMEPRATURE | 2025-08-08 12:06 | crm@crystalgroup.in | NO | [9 empty] | 2025-08-08 12:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-08-08 12:08 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-11 10:58 | 2025-08-07 |  |  |  |  | MYRU4519748 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Unit breakdown | Unit breakdown | Unit breakdown | Not done | Unit breakdown | I have checked voltage wiring and sensor resistance and found the inlet and outlet sensor and suction sensor reading out of range need to be replaced and will observation again and to PTI | Yes | https://drive.google.com/open?id=1WTuSMH5ugKfhXdd6Ui5Gwi89DhT2zhM2 | https://drive.google.com/open?id=14sJL3C2USwHN1mwz6CMDTJWSt6PZR3ka |  | TRIP107 | Yes | No | Urgent | Yas | Yas | technician@crystalgroup.in | REEFER
JUL060/25 | 2025-07-28 11:59 | crm@crystalgroup.in | Dr reddy cto 3 | ASHOK | 8978577878 | NA | GSOU6384240 | COMPRESSOR NEED TO BE CHECKED |  | ashoky@drreddys.com | Hyderabad | Running with issues | COMPRESSOR NEED TO BE CHECKED | Email | HARSHALI | 2025-07-30 18:08 | service@crystalgroup.in | Dr reddy cto 3 | GSOU6384240 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | unit has evp motor defective (three phase), running in bypass mode | need to replace evp motor | Evp motor three phase | Yes | evp motor in bypass mode (three phase) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL060%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA622340472 | RAMESH | Yes | COMPRESSOR NEED TO BE CHECKED | 2025-10-03 10:51 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-03 11:20 | crm@crystalgroup.in | YES | NA | YES |  | Stock | 2025-10-03 11:21 | crm@crystalgroup.in | YES | NA | TECHNICIAN |  |  | Ramesh |  |  | 2025-10-09 17:20 | 04/09/0025 |  |  |  |  | GSOU6384240 |  |  |  | Daikin | 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/180psig | 9.9/9.9/9.8 | 406407/406 v | Short | Unit Instalationcompleted | After replaced reefer unit and wiring job completed with test unit & found working as normal | No | https://drive.google.com/open?id=1exAhwE-JVVX1S1R4RBIZy4WfTaVcTk-t | https://drive.google.com/open?id=1qZXoh2lHxc2y2UsFQMPsSvHDfROxqQTt |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL061/25 | 2025-07-29 10:31 | crm@crystalgroup.in | Crystal | Shubham Tank | 7624011599 | NA | PCIU6007065 | Evaporator Motor Stuck |  | service@crystalgroup.in | JNPT | Running with issues | PCIU6007065 has an evaporator motor stuck, the same has been repaired | Email | PUSHPA MAM | 2025-07-29 11:29 | crm@crystalgroup.in | Crystal Yard | PCIU6007065 | 40FT STD RF | DAIKIN | REPAIR | STOCK | CHARGEABLE | Evaporator motor stuck | NA | NA | REPAIR | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL061%2F25 | Daikin | DAIKIN | NA | NA | NA | Refurbished | NA | SHAHBUDDIN | No | Evaporator Motor Stuck | 2025-07-29 12:40 | crm@crystalgroup.in | YES | IN120 | 2025-07-29 | FOC | Crystal Yard | JNPT | PCIU6007065 | DEPOT | FOC | DAIKIN | 2025-07-29 12:41 | crm@crystalgroup.in | NO |  |  |  |  | 2025-07-29 12:42 | crm@crystalgroup.in | NO
JUL062/25 | 2025-07-29 12:50 | crm@crystalgroup.in | Tianish | Murthy | 9441013280 | NA | TRLU1741601 | Spares requried on site |  | NA | Vizianagaram | Complete Breakdown | Spares requried on site -Compressor -Rellay Board -Display -Gas | Call | PUSHPA MAM | 2025-07-29 12:55 | crm@crystalgroup.in | Tianish | TRLU174160 | 40FT STD RF | Thermo King | SERVICE-AT SITE | LEASE | FOC | Spares requrierd on sites | NA | Compressor Rellay Board DISPLAY | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL062%2F25 | NA | TK-MP3000 | NA | NA | NA | USED | NA | SITARAM | Yes | Spares requried on site | 2025-08-07 17:39 | crm@crystalgroup.in | YES | IN121 | 2025-07-29 | Spares | Tianish | Vizag | TRLU174160 | SITE | PAID | TK-MP3000 | 2025-08-08 14:53 | crm@crystalgroup.in | YES | IN121 | YES | https://drive.google.com/open?id=1HBNX7lb7Osoz6lnNNnavNCm2Qme1D-wx, https://drive.google.com/open?id=1aH2tP2eWn5XBp96YHzUZbNQHSaeDA-9- | Stock and Vendor | 2025-08-08 14:55 | crm@crystalgroup.in | YES | IN121 | COURIER | 1445 | Dolphin |  | https://drive.google.com/open?id=1WeurW6d5eoB1QDQv7O34eB73rOOfL5yS |  | 2025-08-11 09:37 | 2025-08-06 |  |  |  |  | TRLU174160 |  |  |  | Thermo king | +18'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2.1 13.2 | 12.1 12.1 12.1 | 399 399 399 | Not done | Post replacement unit achieved -18'c within 4 hours. Now running within set temperature | Compressor, display, gas charge, relay bord has been replaced. Unit run with -18'c and reach within 4 hours -18.9'c. unit running in good condition | No | https://drive.google.com/open?id=1-gMOYQc64ffCTxmkLBRkzLrPd92UV7cL | https://drive.google.com/open?id=1H7QqvaQT5jWwgbCn8XBYCyJeI_253y0G |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL063/25 | 2025-07-29 16:24 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | SUDU6257274 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:34 | 2025-07-25 |  |  |  |  | SUDU6257274 |  |  |  | Carrier | 3.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.96b 11.26b | 8.2a 8.2A 8.2A | 410V 410V 410V | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1o6i2FtiCreUv0iYJTDfg9KYKkQ3SIzxH | https://drive.google.com/open?id=1Bje8ks_AAYZOvq4njDjILUoHo1X1dBeY |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL064/25 | 2025-07-29 16:26 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | KKFU6711724 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 22:01 | 2025-07-25 |  |  |  |  | KKFU6711724 |  |  |  | Carrier | 20C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4.9bar 9.3bar | Not applicable | 425v 425v 425v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1CYtfKIj8bv4tGJhQf94ihdM1UFRpJ1sC | https://drive.google.com/open?id=1H0DIewC1bMJTsQ8zIsB7YpYOIX-oTRfZ |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL065/25 | 2025-07-29 16:29 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | TDRU7153256 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:30 | 2025-07-25 |  |  |  |  | TDRU7153256 |  |  |  | Daikin | 4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 58psi 1038psi | 9.6A 9.6A 9.6A | 410v 410v 410v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1R0esKOJnfk2JJGIgX7eU783rb17lpAxG | https://drive.google.com/open?id=1sTzLUOAGAvO1KrATKh1224BQVw65_mmG |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL066/25 | 2025-07-29 16:30 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | BMDU9784137 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:27 | 2025-07-25 |  |  |  |  | BMDU9784137 |  |  |  | Daikin | No power connection by factory | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | No power connection | No power connection | No power connection | Not done | No power connection by client | No power connection | No | https://drive.google.com/open?id=15RJG0IQUdhSrbDixlY2jAhLgA2ptjXga | https://drive.google.com/open?id=1Qbr8RTP4hI_WHQiwFgZVb7uK4hRCuH45 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL067/25 | 2025-07-29 16:31 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | APRU5019340 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:24 | 2025-07-25 |  |  |  |  | APRU5019340 |  |  |  | Daikin | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | No power connection by factory | No power connection by factory | No power connection | Not done | No power connection by client | No power connection | No | https://drive.google.com/open?id=1k7ybIDCgLmgGsegkb50swLdKSssBq3vC | https://drive.google.com/open?id=14QY89DmtOddSdgKYNL0BjaGhwL_54KZt |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL068/25 | 2025-07-29 16:33 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | MYRU4505847 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 07:53 | 2025-08-25 |  |  |  |  | MYRU4505847 |  |  |  | Daikin | 21.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 451 790 | In range | 412v 412v 412v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1LS03IPubq37GzbeG7prb0-lqc3NtMsry | https://drive.google.com/open?id=1ZgxkKj1nRFzCmwPnhn0h9gJPFh4JBR88 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL069/25 | 2025-07-29 16:35 | crm@crystalgroup.in | Laurus Unit 3 | 9963198979 | SOMI REDDY | NA | KKFU6710760 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 08:16 | 2025-07-25 |  |  |  |  | KKFU6710760 |  |  |  | Daikin | 21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 251psi 790psi | 8.2A 8.2A 8.2A | 412v 412v 412v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1TYmOkVZ6lK5nl1cAkgVfyXMYhyDAEigI | https://drive.google.com/open?id=1qwjB1rcHdaKGpWEmuj9FG9iiNlOeZpex |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL070/25 | 2025-07-29 16:39 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | DFOU6120384 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:56 | 2025-07-25 |  |  |  |  | DFOU6120384 |  |  |  | Daikin | 20C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 98psi 1082psi | 9.2A 9.2A 9.2A | 418v 418v 418v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=16_UiVwJKeOfUO-6GLTUltQbHDHKxfAuZ | https://drive.google.com/open?id=11IfJIPBv7LfVK40GaJZxhspyNrHMgmWh |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL071/25 | 2025-07-29 16:42 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | MYRU4519115 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:52 | 2025-07-25 |  |  |  |  | MYRU4519115 |  |  |  | Daikin | 20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 53psi 924psi | 9A 9A 9A | 410v 410v 410v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1D1Oi5ztHV6W6HdL7CyDevUuZAsng4fHb | https://drive.google.com/open?id=1gVGHuCkxROsTeDrowL8c9xls75YNqlP1 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL072/25 | 2025-07-29 16:44 | crm@crystalgroup.in | Laurus Unit 3 | SOMI REDDY | 9963198979 | NA | TCLU1512290 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 15:35 | 2025-07-26 |  |  |  |  | TCLU1912290 |  |  |  | Daikin | -20.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 5 938 | Na | 414v 415v 415v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1xKlT209hELjyCVnbtCWpgtegIiK29uNV | https://drive.google.com/open?id=1ytEHS-LIppbdcEkwQw36w8Y4IThboj1A |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL073/25 | 2025-07-29 16:50 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | TITU9930222 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:34 | 2025-07-28 |  |  |  |  | TITU9930222 |  |  |  | Thermo king | 69.8F | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 730psi 1320psi | Nto applicable | 420v 420v 420v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=17mTwQvnKv_5LDRkqgkw3lU3-995hxyx8 | https://drive.google.com/open?id=1yP7D4w2wMpz9knSGWSK-DX8UnEC6Ip6f |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL074/25 | 2025-07-29 16:51 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 99081 27999 | NA | CRSU6101910 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:11 | 2025-07-28 |  |  |  |  | CRSU6101910 |  |  |  | Carrier | 22.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4.2b 11.6b | Not applicable | 420v 420v 420v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1A6ZmFgs_O6i8y7DtEzmgrn-iZsdEtNLF | https://drive.google.com/open?id=18V8Eqp8_llUC5hykMy2m3qGDIa9bRVEb |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL075/25 | 2025-07-29 17:13 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | GESU9454776 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:07 | 2025-07-28 |  |  |  |  | GESU9454776 |  |  |  | Carrier | 23.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 3.4b 8.8b | Not applicable | 410v 410v 410v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1uCpef4wRvWRQCYUPGhKNzMUO9P_f5L5Z | https://drive.google.com/open?id=1UlZ5pxJPdwakYzwZHP4NCMYBwNT3guhq |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL076/25 | 2025-07-29 17:16 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 99081 27999 | NA | PRGU4958724 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 11:18 | 2025-07-28 |  |  |  |  | GESU9454776 |  |  |  | Carrier | 23'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 3.4b, 8.2b | Not applicable | 410410410 | Not done | Pm service done | Working fine | No | https://drive.google.com/open?id=1XealPFecmqP8hH6M1tn9_AZObAkFw0ty | https://drive.google.com/open?id=1QOCKnZIehZRsiOjopYJLTPAbYhsX1HcW |  | TRIP106 | No | No | Can be done on next PM | Not | Nil | technician@crystalgroup.in | REEFER
JUL077/25 | 2025-07-29 17:18 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 99081 27999 | NA | GESU9529290 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 15:28 | 2025-07-28 |  |  |  |  | GESU9529290 |  |  |  | Carrier | 22.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 4.3B 9.1B | 4.3A 4.3A 4.3A | 410v 410v 410v | Not done | PM service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1nDnqtuxut_8qnW_azVwt0p6Ys9qTdJVr | https://drive.google.com/open?id=1K1a6UUfSOi05og0t1A86MyeAgXAekRhW |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL078/25 | 2025-07-29 17:21 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | MURTY | 9908127999 | NA | HDMU5584444 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:03 | 2025-07-28 |  |  |  |  | HDMU5584444 |  |  |  | Thermo king | 4.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5b 14.7b | 14.4A 14.4A 14.4A | 413v 413v 413v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1njskHKop7c-JoDOawvXP5x3RBJVviv4w | https://drive.google.com/open?id=1p1qNoK0UCSzDLD0XlsOiAv2WUcCZE0C- |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL079/25 | 2025-07-29 17:23 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | MURTHY | 99081 27999 | NA | HDMU5586473 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 21:00 | 2025-07-28 |  |  |  |  | HDMU5586473 |  |  |  | Thermo king | 23.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 70psi, 1220psi | 12.1A , 12.1A 12.1A | 413v 413v 413v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1Hcj-_CJjwVjuAVuoLit274jWE4eoqNFb | https://drive.google.com/open?id=1u8aOW0wtzd0NlQBEhis6l49sHr9G1ds8 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL080/25 | 2025-07-29 17:37 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 99081 27999 | NA | BMOU9782197 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 20:57 | 2025-07-28 |  |  |  |  | BMOU9782197 |  |  |  | Daikin | 23.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 237psi, 1513psi | 11.3A, 11.3A 11.3A | 410V410v, 410v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1BalHB_vgFiQe6s-pHC8rLKDzJKDnn180 | https://drive.google.com/open?id=19BJe2Y06IliukaxM6LOn0nPaxOuSnWki |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL081/25 | 2025-07-29 17:48 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 99081 27999 | NA | CXRU1031845 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-30 20:52 | 2025-07-28 |  |  |  |  | CXRU1031845 |  |  |  | Daikin | 23.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 93 psi, 986 psi | 410v, 410v,410v | 8.5A, 8.5A , 8.5A | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1SFH5sPpyCY8Qm0tIAcF4sPazCh0N6qhQ | https://drive.google.com/open?id=1NuuZ4BihboMF0vFLJqbLBRL9XjTCUleN |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL082/25 | 2025-07-29 18:20 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | NA | CXRU1036533 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | 2025-07-30 18:23 | service@crystalgroup.in | Lauras Lab Unit 2 | CXRU1036533 | 40RF | DAIKIN | PREVENTIVE MAINTENANCE | LEASE | AMC | PM SERVICE DUE | PM DONE | NA | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL082%2F25 | DAIKIN | DAIKIN | M000451 | NA | NA | USED | JSGA623040306 | SITARAM | Yes | [30 empty] | 2025-07-31 15:25 | 2025-07-28 |  |  |  |  | CXRU1036533 |  |  |  | Daikin | 21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 108 1053 | 8.7A 8.7A 8.7A | 413v 413v 413v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1IluateAObSnb4W_WG31WyADizSuqyrBV | https://drive.google.com/open?id=1IkwIX7IKEjsFDj2pgwGcKuksEy9zYoYo |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL083/25 | 2025-07-30 12:28 | crm@crystalgroup.in | Hetero Unit 5 | SHYAM SUNDAR | 9154266430 | NA | SUDU6218004 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Hyderabad | Running with issues |  | Call | PUSHPA MAM | 2025-08-14 12:02 | service@crystalgroup.in | HETERO UNIT 5 | SUDU6218004 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | NEED TO INSTALL MAN TRAP ALARM | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL083%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | RAMESH | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-20 10:37 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 10:37 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 10:38 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-03 12:55 | 2025-09-02 |  |  |  |  | SUDU6218004 |  |  |  | Daikin | 5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B, 17.4B | 9.8a | 410V | Short | SERVICE CALL | UNIT WOKING FINE ALL READING WERE OK | No | https://drive.google.com/open?id=1L9zwyd4BVnQ1d0yfE80CLmUfPpIz0G0S | https://drive.google.com/open?id=1e7NfFWR5wNCZfuj-bWu1pE6c-YoMHcUf |  | NA | No | No | Can be done on next PM | NA | NA | service@crystalgroup.in | REEFER
JUL084/25 | 2025-07-30 12:34 | crm@crystalgroup.in | PI Industries Limited | NIRAKAR DAS | 9512030663 | NA | CXRU1035856 | Temp issue |  | NA | Bharuch | Running with issues |  | Call | PUSHPA MAM | 2025-08-11 17:35 | service@crystalgroup.in | PI Industries | CXRU1035856 | 40RF | DAIKIN | SERVICE-AT SITE | SALE | CHARGEABLE | EVP MOTOR DEFECTIVE | need to replace evp motor | EVP MOTOR | Yes | evp motor defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL084%2F25 | DAIKIN | DAIKIN | M000552 | K31412143316 | DECOS 3F 2553 / 1 | USED | NA | SHAHBUDDIN | Yes | Temp issue | 2025-09-29 17:11 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-29 17:12 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-29 17:12 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-17 10:04 | 2025-11-02 |  |  |  |  | CXRU1035856 |  |  |  | Carrier | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | On call | Na | Not done | Na | As per our engineer last visit , unit working fine , | No | https://drive.google.com/open?id=1jM8L4GcnStnwQBEEOF6iUR93X22hQRDx | https://drive.google.com/open?id=17mY3r0EeRA3R2-znPsygaHpI5ZqtU4yY |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL085/25 | 2025-07-30 12:50 | crm@crystalgroup.in | DR REDDY CTO 06 | Sai Babu | 9618849181 | NA | CXRU1033616 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-07-31 15:20 | 2025-07-30 |  |  |  |  | CXRU1033616 |  |  |  | Daikin | 4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -7psi 1096psi | 8.2A 8.2A 8.2A | 396V 396V 396V | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1DniQNlgkSseBrCjYd_Oq7sy_CSxOmN4F | https://drive.google.com/open?id=1h7F5Sc78Bm_nFs5a4UrbclOiW07PByVY |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
JUL086/25 | 2025-07-30 13:56 | crm@crystalgroup.in | DR REDDY CTO 06 | Sai Babu | 96188 49181 | NA | TRIU6616969 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 07:48 | 2025-08-25 |  |  |  |  | TRIU6616969 |  |  |  | Carrier | 5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 1.6b 14.5b | Not | 405v 405v 405v | Not done | Customer complaint - pm service and general inspection done and unit was in range but the customer reported occasionally temperature spike slow decrease | After detailed inspection the supply recoder sensor was found out of range unit has been thoroughly checked and tested with -18'c .its function correctly. Supply sensor need to be replace | Yes | https://drive.google.com/open?id=1YPWsNNlMDuaDRkzhWzYKOv30UscPGfzH | https://drive.google.com/open?id=1feTRWf3dprJxFMvBQhJNC3n--_uXcYdA |  | TRIP106 | No | No | Can be done on next PM | Supply sensor need to replace | Supply sensor | technician@crystalgroup.in | REEFER
JUL087/25 | 2025-07-30 17:38 | crm@crystalgroup.in | Balaji Enterprises | Suman Ghosh | 8585006401 | NA | TRIU6616911 | Motor not working |  | NA | Begusarai | Running with issues | During installation it was found that one stand by motor is not functioning which was confirmed by service engineer during video call. | Email | PUSHPA MAM | 2025-08-02 16:00 | service@crystalgroup.in | Balaji Enterprises | TRIU6616911 | 20RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | EVP MOTOR NOT WORKING | BYPASSED ONE EVP MOTOR & UNDER TROUBLESHOOTING |  | CONFIRMATION PENDING | EVP MOTOR NOT WORKING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL087%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | M3X60329564 | NA | Used | NA | SHAHBUDDIN | Yes | Motor not working | 2025-09-29 17:17 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-29 17:17 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-29 17:18 | crm@crystalgroup.in | NO
JUL088/25 | 2025-07-31 15:52 | crm@crystalgroup.in | WOCKHARDT | ANIL PUND | 9049534108 | NA | JXLU517262 | Sensor faulty |  | NA | Aurangabad | Running with issues |  | Call | PUSHPA MAM | 2025-08-14 11:51 | service@crystalgroup.in | WOCKHARDT | JXLU517262 | 40RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | UNIT HAS CONTROLLER & SENSORS DEFECTIVE | NA | CONTROLLER DECOS 3D & SENSORS | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=JUL088%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | No | Sensor faulty | 2025-09-30 11:50 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-15 10:55 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 14:35 | crm@crystalgroup.in | NO
JUL089/25 | 2025-07-31 20:51 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | Subha Reddy | 8106009300 | NA | BMOU9787239 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 08:01 | 2025-08-31 |  |  |  |  | BMOU9787239 |  |  |  | Daikin | 3.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Not visible | Not visible | Not visible | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly control pannel with sheet key found damage and blank condition need to replace | No | https://drive.google.com/open?id=13E1GEY_Y2xL-Olxh7Gy4XUO7vWqTwbjD | https://drive.google.com/open?id=1UP8aeYf13rGd9bE9EIJMc_k69zsfWhrG |  | TRIP106 | Yes | No | Can be done on next PM | Control pannel with sheet key need to replace | Control pannel with sheet key | technician@crystalgroup.in | REEFER
JUL090/25 | 2025-07-31 21:01 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | SUBHA REDDY | 8106009300 | NA | ARCU4530720 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 08:10 | 2025-08-31 |  |  |  |  | ARCU4530720 |  |  |  | Carrier | 3.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Not visible | Not visible | Not visible | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly, found display blank condition need to replace | Yes | https://drive.google.com/open?id=1s1u8tnn-EFp-3MSzZINwRSMG9tWM9TXm | https://drive.google.com/open?id=1LLEqriNDT41LvacMTNv2HTyEohULDza8 |  | TRIP106 | No | No | Can be done on next PM | Na | Display need to replace | technician@crystalgroup.in | REEFER
JUL091/25 | 2025-07-31 21:05 | crm@crystalgroup.in | Dr. Reddy's laboratories Ltd. | V Tejeswar Rao | 7680885241 | NA | KKFU6712802 |  |  | payableshelpdesk@drreddys.com | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 08:05 | 2025-08-30 |  |  |  |  | KKFU6712802 |  |  |  | Carrier | 3.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2b 11.3b | 12.9a 12.9a 12.9a | 396v 396v 396v | Not done | PM service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1td2jR1kf9Qq2fGt4jISD-vwON8l2L-JB | https://drive.google.com/open?id=1n4N35sh0HasfObeyo10ic490n-RIZKXc |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG001/25 | 2025-08-01 15:09 | crm@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | Meghana Joshi | 7499611761 | CEO | SEGU9511192 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Dahanu | Running with issues | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | Email | HARSHALI | 2025-08-12 11:22 | service@crystalgroup.in | TAKSHAVI PRIVATE LIMITED | SEGU9511192 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | ICE FROSTING ON EVP COIL AND MOTOR | removed the ice. | na | No | ice frosting on evp coil and motor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG001%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | na | NA | NA | USED | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-15 12:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-15 13:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-15 13:11 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-08 11:12 | 2025-08-07 |  |  |  |  | SEGU9511192 |  |  |  | Carrier | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/.6/170/180 | 9.9/9.8/9.9x2 | 402/403/403 | Short | Al 22 & PM service | repaired and replaced evp. cover with clean ice from motor and pm service completed both twoway unit. | No | https://drive.google.com/open?id=128T21Jw-uI6US5DMxwUApeDuLPUoI2Hw | https://drive.google.com/open?id=1ahbjdlSIRcIDg14V6WBTPdbNr2tsAA4W |  | 107 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
AUG002/25 | 2025-08-01 15:54 | crm@crystalgroup.in | Crystal | SHUBHAM | 7624 011 599 | NA | CRIU2024327 | NA |  | service@crystalgroup.in | JNPT | REBURBISHMENT | NEED TO COVER CONTAINER WITH POLYTHENE SHEET | Email | NA | 2025-08-01 16:01 | crm@crystalgroup.in | CRYSTAL YARD | CRIU2024327 | 20FT STD RF | THERMOKING | NA | STOCK | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG002%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | No | NA | 2025-10-18 14:48 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-18 14:48 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-18 14:49 | crm@crystalgroup.in | NO
AUG003/25 | 2025-08-01 15:58 | crm@crystalgroup.in | Crystal | SHUBHAM | 7624 011599 | NA | CRIU2024311 | REFURBISHMENT |  | service@crystalgroup.in | JNPT | REFURBISHMENT | NEED TO COVER CONTAINER WITH POLYTHENE SHEET | Call | NA | 2025-08-01 16:04 | crm@crystalgroup.in | CRYSTAL YARD | CRIU2024311 | 20FT STD RF | THERMOKING | NA | STOCK | NA | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG003%2F25 | Thermoking | TK-MP4000 | NA | NA | NA | New | NA | SHAHBUDDIN | No | REFURBISHMENT | 2025-10-06 11:24 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-15 11:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 14:36 | crm@crystalgroup.in | NO
AUG004/25 | 2025-08-01 16:12 | crm@crystalgroup.in | DR REDDY FTO 7 | Ajit Kumar Sahu | 98228 84152 | NA | PCIU6025808 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-02 08:15 | 2025-08-01 |  |  |  |  | PCIU6025808 |  |  |  | Daikin | 20.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7 1224 | 8.8a 8.8a 8.8a | 412v 412v 412v | Not done | Pm service and general inspection done | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly | No | https://drive.google.com/open?id=1DmKYdnvpLin9YAgoAvHAiFg0iRo0S79L | https://drive.google.com/open?id=1mcOj-rPabdEhZ99Ex9NLA3OfywOQ1L54 |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG005/25 | 2025-08-01 16:16 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | MADHUSUDHAN | 7259366532 | NA | NYKU7931149 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-03 12:47 | 2025-07-28 |  |  |  |  | NYKU7931149 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4 16.5bar | 7.1 7.1 7.1 | 415 415 415 | Not done | Pm service and general inspection done | Pm service complete with unit operation and internal check this unit power check cricket breaker input and output voltage check all sensor reading gas leval check evp motor voltage all contractor resistance check condenser coil clean were all found ok. | No | https://drive.google.com/open?id=1T_fFyCNpUmYy6udlokQrm6DS4DlZ5pYG | https://drive.google.com/open?id=1RIIhSKBjoZ7Udub9GpmjQSEJfSVhByCA |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG006/25 | 2025-08-01 16:19 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | MADHUSUDHAN | 7259366532 | NA | CRLU3604920 |  |  | NA | Bidar | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-03 12:56 | 2025-07-29 |  |  |  |  | CRLU3604920 |  |  |  | Daikin | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8 1200 | 7.3 7.3 7.3 | 415 415 415 | Not done | Pm service and general inspection done | Pm service complete with unit operation and internal check this unit power check cricket breaker input and output voltage check all sensor reading gas leval check evp motor voltage all contractor resistance check condenser coil clean were all found ok. | No | https://drive.google.com/open?id=1cQGFjRMsLL2TKbUA6MW1IUO_xlcOClMm | https://drive.google.com/open?id=1aAzM7tyNqZ06qY6BUgFWOk-2pszrDuOd |  | TRIP110 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG007/25 | 2025-08-07 11:39 | crm@crystalgroup.in | Qwik Supply | Eashub | 9515150647 | NA | CICU3876591 | FLUCTUATIONS IN TEMEPRATURE | NA | NA | Vijaywada | Running with issues | NA | Call | PUSHPA MAM | 2025-08-08 16:11 | service@crystalgroup.in | Qwik Supply | CICU3876591 | 10RF | THERMOKING MP 4000 | SERVICE-ON CALL | LEASE | FOC | TEMP NOT FALLING | NAT | NA | No | Unit is working fine without any alarms | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG007%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | NA | NA | SHAHBUDDIN | No | FLUCTUATIONS IN TEMEPRATURE | 2025-10-15 12:41 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-15 13:08 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-15 13:11 | crm@crystalgroup.in | NO
AUG008/25 | 2025-08-08 10:18 | crm@crystalgroup.in | Tianish Laboratories Private Limited | Ravi kumar | 7799045848 | NA | CXRU1040451 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Pushpa mam | [54 empty] | 2025-08-11 10:20 | 2025-08-05 |  |  |  |  | CXRU1040451 |  |  |  | Daikin | 21.5'c, 18.0 double unit | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.9 11.1 | 9.7 9.7 9.7 | 398 398 398 | Not done | Pm service and general inspection done both unit | I have checked voltage input output voltage sensor reading and found humidity sensor defective need to replace and display control pannel damage need to replace | Yes | https://drive.google.com/open?id=1XNYvA1AIY5Y2JDpTMDh9c9WA5Qg4Fp8v | https://drive.google.com/open?id=1fkJ4Q0VxI2wq4CpAV_U_nhenQf8MHpTP |  | TRIP106 | No | Yes | Can be done on next PM | Na | Humidity sensor User control pannel without display | technician@crystalgroup.in | REEFER
AUG009/25 | 2025-08-08 10:55 | crm@crystalgroup.in | LAURUS UNIT -1 | SOMI REDDY | 9963198979 | NA | CICU1442209 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-11 10:03 | 2025-08-07 |  |  |  |  | CICU1442209 |  |  |  | Thermo king | -0.2'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9 13.2 | 9.2 9.2 9 2 | 396 396 396 | Short | As per client request i visit to unit and observed container running in range. Customer complaint it going in defrosting in 24 hours. This unit equipped automatic defrosting sensor. | I have checked all sensors reading input output voltage were all checked and found all ok. I have washed eveporator coil by customer request. Now unit running in good condition. | No | https://drive.google.com/open?id=1Q2v4bV6Vk_OL8VoO64WV1PA0gI0onHZV | https://drive.google.com/open?id=1165tf8UCwcF7RSAKASaiwAXuOU3sCpYy |  | TRIP106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG010/25 | 2025-08-08 11:01 | crm@crystalgroup.in | Qwik Supply | MURGAN | 9867118776 | NA | TDRU7151504 | SERVICING, Evaporator inlet sensor issue |  | NA | SEWRI | Running with issues | Evaporator inlet sensor issue | Call | Pushpa mam | 2025-09-02 14:59 | service@crystalgroup.in | Qwik Supply | TDRU7151504 | 40RF | THERMOKING | SERVICE-AT SITE | LEASE | FOC | RETURN SENSOR DEFECTIVE | NEED TO REPLACE RETURN SENSOR | Return Sensor | Yes | RETURN SENSOR DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG010%2F25 | THERMOKING | TK-MP3000 | NA | NA | NA | USED | NA | NEMICHAND | Yes | SERVICING, Evaporator inlet sensor issue | 2025-09-02 15:04 | service@crystalgroup.in | NO | [9 empty] | 2025-09-02 15:05 | service@crystalgroup.in | YES | NA | YES |  | Stock | 2025-09-29 17:35 | crm@crystalgroup.in | YES | NA | TECHNICIAN |  |  | NIMICHAND |  |  | 2025-08-08 14:07 | 2025-08-06 |  |  |  |  | TDRU7151504 |  |  |  | Daikin | 12C sup 12.0C Ret 16.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | HPT 1201 LPT 13 | CT1 17.3A CT2 13.6A | 376V | Not done | Container was malfunctioning return sensor and evp inlet sensor failure container is now running in range temperature after repair | Attended to container malfunction replacement faulty return sensor container is now operations normal within range tepm. | Yes | https://drive.google.com/open?id=10k55JvGVd0hRrA_P0JaVNXkoOA50X1p5 | https://drive.google.com/open?id=1l72bduYO0De_iTB7VX_Z4Xrr9Qx7x53K |  | N/E | Yes | No | Can be done on next PM | Evaporator inlet sensor | Evaporator inlet sensor | technician@crystalgroup.in | REEFER
AUG011/25 | 2025-08-08 17:24 | crm@crystalgroup.in | Parle Biz | SUPRIT LAMBA | 9917480215 | NA | CXRU1041123 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | VILE PARLE | Running with issues |  | Call | PUSHPA MAM | 2025-08-11 15:35 | service@crystalgroup.in | PARLE | CXRU1041123 | 40FT STD RF | DAIKIN | SERVICE-ON CALL | SALE | CHARGEABLE | Unit has sheet key defective | instructed client to replace the sheet key | sheet key | Yes | unit has sheet key defective | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG011%2F25 | DAikin | DAIKIN | M002147 | K31408135759 | DECOS 3F / 2609 / 1 | Used | na | SHAHBUDDIN | No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | [12 empty] | 2025-11-17 11:16 | crm@crystalgroup.in | YES | IN334 | YES |  | Stock
AUG012/25 | 2025-08-11 18:10 | crm@crystalgroup.in | MANTRA EVENTS AND PROMOTIONS PRIVATE LIMITED | SUMIT SONI |  | MANAGER | CKLU2058158 OOLU1481295 WHLU0279473 TCKU2842760 | REPAINT OF CONTAINERS |  | sumit@mantraevents.com | GOREGAON | REPAITING OF CONTAINER |  | Email | PUSHPALATHA SHETTY | 2025-08-12 11:35 | service@crystalgroup.in | MANTRA EVENTS AND PROMOTIONS PRIVATE LIMITED | CKLU2058158 OOLU1481295 WHLU0279473 TCKU2842760 | 20DV | NA | REFURBISHMENT OF CONTAINER | STOCK | FOC | INSPECTED & PURCHASED | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG012%2F25 | NA | DRY | NA | NA` | NA | USED | NA | AKSHAY | No | REPAINT OF CONTAINERS | 2025-08-12 10:56 | crm@crystalgroup.in | YES | IN130 | 2025-08-11 | Paid | MANTRA EVENTS AND PROMOTIONS PRIVATE LIMITED | GOREGAON EAST | "CKLU2058158 OOLU1481295 WHLU0279473 TCKU2842760" | DEPOT | PAID |  | 2025-08-12 10:59 | crm@crystalgroup.in | YES | IN130 | YES | https://drive.google.com/open?id=1Ea2YBnOLNj2-b3syWTHtp7Uhrh29YlTn | Vendor | 2025-08-12 11:05 | crm@crystalgroup.in | YES | IN130 | ARRENGING AT SITE | [5 empty] | 2025-08-12 11:08 | [54 empty] | crm@crystalgroup.in | DRY/Others
AUG013/25 | 2025-08-14 14:46 | crm@crystalgroup.in | CIPLA | LAXAMAN RAWOOL |  | STORE MANAGER | TRIU6681434 | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | NA | Laxman.Rawoot@cipla.com | Goa | Temperature Excursion in cold storage container | Temperature Excursion in cold storage container was observed on 13.08.2025, Temperature found Below 2°C | Email | NA | 2025-08-18 18:18 | service@crystalgroup.in | CIPLA | TRIU6681434 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | UNIT IS HAVING SENSOR ISSUES ( RETURN & SUPPLY SENSOR) | NEED TO REPLACE SENSORS | SUPPLY SENSOR -2 NOS & RETURN SENSOR - 01 NOS | Yes | SENSOR FAULTY | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG013%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | JSGA623040304 | NEMICHAND | Yes | FLUCTUATIONS IN TEMEPRATURE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-06 11:50 | crm@crystalgroup.in | NO | [26 empty] | 2025-08-20 13:42 | 2025-08-20 |  |  |  |  | TRIU6681434 |  |  |  | Carrier | +5C Supply +4.9C Return +5.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.6 bar 13.8 bar | R 10.7A B 10.7A Y 9.3A | 413V 413V 413v | Not done | Supply and return sensor faulty | Attended to container malfunction replaced faulty supply and return sensor. Container is now operational within range temperature. | No | https://drive.google.com/open?id=1O5J6rkeQ5VZQRqNxkscBFlPOuFuwvxGk | https://drive.google.com/open?id=1VZMRbaN8PX7u3wyhSeL4mLod9tJ8Uvhc |  | 112 | No | No | Can be done on next PM | N/A | N/A | technician@crystalgroup.in | REEFER
AUG014/25 | 2025-08-16 12:23 | operation@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Warehouse Manager | MYRU4518356 | REPAIRS & REPLACEMENT | NA | gopal5.krishna@qwick.co.in | Lucknow | Complete Breakdown | It was observed that some part appears to be short-circuited | Email | Pushpalata Shetty | 2025-08-16 12:58 | operation@crystalgroup.in | Qwik Supply | MYRU45183545R1 | 40ft | Daikin | Breakdown | LEASE | FOC | MYRU45183545R1 | Replacement of Contactor | Contactor | Yes | Contactor burned | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG014%2F25 | Daikin | DAIKIN | MYRU45183545R1 | DCOZ3E | JSGA622180065 | used | M005086 | RAJ KUMAR | Yes | REPAIRS & REPLACEMENT | [29 empty] | 2025-09-29 14:29 | 2025-08-30 |  |  |  |  | MURU4518356 |  |  |  | Daikin | 18'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B, 16.2B | 10.1A 10.1A 10.1A | 396v 396v 396v | Not done | Malfunction attend | Unit breakdown, i have checked and found compressor contractor burnt out, phase contractor noisy need to replace, user panel with sheet key not working properly need to replace, ambent and suction SENSOR out of calibration need to change | Yes | https://drive.google.com/open?id=1XQp49VkQ-sgbF3Gu2pTL3jrISkX8DdXE | https://drive.google.com/open?id=1yxfxsHE6uuVlqpr-QtCL9f0tfdjy_NIp |  | Na | Yes | Yes | Urgent | Unit breakdown | Compressor contractor with wiring User panel with sheet key Phase contractor both Suction SENSOR Discharge sensor | technician@crystalgroup.in | REEFER
AUG015/25 | 2025-08-16 15:37 | operation@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | TDRU7151675 |  |  | gopal5.krishna@qwick.co.in | Lucknow | Preventive Maintenance |  | Email | Pushpalata Ma'am | 2025-08-16 16:01 | operation@crystalgroup.in | Qwik Supply | TDRU7151675 | 40FT Spl RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG015%2F25 | Daikin | DAIKIN | RFG20R | NA | NA | RefurbiShed | JSGA622180053 | RAJ KUMAR | Yes | [30 empty] | 2025-08-30 22:52 | 2025-08-30 |  |  |  |  | TDRU7151675 |  |  |  | Daikin | +18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3bar/14.8bar | 7.9A/7.9A/7.9A | 399v/399v/399v | Not done | Pm service | We have check and found outlet sensor, inlet sensor, ambient temperature sensor, return sensor out of range need to replace | Yes | https://drive.google.com/open?id=1Y4Oy7xX0fbkyYDS_ZDZ2OawUl41zX6qB | https://drive.google.com/open?id=1ALBAXhEzkaPNr4U02HCYWGt9Si1D2aeN |  | 104 | Yes | Yes | Urgent | Required part list | Outlet sensor. 01 nose Inlet sensor. 01 nose Ambient temperature sensor. 01 nose Return sensor 01 nose | rajreefertech@gmail.com | REEFER
AUG016/25 | 2025-08-16 15:42 | operation@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | MYRU4518356 |  |  | gopal5.krishna@qwick.co.in | Lucknow | Preventive Maintenance |  | Call | Psuhpa Ma'am | 2025-08-16 16:05 | operation@crystalgroup.in | Qwik Supply | MYRU4518356 | 40FT STD RF | Daikin | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG016%2F25 | Daikin | DAIKIN | M005086 | DCOZ3E | NA | Used | JSGA622180065 | RAJ KUMAR | Yes |  | 2025-09-02 13:12 | operation@crystalgroup.in | YES | IN151 | 2025-09-02 | FOC | ITC limited | Bangalore | PCIU6007065 | SITE | FOC | DAIKIN | [17 empty] | 2025-08-30 22:37 | 2025-08-30 |  |  |  |  | MYRU4518356 |  |  |  | Daikin | +18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2 bar /16.8bar | 10.1A/10.1A/10.8A | 396V/396V/396V | Short | Unit brackdown | We have check and found compressor contacter burnt out, phese contactor noisy need to replace, ambient temperature sensor out of range, keypad not working properly need to replace | Yes | https://drive.google.com/open?id=1WpXV-pZ9bqm1iuat-bdXv0JlbOcsSDLC | https://drive.google.com/open?id=154LyLaYonJGs12YVzc072JVuE_31s5m8 |  | 104 | Yes | Yes | Urgent | Required part list | Compressor contactor 01 nose Phese contactor 01 nose User panal with sheet key 01 nose Ambient temperature sensor 01 nose Section gas temperature sensor 01 nose Ring termind crimp. 15 nose | rajreefertech@gmail.com | REEFER
AUG017/25 | 2025-08-16 15:45 | operation@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | TCLU1903088 |  |  | gopal5.krishna@qwick.co.in | Lucknow | Preventive Maintenance |  | Call | Pushpa Ma'am | 2025-08-16 16:08 | operation@crystalgroup.in | Qwik Supply | TCLU1903088 | 20FT STD RF | NA | PREVENTIVE MAINTENANCE | LEASE | FOC | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG017%2F25 | Daikin | DAIKIN | RFG20R | NA | NA | Used | JSGA622180051 | RAJ KUMAR | Yes | [30 empty] | 2025-08-30 22:19 | 2025-08-30 |  |  |  |  | TCLU1903088 |  |  |  | Daikin | -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace | https://drive.google.com/open?id=1dNbMMYZ98fkddNz8HuYL3DPoSefCmZ64 | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | S. 0.2 bar. D 14.2 bar | 8.1/8.1/8.1 | 402/402/402 | Not done | Pm service | We have check and found unit running but showing alarm inlet sensor,outlet sensor, supply sensor out of range need to replace | Yes | https://drive.google.com/open?id=1b1jynO0dC1gAttUu6JRFKgYOosnaXHOL | https://drive.google.com/open?id=1HaAo70gkGOp_PkC7NKmxYUl0CnzVgUvI |  | 104 | Yes | No | Urgent | Required part | Supply sensor 01 nose Inlet sensor. 01 nose Outlet sensor. 01 nose Display | rajreefertech@gmail.com | REEFER
AUG018/25 | 2025-08-16 16:24 | operation@crystalgroup.in | Luckhnow International Airport | Vivek Chauhan | 9161113399 | NA | TRIU6618581 |  |  | vivek.Chauhan@adani.com | Lucknow | Preventive Maintenance |  | Call | Pushpa Ma'am | 2025-08-16 16:26 | operation@crystalgroup.in | Luckhnow International Airport | TRIU6618581 | 20FT STD RF | NA | PREVENTIVE MAINTENANCE | LEASE | CHARGEABLE | NA | NA | NA | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG018%2F25 | Carrier - Thinline | DAIKIN | NOT AVAILABLE | NOT AVAILABLE | NOT AVAILABLE | Refurbished | RFG20R | RAJ KUMAR | Yes
AUG019/25 | 2025-08-18 10:44 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6031328 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:48 | 2025-08-16 |  |  |  |  | PCIU6031328 |  |  |  | Daikin | 22.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.4B 13.4B | 7.9A 7.9A 7.9A | 408V 408V 408V | Not done | Pm service and general inspection done | Unit working in good condition but recorder supply sensor, return sensor and outlet sensor defective need to chenge in upcoming service | Yes | https://drive.google.com/open?id=1BBvb-Va9DC2zeEiUQJtPf7AB2eabEZmi | https://drive.google.com/open?id=1mU1_h85wID9LSPjlWvanIQ4bWyAcSAq_ |  | 106 | No | No | Can be done on next PM | Na | Supply sensor Rerun sensor Outlet sensor | technician@crystalgroup.in | REEFER
AUG020/25 | 2025-08-18 10:59 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | HDMU5542114 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:44 | 2025-08-16 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | 4.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.4B | Na | 418V 418V 418V | Not done | Pm service and general inspection done | Unit working in good condition | Yes | https://drive.google.com/open?id=1ZfX56L7LuSZJtbKwn7DBH-viOrqCsjpU | https://drive.google.com/open?id=1HomCnSD9Kz4W_ZHryyYLTC8cKuNHqsOC |  | 106 | Yes | Yes | Can be done on next PM | Display | Display | technician@crystalgroup.in | REEFER
AUG021/25 | 2025-08-18 11:03 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6032622 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:41 | 2025-08-16 |  |  |  |  | PCIU6032622 |  |  |  | Daikin | 21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 11.4B | 7.8b 7.8b 7.8b | 418V 418V 418V | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1vfN6d6FLgd9Ah45xMhfIHfy1LbfOhM94 | https://drive.google.com/open?id=19oEkTENIf7vTNjPcLp_NSOA7dTkuwOAV |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG022/25 | 2025-08-18 11:04 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6034374 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:38 | 2025-08-16 |  |  |  |  | PCIU6034374 |  |  |  | Daikin | 20.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.4 | 7.8b 7.8b 7.8b | 417V 417v 417v | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1gu2NqIC6vbFjQ8XrMeIqykDdgoHjjtsK | https://drive.google.com/open?id=1NQ4wtE-dKi6x8H8jtOCQI9ztPNM7-Y2D |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG023/25 | 2025-08-18 11:06 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | TITU9930032 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:22 | 2025-08-16 |  |  |  |  | TITU9930032 |  |  |  | Carrier | 3.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2b 11.4b | 6.4a 6.4a 6.4a | 420v 420v 420v | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1rsV9CRibv4jfv1P7QC0komBJKVB7Llhe | https://drive.google.com/open?id=1jXVJZ35px_-F4VUhA8cTu4fM5pF4wRYB |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG024/25 | 2025-08-18 11:09 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Tharunkishore | 7032638267 | NA | MYRU4518042 |  |  | tharunkishore.r@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:19 | 2025-08-16 |  |  |  |  | MYRU4518042 |  |  |  | Daikin | 5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 12.9B | 7.8a 7.8a 7.8a | 415v 415v 415v | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1z8LAAP_PpA8pik7CF0yPZiCIKvqnJ0_p | https://drive.google.com/open?id=1hHTgsOa7j2dL8Vqq-LOOqGDaPbqN7Sek |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG025/25 | 2025-08-18 11:36 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | NYKU7031149 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:16 | 2025-08-16 |  |  |  |  | NYKU7931149 |  |  |  | Carrier | 5.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2b 11.4b | 12.A 12A 12A | 415v 415v 415v | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1phzy251WxLrpywJe4XtDP6yZ3tAAAMm- | https://drive.google.com/open?id=14gtQAWXax8WCREUuR4OlXMVtekJ8KU3U |  | 106 | No | No | Can be done on next PM | Na | N | technician@crystalgroup.in | REEFER
AUG026/25 | 2025-08-18 11:41 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | CRLU3904920 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:12 | 2025-08-16 |  |  |  |  | CRLU3904920 |  |  |  | Daikin | 4.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2.1b 10.1b | 8.4a 8.4A 8.4A | 404v 404v 404v | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1aLpPlZHWTyOY0iRtuZSCMJVLPLrJyOtm | https://drive.google.com/open?id=1r0KOM0aOW6Kx_7AX_zj9Edftk_KDNNGw |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG027/25 | 2025-08-18 11:44 | operation@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Excutive | GESU9460634 |  |  | Madhusoodhana.k@sailife.com | Bidar | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-20 10:09 | 2025-08-16 |  |  |  |  | GESU9460634 |  |  |  | Carrier | -3.9'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9b 10.4b | 5.7a | 422v 422v 422v | Not done | Pm service and general inspection | Unit running in good condition | No | https://drive.google.com/open?id=1U55hVCICycsBLq--tJGqHdiNNhiB62Oi | https://drive.google.com/open?id=1X4I42ucN75h6gNOQRCHS4orO6kRtwn8Q |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG028/25 | 2025-08-20 10:03 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU8431985 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:33 | 2025-08-13 |  |  |  |  | TRIU8431985 |  |  |  | Daikin | -12.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 11.2B | 9.5A 9.5A 9.5A | 396V 396V 396V | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=18H-y6Q6IwZWaUi0jwR9nUfndb8gGjKwH | https://drive.google.com/open?id=1LNhupyYJUUYUNaDlV8lXbI8p6InnzNMq |  | 106 | No | No | Can be done on next PM | Nan | Na | technician@crystalgroup.in | REEFER
AUG029/25 | 2025-08-20 10:06 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | On Duty Officer | TCLU1003229 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:30 | 2025-08-13 |  |  |  |  | TCLU1003229 |  |  |  | Thermo king | 13.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8B 14.4B | 7.9A 7.9A 7.9A | 402V 402V 402V | Not done | Pm service and general inspection done | Unit working in good condition | No | https://drive.google.com/open?id=1hUUBR-wj4jBiLUEFw9ofawaZw2AiPO84 | https://drive.google.com/open?id=1Z1fmM1wnGT8P-h91d3Fey-brxXu4PB6v |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG030/25 | 2025-08-20 10:09 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | APRU5390455 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:26 | 2025-08-13 |  |  |  |  | APRU5390455 |  |  |  | Carrier | -21C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.9B | 11.4A 11.4A 11.4A | 398V 398V 398V | Not done | Pm service and general inspection | Unit working in good condition, ice inside kick plate cleard | Yes | https://drive.google.com/open?id=1Z6yPwNNytB2JF6KlAEpsEP1DVqlZSl0_ | https://drive.google.com/open?id=17C0eCsKxnnTh7Xpz2n55_naI2Z-j5SP- |  | 106 | No | No | Can be done on next PM | Diplay pending | Display | technician@crystalgroup.in | REEFER
AUG031/25 | 2025-08-20 10:11 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TDRU7152244 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:19 | 2025-08-13 |  |  |  |  | TDRU7152244 |  |  |  | Daikin | -12.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8B 11.4B | 9.2A 9.2A 9.2A | 398V 398V 398V | Not done | Pm service and general inspection | Unit working in good condition | No | https://drive.google.com/open?id=1GQkgTNSa_Ww0YwOQDOk3IA7JC4hBpqm_ | https://drive.google.com/open?id=15gNy62MNP1Z19EiNykbzxDsyml9tqsCT |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG032/25 | 2025-08-20 10:13 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU1703263 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:15 | 2025-08-13 |  |  |  |  | TRIU1703263 |  |  |  | Carrier | 5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.4B | 11.2A 11.2A 11.2A | 404V 404V 404V | Not done | Pm service and general inspection | Unit working in good condition | No | https://drive.google.com/open?id=1ZZcEfKMW-RfycSQmkcbHTRVs4drsc2X8 | https://drive.google.com/open?id=1Dv6sJ7vzOYjoTwGfEP4TD8PdS_Khrbbv |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG033/25 | 2025-08-20 10:16 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU8363258 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 19:12 | 2025-08-13 |  |  |  |  | TRIU8363258 |  |  |  | Carrier | -4.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 13.9B | 11.9A 11.9A 11.9A | 404V 404V 404V | Not done | Pm service and general inspection | Unit working in good condition | No | https://drive.google.com/open?id=1sO7I-RmKk3X0PfmMFUYNFTRrMRYvW9_- | https://drive.google.com/open?id=1suguEMMPxvRwBaqBfXogvkDmumKTKONk |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG034/25 | 2025-08-20 10:19 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CXRU8387141 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 18:10 | 2025-08-13 |  |  |  |  | CXRU8387141 |  |  |  | Carrier | 21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 11.0B | 12.4A 12.4A 12.4A | 398V 398V 398V | Not done | Pm service and general inspection | Unit working in good condition | No | https://drive.google.com/open?id=1YJ1x7We7TdCdLnINFOpO2oyd4bUWjlhA | https://drive.google.com/open?id=1ByyMhrsBaUtL0LSkuiqoSRbQ3deimpCg |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG035/25 | 2025-08-20 10:23 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CGMU4984529 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | 2025-09-02 16:31 | service@crystalgroup.in | Divis labs | CGMU4984529 | 40RF | CARRIER THINLINE | PREVENTIVE MAINTENANCE | SALE | FOC | PM CARRIED OUT | NEED TO CARRYOUT PM | - | No | PM | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG035%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | Yes | [30 empty] | 2025-08-22 18:06 | 2025-08-13 |  |  |  |  | CGMU4984529 |  |  |  | Carrier | 21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8B 11.9B | 11.9A 11.9A 11.9A | 400V 400V 400V | Not done | Pm service and general inspection done | Water coming inside the container, fix water hose pipe, unit working in good condition | No | https://drive.google.com/open?id=1Y5cei8wzUXPPWNdajKJXBiHsh2noUjB1 | https://drive.google.com/open?id=1WHxtjEhAqk9Q2d9N3FXSV0T9T0-92MAk |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG036/25 | 2025-08-20 10:26 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU1703263 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 17:59 | 2025-08-13 |  |  |  |  | TRIU1703263 |  |  |  | Carrier | 5.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.4B | 11.2A 11.2A 11.2A | 404V 404V 404V | Full | Pm service and general inspection | Unit working in good condition | No | https://drive.google.com/open?id=1WTufiDOkOZMGj6idZdW4bUHdDgBRidmj | https://drive.google.com/open?id=1oIncuQSnc3OJsfbu97fUPjL5oGL3fHvn |  | 106 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG037/25 | 2025-08-20 10:28 | operation@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU8339605 |  |  | M.Ramakrishna@divislabs.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am | [54 empty] | 2025-08-22 11:48 | 2025-08-13 |  |  |  |  | TRIU8339605 |  |  |  | Carrier | 13C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 11.3B | 13.1A 13.1A 13.1A | 398V 398V 398V | Not done | Pm service and general inspection done | Unit working in good condition . Display not visible properly | Yes | https://drive.google.com/open?id=1fjz3ZBDhMCURVikEPX6gni1MW-6dmmlC | https://drive.google.com/open?id=15m37wxDsZ2DDj66WZbe7VzUMq_ylk1cA |  | 106 | No | No | Can be done on next PM | Na | Display | technician@crystalgroup.in | REEFER
AUG038/25 | 2025-08-21 10:12 | operation@crystalgroup.in | ITC Ltd | Shiva | 9849765331 | Manager | MYRU4517508 |  |  | NA | Bapatla | Preventive Maintenance |  | Call | Pushpa Ma'am
AUG039/25 | 2025-08-21 10:15 | operation@crystalgroup.in | Qwik Supply | Eashub | 9515150647 | NA | CICU3876591 |  |  | NA | Vijaywada | Preventive Maintenance |  | Call | Pushpa Ma'am
AUG040/25 | 2025-08-21 10:18 | operation@crystalgroup.in | Qwik Supply | avinash | 9281026402 | NA | CICU2779920 |  |  | Battula.Sateesh@ril.com | Shamshabad | Preventive Maintenance |  | Call | Pushpa Ma'am
AUG041/25 | 2025-08-21 10:21 | operation@crystalgroup.in | DSV Solutions Pvt Ltd | SAGAR | 9030909007 | NA | TITU8258978 |  |  | somnath.shewale@dsv.com | Kompally | Preventive Maintenance |  | Call | Pushpa Ma'am
AUG042/25 | 2025-08-21 10:41 | operation@crystalgroup.in | DHL Supply Chain pvt Ltd | Ritesh Ingle ¦ Yogindar Singh ¦ Niranjan Kanthe | 9703874353 ¦ 9460975040 ¦ 70830 26116 ¦ 9885755890 | NA | DFOU6120281 |  |  | yogindar.singh@dhl.com ¦ niranjan.kanthe@dhl.com ¦ nikhil.adicherla@dhl.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Ma'am
AUG043/25 | 2025-08-21 11:50 | sales@crystalgroup.in | Navios Automation Pvt Ltd | Tony P G | 7559927714 | Operations Manager | CRIU2024311 CRIU2024327 | Installation | NA | sales@navios.in | Kochi, Kerala | Installation | NA | Call | NA | 2025-08-21 12:20 | service@crystalgroup.in | Navios Automation Pvt Ltd | CRIU2024311,CRIU2024327 | 20RF | THERMOKING MP4000 | INSTALLATION | SALE | CHARGEABLE | INSTALLATION OF 02 UNITS. | INSTALLATION OF 02 UNITS | - | No | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG043%2F25 | TK MP 4000 | TK-MP4000 | NA | NA | NA | NEW | NA | NEMICHAND | Yes | Installation | 2025-09-29 16:46 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-29 16:47 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-29 16:47 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-25 21:16 | 2025-08-23 |  |  |  |  | TRIU6680016 |  |  |  | Thermo king | -40C Rat. -38.7C Sup. -43.8C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc. 1.2 bar dis. 15.7bar | R 9.8A B 9.8A Y 8.8A | 406V 406V 406V | Not done | Pm service and general inspection | Attended routine checkup of container verified all operational are normal container functioning within temperature | No | https://drive.google.com/open?id=1-h6t0vHoaVu-UikuFdQPLm3rCMplsYIt | https://drive.google.com/open?id=1iO4vglYHzW1ooPDYVZ_cwVCyWZZQj-h0 |  | 112 | No | No | Can be done on next PM | 0 | 0 | technician@crystalgroup.in | REEFER
AUG044/25 | 2025-08-21 14:42 | sales@crystalgroup.in | Choice Trading Corporation Pvt.Ltd | Nandu Prasad | 8086880053 | Plant Engineer | TRIU6619090 TRIU6680016 |  |  | nandu.prasad@choicegroup.in | Kochi, Kerala | Preventive Maintenance |  | Call | Radheyshyam | [54 empty] | 2025-08-31 16:51 | 2025-08-23 |  |  |  |  | TRIU6619090 |  |  |  | Carrier | -17C Ret.-16.8C sup.-21.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace | https://drive.google.com/open?id=14V3zojoTub64-vJykbeXdmmKeukgoH1y | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Suc. 0.4 bar Dis. 12.4 bar | R 12.2A B12.1A Y 12.1A | 404V 404V 404V | Not done | Pm service | Attended routine checkup of container verified all operations are normal within range temperature. Ambient sensor faulty and display need to replace | Yes | https://drive.google.com/open?id=1ht16hd2u4f1uaCL588MZwE7IYgQRJX7H | https://drive.google.com/open?id=1fJ7jeze1KQ-HFOeKIWhMFyjDFOydxSHC |  | 112 | Yes | Yes | Can be done on next PM | Display and ambient sensor | Ambient sensor Display | technician@crystalgroup.in | REEFER
AUG045/25 | 2025-08-22 17:13 | sales@crystalgroup.in | DIVIS LAB | PAPA RAO | 7013694117 | ON DUTY OFFICER | APRU5390955 | ICE FORMATION | SCREW BACK PANEL / WASHER USED , RIVET BLIND USED IN SERVICE | M.Ramakrishna@divislabs.com | Hyderabad | Running with issues | ICE FORCASTING FROM BACK PANEL | Call | PUSHPA MAM | 2025-09-02 18:28 | service@crystalgroup.in | DIVIS LAB | APRU5390955 | 40RF | CARRIER | SERVICE-AT SITE | LEASE | FOC | ice frosting on evp coil areaa | need to remove the ice | screw and revit required | screw & revit required - 20-20 nos | ice frosting on evp coil area | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG045%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | ICE FORMATION | 2025-10-20 12:28 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 12:29 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 12:29 | crm@crystalgroup.in | NO | [7 empty] | 2025-08-26 11:04 | 2025-08-20 |  |  |  |  | APRU5390955 |  |  |  | Carrier | -21.0C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | On call | Not done | On call | Ice frosting on inside evaporator panel, kick plate need to refix and clean and remove cable from back side drain hose. All evaporator panel screw need to fix with same size | Yes | https://drive.google.com/open?id=137M2nqWVlvJF5NinSWL31UfMpaIlG4CY | https://drive.google.com/open?id=1kW9raaFR-8uZPpc8gjxm4HnTgeXjQNJb |  | 106 | Yes | Yes | Urgent | Need to melt ice | Evaporator panel screw | technician@crystalgroup.in | REEFER
AUG046/25 | 2025-08-25 11:32 | sales@crystalgroup.in | Qwik Supply | Ankit singh | 9780266737 | CPC Manager | APRU5066497 | Machine is not getting ON | NA | ankit111.singh@qwik.co.in | Surat | Complete Breakdown | Machine is not getting ON | Call | Pushpa Mam | 2025-09-27 16:25 | service@crystalgroup.in | Qwik Supply | APRU5066497 | 40RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | unit found to be working fine | NAT | NA | No | UNIT FOUND TO BE WORKING FINE WITHOUT ANY ISSUES. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG046%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | No | Machine is not getting ON | 2025-09-27 16:29 | service@crystalgroup.in | NO | [9 empty] | 2025-09-27 16:31 | service@crystalgroup.in | NO |  |  |  |  | 2025-09-27 16:31 | service@crystalgroup.in | NO | [7 empty] | 2025-09-29 14:53 | 2025-09-27 |  |  |  |  | APRU5066497 |  |  |  | Carrier | -20, supp -22.2, ret. -19.2'C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | On call | Full | Customer request, | I have checked with site engineer and found unit temperature in range. No issues found. Unit working fine | No | https://drive.google.com/open?id=1lSlCOvl3_H-F0HN29WVKiBSdJsjhQAie | https://drive.google.com/open?id=1uNMJVFoamqP5cWOvHknLrfHVcoa22jC7 |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG047/25 | 2025-08-25 15:02 | sales@crystalgroup.in | Crystal | Shubham | 7624011599 | Depot Manager | PCIU6007065 | SERVICING |  | service@crystalgroup.in | Uran | Running with issues | Evaporator Motor Stuck | Call | Shubham | 2025-09-06 14:52 | service@crystalgroup.in | Crystal Yard | PCIU6007065 | 40FT STD RF | DAIKIN | REPAIR | STOCK | CHARGEABLE | EVP MOTOR DEFECTIVE | NA | EVP MOTOR | No | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG047%2F25 | Daikin | DAIKIN | NA | NA | NA | Refurbished | NA | RAMESH | No | SERVICING
AUG048/25 | 2025-08-25 18:05 | crm@crystalgroup.in | Tata Advance | Raghu Ramesh |  | NA | BMOU9788370 | COMPRESSOR MAKING NOISE | issue in temperature | raghur@tataadvancedsystems.com | Bangalore | Running with issues | issue in temperature | Email | PUSHPA MAM | [54 empty] | 2025-09-03 17:53 | 2025-09-03 |  |  |  |  | BMOU9788370 |  |  |  | Daikin | -29C Ret.-27.7C Sup.-28.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | LPT-55 HPT804 | 9.6A 7.3A | 405V 405V 405V | Not done | Pm service and general inspection | Attended routine checkup of container verified all operational are normal container functioning within range temperature | No | https://drive.google.com/open?id=1bzDr4o03zvUdex9gsQybWcFuRMGDdAYa | https://drive.google.com/open?id=1Zi0nVcA8ar2HPj7jSKXP3b-Gzkt0Qs2s |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
AUG049/25 | 2025-08-28 10:52 | crm@crystalgroup.in | Qwik Supply | Biplab Sharker | 6294502398 | Manager | CXRU1042578 | Cooling Problem |  | biplab.kr.2018@gmail.com | Siliguri | Running with issues | Cooling Problem & Greasy type on back side of container | Call | Pushpa Mam | 2025-10-30 17:15 | service@crystalgroup.in | Qwik Supply | CXRU1042578 | 40FT | na | SERVICE-ON CALL | NA | NA | as per customer unit working fine | na | na | No | unit working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG049%2F25 | Daikin | DAIKIN | M002230 | K31405124622 | DECOS 3F 2553 / 1 | Used | JSGA622180032 | na | No | Cooling Problem | 2025-11-03 12:01 | service@crystalgroup.in | NO | [9 empty] | 2025-11-03 12:01 | service@crystalgroup.in | NO |  |  |  |  | 2025-11-03 12:02 | service@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=AUG049%2F25 | 2025-11-09 21:17 | 2025-11-09 |  |  |  |  | CXRU1042578 |  |  |  | Carrier | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | On call | On call | Not done | As discussed on call with client, unit working fine | Unit working fine | No | https://drive.google.com/open?id=1aKr4M046pA_0ilJ14op06AyN6SMTGZOS | https://drive.google.com/open?id=1Fedg4JUDLbb6n3P3UxenLJU_4ZhcMjDY |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG050/25 | 2025-08-28 10:52 | service@crystalgroup.in | CRYSTAL DEPOT | SHUBHAM TANK | 7624011599 | DEPOT MANAGER | NA | AIR COMPRESSOR |  | service@crystalgroup.in | NEW DEPOT - DHIGODE | AIR COMPRESSOR |  | Email | SHUBHAM | 2025-09-06 15:03 | service@crystalgroup.in | CRYSTAL DEPOT | NA | NA | TOYO AIR COMPRESSOR | NA | NA | NA | NA | NA | NEW AIR COMPRESSOR - TOYO BRAND | Yes | NEW AIR COMPRESSOR | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG050%2F25 | NA | NA | NA | NA | NA | NEW | NA | Shubham Tank | No | AIR COMPRESSOR
AUG051/25 | 2025-08-28 11:01 | crm@crystalgroup.in | Dr Reddy | Suresh Kasam | 9908125456 | Plant Engineer | TITU9930074 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-08-29 21:36 | 2025-08-27 |  |  |  |  | TITU9930074 |  |  |  | Thermo king | -28c/. -26c Dual unit | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/.6 Dis . 18/19 br | 9.8/9.9- 9.8/9.8/-9.9/9.9 | 407/408/407 | Short | Two way unit one tk mp 4000& 2nd mp300 | both two way unit thermoking pm Complited | No | https://drive.google.com/open?id=14S36c4t93yrF1bxjq2NteM-36F_K_DOS | https://drive.google.com/open?id=1r2LJKpTBf1Ev3IuB0TliAqnIfuvCIzbR |  | 115 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
AUG052/25 | 2025-08-28 11:03 | crm@crystalgroup.in | Dr Reddy | Suresh Kasam | 9908125456 | Plant Engineer | TITU9930114 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-08-29 21:43 | 2025-08-27 |  |  |  |  | TITU9930114 |  |  |  | Thermo king | -28c & -26c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/.8. bar Dis . 18/20 br | 9.9/9.8 - 9.9/9.8-9.9/9.9 | 407/408/407 | Short | pm due for two way thermoking unit | pm completed | No | https://drive.google.com/open?id=1PYWoSiN94ERZ7rGa21NBbDxVst0hGvaZ | https://drive.google.com/open?id=1A6mD_WEc0ylyCh1OHhR9OZ1XA78XX4Tj |  | 115 | Yes | No | Can be done on next PM | long time bal to replace compressor- unit temp. maintain side support unit | na | technician@crystalgroup.in | REEFER
AUG053/25 | 2025-08-28 11:19 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 916307373723 | NA | CICU3876605 |  |  | NA | Lucknow | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-08-31 15:55 | 2025-08-30 |  |  |  |  | CICU3876605 |  |  |  | Thermo king | --- | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | ----/--- | ---/---/--- | Not proper | Not done | Breakdown | I have checked and found unit in breakdown condition, i inspected properly and found power fluctuations two much. Thats the reason for controller and power module defective. Both are suspected. | Yes | https://drive.google.com/open?id=1c-anVfAR0FYw7SZwftABDKC_X4lv5BtF | https://drive.google.com/open?id=1-DivEKjR_sVUQ5cqgbTSw2mZYiwrMoqc |  | 104 | Yes | Yes | Urgent | Above | Controller Power module | technician@crystalgroup.in | REEFER
AUG054/25 | 2025-08-28 12:05 | crm@crystalgroup.in | Qwik Supply | Ragesh TP | 9995585896 | Shift Executive | CICU3876626 |  |  | NA | Panambara , Malapuram | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-08-28 22:41 | 2025-08-25 |  |  |  |  | CICU3876626 |  |  |  | Thermo king | -40C sup. -38.0C ret. -34C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.5 bar dis. 18.3 bar | R 9.5A B 9.3A Y 9.9A | 397V 397V 397V | Not done | Pm service and general inspection | Attended routine checkup of container verified all operating areas normal container functioning within range temperature. | No | https://drive.google.com/open?id=1EOr9VVgDGcmFElYSpwwoeJqfcNFad6DD | https://drive.google.com/open?id=1Mf__liyG-LSMzr38Cgp1p4OTyXUzULTt |  | 114 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
AUG055/25 | 2025-08-28 13:56 | crm@crystalgroup.in | ITC Ltd | DILIP KOMA | 8870815451 | Team Lead | PCIU6007065 | DOOR NOT CLOSING |  | Dillip.Kumar@itc.in | Bangalore | Running with issues | Suspected Controller , I-O Board ,PCTC board | Call | Pushpa Mam | 2025-09-02 18:15 | service@crystalgroup.in | ITC | PCIU6007065 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | PM | have to check | NA | No | unit not working | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG055%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | NEMICHAND | Yes | DOOR NOT CLOSING | 2025-09-02 10:54 | operation@crystalgroup.in | YES | IN149 | 2025-09-02 | FOC | ITC | Banglore | CXRU1037294 | SITE | FOC | DAIKIN | [17 empty] | 2025-09-03 13:02 | 2025-08-31 |  |  |  |  | PCIU6007065 |  |  |  | Daikin | No | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Breakdown | Breakdown | Breakdown | Not done | Pm service and general inspection | We have checked mcb input and output voltage ok Transformer in put ok but output not ok so transformer need to replace. | Yes | https://drive.google.com/open?id=1z_rkT3Hk9szU3XiBGSNcdB1o1MtHy71m | https://drive.google.com/open?id=1_GUyuXNbNZ_iOfjoq73-kQg5zSkvNirM |  | 121 | No | Yes | Urgent | No | Transformer | technician@crystalgroup.in | REEFER
AUG056/25 | 2025-08-28 18:02 | crm@crystalgroup.in | Dr Reddy CTO 3 | ASHOK | 8978577878 | NA | GSOU6384240 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-08-29 21:52 | 2025-08-28 |  |  |  |  | GSOU6384240 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Rusty | Need to replace | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | 3/150 | 9.9/10/10 | 406/407/406 | Not done | carrier thin line unit found compressor low pumping and not discharged gas proper pressureand one Evaprator motor grounded with evp.coil rust found due to chemicals inside effect | replace gas and filter drier but compressor not compression gas low pumping, suggest to replace Complit unit due to multi malfunction and carrying. | Yes | https://drive.google.com/open?id=1Cv74anFjLlj4qv4f8nvBEt20QgGxXitR | https://drive.google.com/open?id=1bS7W6BrRa3lL3g_evKqB4V1F0pJkyYm4 |  | 115 | Yes | No | Can be done on next PM | reefer unit need to fixed once available on site | Complit reefer unit any model | technician@crystalgroup.in | REEFER
AUG057/25 | 2025-08-29 09:39 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 6307373723 | Warehouse Manager | MYRU4518356 | REPAIRS & REPLACEMENT |  | gopal5.krishna@qwick.co.in | Lucknow | Running with issues | Repairing Od Container | Call | Pushpa Mam | 2025-09-29 16:11 | service@crystalgroup.in | Qwik Supply | MYRU45183545R1 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT IS IN OFF CONDITION | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD NEEDS TO REPLACE | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD. | Yes | COMPRESSOR CONTACTOR, AMBIENT SENSOR, PHASE CONTACTOR -2NOS, SUCTION SENSOR & ENTIRE KEYPAD NEEDS TO REPLACE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=AUG057%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | Yes | REPAIRS & REPLACEMENT
AUG058/25 | 2025-08-29 09:42 | crm@crystalgroup.in | Qwik Supply | Lalit Saini | 9928034131 | Manager | TRIU6680335 |  |  | lalit.saini@qwik.co.in | Jaipur | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-11-04 18:58 | 31/10/0025 |  |  |  |  | TRIU6680335 |  |  |  | Daikin | -30 Ret.-25.8C Sup.-23.6C | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | Suction LPT-23 Discharge HPT1278 | 12.7A 10.5A | 408V 408V 408V | Not done | I visited the site and thoroughly checked the entire unit. Everything is fine, including the wiring. However, the ambient sensor and supply sensor readings are out of range and need to be replaced. The compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | The ambient sensor and supply sensor readings are out of range and need to be replaced. The compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | Yes | https://drive.google.com/open?id=1IIonH4bq6YdnQncZ1hDklTVI7DrgU6kC | https://drive.google.com/open?id=1BJidBu1axOjNWdO7LILBaM_atxDp7EQr |  | 127 | Yes | Yes | Urgent | Compressor daikin Gas 5kg Filter drier Vacuum pump Ambent sensor Supply sensor 2 nos | Compressor daikin Gas 5kg Filter drier Vacuum pump Ambent sensor Supply sensor 2 nos | technician@crystalgroup.in | REEFER
AUG059/25 | 2025-08-29 09:44 | crm@crystalgroup.in | Qwik Supply | Deepak Singh | 9254012557 | NA | TITU9927240 |  |  | Deepak91.Singh@ril.com | Sonipat, Haryana | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-04 17:23 | 2025-09-04 |  |  |  |  | TITU9927240 |  |  |  | Thermo king | 3.2, supply 3.9, Return 4.1 | Clean | Clean | https://drive.google.com/open?id=1MDVc_EIvEPvrnE8IsObGTd6d7-Roz3Mr | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2b 16.7b | 11.1A 11.1A 11.1A | 407v 407v 407v | Short | Pm service and general inspection done | I have checked all functions working properly. Display visible properly need to replace. Battery need to replace | Yes | https://drive.google.com/open?id=1qhreKamdG0gg4cOvpVryblBStldJ3JeQ | https://drive.google.com/open?id=1RDpa-ClSoDTlp5e2LLx8rBpaOu221Ntj |  | 117 | Yes | Yes | Urgent | Parts need to arrange | Battery for mp 4000 Display for mp 4000 | technician@crystalgroup.in | REEFER
AUG060/25 | 2025-08-29 09:51 | crm@crystalgroup.in | Qwik Supply | VEER SHING | 9813816264 | Supervisor | TRIU6618391 |  |  | NA | Sonipat, Haryana | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-04 09:29 | 2025-09-03 |  |  |  |  | TRIU6618391 |  |  |  | Carrier | -30 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.4 10.9b | 11.2 11.2 11.2 | 404v 404v 404v | Not done | Pm service | Double unit I have checked and found side unit have less gas and front unit giving alaram , i have checked found return sensor out of calibration and condenser pressure transducer out of range, both unit working with issue | Yes | https://drive.google.com/open?id=1SvsyUCba7fFSjJ91zIsvZnRBiNTtUjoA | https://drive.google.com/open?id=1rTlGC6W4dOfOnEtwSqVu2n7EMxlLO5aH |  | 117 | Yes | Yes | Urgent | Ys | Return sensor Condensor pressure transducer Gas 2 kg 134a | technician@crystalgroup.in | REEFER
AUG061/25 | 2025-08-29 09:57 | crm@crystalgroup.in | Qwik Supply | VEER SINGH | 9813816264 | MST | CICU2779914 |  |  | NA | Kamaspura, Haryana | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-04 09:20 | 2025-09-03 |  |  |  |  | CICU2779914 |  |  |  | Thermo king | -40 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9b 16.7b | 7.8 7.8 7.8 | 404v 404v 404v | Not done | Pm service | I have fully inspect unit it working fine , condensor coil has been washed due to durty | No | https://drive.google.com/open?id=1cLUaD_suLq10u4SjNeAgFwDFXnZTvRwP | https://drive.google.com/open?id=1So5WSgL759nd3dSYHa8WrzET_SYiDijP |  | 117 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG062/25 | 2025-08-29 09:59 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | MYRU4501435 |  |  | Nitin55.Sharma@ril.com | Sirhind, Punjab | Preventive Maintenance |  | Call | Pushpa Mam
AUG063/25 | 2025-08-29 10:01 | crm@crystalgroup.in | Qwik Supply | Nitin Sharma | 7015996489 | Operations Manager | NYKU7931452 |  |  | Nitin55.Sharma@ril.com | Sirhind, Punjab | Preventive Maintenance |  | Call | Pushpa Mam
AUG064/25 | 2025-08-29 10:06 | crm@crystalgroup.in | Qwik Supply | NIRAV | 8082455555 | OPERATION MANAGER | CICU3876570 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-26 10:33 | 2025-09-16 |  |  |  |  | CICU3876570 |  |  |  | Thermo king | -4.0c. Supply -37.0'c, Return -35.0'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1B 16.4B | 9.2A 9.2A 9.2A | 402, 402, 402 | Short | Pm service | Unit working fine, stuffed with PCM paid 1200' nos | No | https://drive.google.com/open?id=1VGmQH-HjMx0NnnFYd5n63Q6Hr4QChbnB | https://drive.google.com/open?id=1ekGqRAdsrFK23hqs5blsE866-PQlh2zY |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG065/25 | 2025-08-29 10:08 | crm@crystalgroup.in | Qwik Supply | RAJVEER YADAV | 8826818750 | CPC MANAGER | TCLU1130265 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-16 14:04 | 2025-09-16 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | 3.0'c, sup. 3.2'c return 3.1'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 16.2B | 7.2A 7.2A 7.2A | 404V 404V 404V | Short | Pm service | Unit working in good condition, coil has been washed | No | https://drive.google.com/open?id=1BnCWXnEjgx-li1tsLWLoy5oFf_GCmWCI | https://drive.google.com/open?id=11346jASf8qPcljQYtXBLVoNAZHx7czez |  | 118 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG066/25 | 2025-08-29 10:35 | crm@crystalgroup.in | Qwik Supply | DEEPAK S | 8814085199 | ASST. CPC MANAGER | CXRU1045453 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-16 14:01 | 2025-09-16 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -18'c, supply-19.9'c return-17'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 2.1B 12.4B | 9.2A 9.2A 9.2A | 402V 402V 402V | Short | Pm service | Unit working in good condition, coil has been washed | No | https://drive.google.com/open?id=1F1Ht5GswPCEVCrBI-5HQxjB_oekJP-iz | https://drive.google.com/open?id=1Yr8-2Lorflm1S1urZgTcoEPc0dO4p_q2 |  | 118 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG067/25 | 2025-08-29 10:37 | crm@crystalgroup.in | Qwik Supply | Surjit Singh | 9779944073 | NA | CICU3876631 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-16 13:57 | 2025-09-16 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | Pm service | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1B 16.4B | 9.2A 9.2A 9.2A | 402V 402V 402V | Short | Pm service | Unit working in good condition, coil has been washed , battery need to replace | No | https://drive.google.com/open?id=1nQvaBLUxpy6tQln4lv6VcyaVro87Sg6i | https://drive.google.com/open?id=1rvSvJ7M3kJuj5zauqMVaCjyNTyN8smYS |  | 118 | Yes | Yes | Urgent | Battery Installation | Battery mp 4000 | technician@crystalgroup.in | REEFER
AUG068/25 | 2025-08-29 10:41 | crm@crystalgroup.in | Qwik Supply | Ajit Sisodiya | 9729277445 | NA | CICU8118130 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-16 13:53 | 2025-09-16 |  |  |  |  | CICU8118130 |  |  |  | Thermo king | -20'c, supply-19.2'c , Return-18'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 16.4B | 9.1A 9.1A 9.1A | 402V 402V 402V | Short | Pm service | Unit working in good condition, coil has been washed | No | https://drive.google.com/open?id=1G0QavFbZSli9yz3JUkXT_sNqB3_Iek_l | https://drive.google.com/open?id=1fxrvr66nnbCLS54P4yDWRkYszyGpiuml |  | 118 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG069/25 | 2025-08-29 10:47 | crm@crystalgroup.in | Qwik Supply | Ajit | 9729277445 | Manager | SJKU4000022 |  |  | NA | Rajpura, Punjab | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-16 13:46 | 2025-09-16 |  |  |  |  | SJKU4000022 |  |  |  | Carrier | 2.0, sup. 2.0 ,Return 1.9c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 11.4B | 6.1A 6.1A 6.1A | 402V 402V 402V | Short | Pm service | Unit working in good condition, coil has been washed. | No | https://drive.google.com/open?id=1_mI18pXX4_2b7o3yyc5jFAbBGn1jxcqd | https://drive.google.com/open?id=1t_dD6kQm1hnmHiXGuSgyb_nOE1I8VghV |  | 119 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
AUG070/25 | 2025-08-29 10:58 | crm@crystalgroup.in | The Amritsar District Cooperative Milk Producers Union Limited | Hazoor Singh | 7888747805 | Manager | CXRU1186385 |  |  | engg.asr@verka.coop | Amritsar | Preventive Maintenance |  | Call | Pushpa Mam
AUG071/25 | 2025-08-29 17:31 | crm@crystalgroup.in | Quick supply chain PVT LTD | NA | NA | NA | CICU2779940 |  |  | NA | COACHIN | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-29 17:43 | 2025-08-29 |  |  |  |  | CICU2779940 |  |  |  | Thermo king | -40C Rat. -33.7C sup. -37C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc. 1.0 bar dis. 15.6 bar | R 8.9A B 8.7A Y 9.4A | 404A 404A 404A | Not done | Pm service and general inspection | Attended rutine checkep of container verified all operation are normal container functioning within range temperature | No | https://drive.google.com/open?id=1aE2iUZ85vveQ-1IrdmRHmZ72z39KCBnn | https://drive.google.com/open?id=1_kdnLPNsbdOm189eOq5Qx3LPcccY-NUh |  | 114 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP001/25 | 2025-09-02 10:48 | crm@crystalgroup.in | Swadesh Milk | RAJESH UPADHYAY | 8077759700 | NA | GESU9290991 | EVAPORATOR COIL INTERNAL LEAK |  | NA | Lucknow | Complete Breakdown |  | Call | PUSHPA MAM | 2025-09-06 15:27 | service@crystalgroup.in | SWADESH MILK DAIRY | GESU9290991 | 40FT STD RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | CHARGEABLE | UNIT HAS MULTIPLE LEAK FROM EVP COIL... | NEED TO REPLACE THE EVP COIL | EVP COIL | Yes | Unit i | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP001%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SITARAM | Yes | EVAPORATOR COIL INTERNAL LEAK | [29 empty] | 2025-09-09 14:56 | 2025-09-02 |  |  |  |  | GESU9290991 |  |  |  | Carrier | Breakdown | Clean | Clean |  | Okay | Leakage | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Need to replace |  | Breakdown | Breakdown | Breakdown | Not done | No gas found in system, have checked with n2 test found leakage in evaporator coil need to change | Need to change evaporator coil, not possible to brizing | Yes | https://drive.google.com/open?id=1wSodowz1v11-LCokFU0ZAHqX5q6my1zN | https://drive.google.com/open?id=1ulxbJrcUkyExPfeMr3nT2E4Gqa2lEi1D |  | 116 | Yes | Yes | Urgent | Same | Evaporator coil Gas r134a 4.5kg Filter drier Brizing new coil N2 test | technician@crystalgroup.in | REEFER
SEP002/25 | 2025-09-02 10:52 | crm@crystalgroup.in | Swadesh Milk | RAJESH UPADHYAY | 8077759700 | NA | NYKU7932356 | CONDENSOR FAN NOT WORKING |  | NA | Lucknow | Running with issues | CONDENSOR FAN NOT WORKING DUR TO CAPACITOR WEAK | Call | PUSHPA MAM | 2025-09-06 15:32 | service@crystalgroup.in | SWADESH MILK DAIRY | NYKU7932356 | 40FT STD RF | CARRIER THINLINE | SERVICE-AT SITE | SALE | AMC | WORKING FINE | UNIT IS WORKING FINE | NO | No | UNIT IS WORKING FINE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP002%2F25 | Carrier | CARRIER-THINLINE | NA | NA | NA | Used | NA | SITARAM | Yes | CONDENSOR FAN NOT WORKING | [29 empty] | 2025-09-09 09:50 | 2025-08-30 |  |  |  |  | NYKU7932356 |  |  |  | Carrier | -24 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b 14.7b | 11.4A 11.4A 11.4A | 398v 398v 398v | Short | Pm service | Condensor capacitor found weak and has been change , unit working fine | No | https://drive.google.com/open?id=1-VI-g2d6CiBA205F5Jh7I4jndE40Rcxc | https://drive.google.com/open?id=154yaCq2FUJsC1fUSC3eIEF9UhxtrWczX |  | 116 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP003/25 | 2025-09-02 10:57 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering | CXRU1030387 |  |  | brahmaiah.g@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-06 10:03 | 2025-08-31 |  |  |  |  | CXRU1030387 |  |  |  | Daikin | -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/7 & 180/190 psig | 9.9/10. 10/9.9. 10.9.9 | 402/401/401 | Short | Two way unit for pm service | Two way daikin unit pm service completed | No | https://drive.google.com/open?id=1UkH8dFHZ3Pro2LN9gUwU6wypZFAw1Aoa | https://drive.google.com/open?id=1VXLGuXewmJWSAJs40Yeew5YX-NwaBN89 |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP004/25 | 2025-09-02 11:00 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering | MYRU4500887 |  |  | brahmaiah.g@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-06 10:11 | 2025-08-29 |  |  |  |  | MYRU4500887 |  |  |  | Daikin | -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/.7. & 180/190 psig | 9.8/9.8. 9.9/9.8. 9.9/9.8 | 412/413/413 | Short | Two way unit for pm & observe main unit compressor not working noisy with mechanical issue internal. | Pm completed. Suggest to replaced complete reefer unit | No | https://drive.google.com/open?id=1BtaPM6QlIEvgw7ejI-BBBRsK_RMMuEvr | https://drive.google.com/open?id=1JERXmNo5dAN90Uby7sF-aebucvB607aZ |  | 115 | No | No | Can be done on next PM | Na | na | technician@crystalgroup.in | REEFER
SEP005/25 | 2025-09-02 11:50 | operation@crystalgroup.in | ITC Ltd | DILIP KOMA | 8870815451 | Team Lead | CXRU1037294 |  |  | Dillip.Kumar@itc.in | Bangalore | Preventive Maintenance |  | Call | Pushpa Mam | [25 empty] | 2025-09-02 12:24 | operation@crystalgroup.in | YES | IN150 | 2025-09-02 | FOC | ITC LImited | Bangalore | CXRU1037294 | SITE | FOC | DAIKIN | [17 empty] | 2025-09-03 13:33 | 2025-08-31 |  |  |  |  | CXRU1037294 |  |  |  | Daikin | Breakdown | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Breakdown | Breakdown | Breakdown | Not done | Pm service | I have inspection this unit and found issues phase contactor and inlet sensor are defective and the f1 fuse is blowing repeatedly due to phase contactor and inlet sensor. | Yes | https://drive.google.com/open?id=1cXyZYEuYG27YlG2mewK3IRCyePmOKWKU | https://drive.google.com/open?id=1ViMj-oQKE0zpTB8xk1-ot4qlG_zXS58n |  | 121 | No | No | Urgent | No | Phase contactor (pcc2) Inlet sensor Fuse 10A 5 nos | technician@crystalgroup.in | REEFER
SEP006/25 | 2025-09-02 12:50 | crm@crystalgroup.in | ITC Ltd | DILIP KOMA | 8870815451 | Team Lead | CAIU5404270 |  |  | Dillip.Kumar@itc.in | Bangalore | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-03 13:21 | 2025-08-31 |  |  |  |  | CAIU5404270 |  |  |  | Daikin | +4C Ret.+5.0C Sup.+4.1C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | LPT150 HPT 1800 | 17.2A 12.4A | 410V 410V 410V | Not done | Pm service and general inspection | Attended routine checkup of container verified all operational are normal container within range temperature | No | https://drive.google.com/open?id=1KFrr2K45ssVY54vWVBwlLRloo6cH-LgT | https://drive.google.com/open?id=1zG_bcVNy0QybD8F_DRlldIg0Zy2wZ6eS |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP007/25 | 2025-09-02 13:17 | crm@crystalgroup.in | QUICK SUPPLY RELIANCE | AVINASH | 9281026402 | SHIFT INCHARGE | CICU1799177 |  |  | NA | Shamshabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-08-30 20:27 | 2025-08-30 |  |  |  |  | CICU1799177 |  |  |  | Thermo king | -40c | Clean | Clean | https://drive.google.com/open?id=18weUa-XBny_ZhxBsyAkAHoZwO5ORo8yd | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1teYAXYpOdFwZdCZZaDdUqxYnjPji_7xA | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18 br | 10.2/10.3/10.2 | 415/414/414 | Short | pm service due | pm service completedand unit working as satisfactory | No | https://drive.google.com/open?id=1XKquXDSIJzjWQcgZSGsLI7DOC5Pmk4vo | https://drive.google.com/open?id=1kptCPkUjm-FYvGUADBPolGOzUnLp7yrD |  | 115 | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
SEP008/25 | 2025-09-02 13:22 | crm@crystalgroup.in | Hetero Unit 5 | B. SHYAMSUNDER | 9154266430 | Asst Manager | SUDU6218004 |  |  | ShyamSunder.B@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-02 22:54 | 2025-09-01 |  |  |  |  | SUDU6218004 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay | https://drive.google.com/open?id=1dWUkXzj4Z8DFwYqeDimcsz8K-yAVb4SH | Okay | https://drive.google.com/open?id=109HitTZXyyE0Fu0ux34adNmghhpN2xdH | Okay |  | Okay | Okay | https://drive.google.com/open?id=1gwxUdj2ZP-QyFKBiyFNcW_sisypwAw4Y | Okay | https://drive.google.com/open?id=1r4F9V8FOdIys_xRCVKsga8-Rc7F2oE7G | Okay | Okay | Okay | Done | Clean |  | 9/180 psig | 11.2/11.3/11.3 | 406/405/405 | Short | unit working as satisfactory | pm Complited with fixed Man trap | No | https://drive.google.com/open?id=11g18T6GTG0prmDrldXoOkkDmBlvr8bWc | https://drive.google.com/open?id=17EGuiCM9Ps76Gc983z-mWZK8hQZw2rut |  | 115 HYD | No | No | Can be done on next PM | na | na | technician@crystalgroup.in | REEFER
SEP009/25 | 2025-09-02 16:31 | crm@crystalgroup.in | Qwik Supply | VEER SHING | 9813816264 | Supervisor | TRIU6618391 |  |  | NA | Sonipat, Haryana | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-11 12:42 | 2025-09-03 |  |  |  |  | TRIU6618391 |  |  |  | Carrier | -30'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Double unit 0.6B 14.2B 0.5B 9.2B | 14.4A 14.4A 14.4A | 402V 402V 402V | Not done | Pm service | Double unit, One unit working fine but showing return sensor out of calibration and condensor pressure transducer need to replace. Second unit I have checked nd found low gas in system need to to pup 2 kg r134gas. Need to update software also | Yes | https://drive.google.com/open?id=12t0TorJ-ENZxgJbbS7CtOdGIcxDFY4U1 | https://drive.google.com/open?id=1xz7jBXsIEWrcWQMjcoJMrDlxWkdogknv |  | 118 | Yes | Yes | Urgent | Samae | Return sensor Condensor pressure transducer 2kg gas r134a Software update | technician@crystalgroup.in | REEFER
SEP010/25 | 2025-09-02 16:35 | crm@crystalgroup.in | Qwik Supply | Deepak Singh | 9254012557 | NA | TITU9927240 |  |  | Deepak91.Singh@ril.com | Sonipat, Haryana | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-04 17:30 | 2025-09-04 |  |  |  |  | TITU9927240 |  |  |  | Thermo king | 3.2, | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Partially defective |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2B 16.7B | 11.1A 11.1A 11.1A | 407v 407v 407v | Short | Pm service and general inspection | I have checked all functions working properly. Display visible properly need to replace. Battery need to replace | Yes | https://drive.google.com/open?id=1_EDem7ylQtrzYOToQVRV2lAxkXY7gmrW | https://drive.google.com/open?id=1SAnxA4mQr-KhQk0CO2x94q7D6sv2DL4L |  | 117 | Yes | Yes | Urgent | Same parts need to replenishment | Battery for mp4000 Display for mp 4000 | technician@crystalgroup.in | REEFER
SEP011/25 | 2025-09-02 16:39 | crm@crystalgroup.in | Qwik Supply | VEER SINGH | 9813816264 | MST | CICU2779914 |  |  | NA | Kamaspura, Haryana | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-11 12:35 | 2025-09-04 |  |  |  |  | CICU2779914 |  |  |  | Thermo king | -40'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 16.2B | 11.4A 11.4A 11.4A | 404V 404V 404V | Short | Pm service | Unit working fine no issues found, condensor coil washed | No | https://drive.google.com/open?id=1o7AsZwft-FVEToRbTxGiV6acS9BwbEfW | https://drive.google.com/open?id=1oYnJKXVMK6QxcXZDCUITi_NmjV5bxrgr |  | 117 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP012/25 | 2025-09-02 17:23 | crm@crystalgroup.in | Tata Advanced Systems Ltd | Sachin | 7337832756 | NA | CZZU6009100 |  |  | NA | Bangalore | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-03 08:54 | 2025-09-01 |  |  |  |  | CZZU6009100 |  |  |  | Daikin | -20C Ret.-10.4C Sup.-18.6C | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | LPT45 HPT1002 | 7.9A 14.3A | 415V 415V 415V | Not done | Pm service and general inspection | I visited the site and found the container wasn't cooling. Upon inspection, I found no ice. After removing the cover, I noticed the left side evaporator motor blade had broken and fallen onto the coil, causing the issue. Additionally, the keypad and display are also damaged and will need to be replaced. | Yes | https://drive.google.com/open?id=1gtDqPTN9cI0FXXLMtZQ_kPADcHal_WU5 | https://drive.google.com/open?id=10Tp751eZQe5nD1l9s_uJeN4_iP9LFfiz |  | 120 | No | No | Can be done on next PM | No | Evaporator motor with fan blade Keypad set Display | technician@crystalgroup.in | REEFER
SEP013/25 | 2025-09-02 17:25 | crm@crystalgroup.in | Tata Advanced Systems Ltd | Sachin | 7337832756 | NA | CBHU2811760 |  |  | NA | Bangalore | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-03 09:01 | 2025-09-01 |  |  |  |  | CBHU2811760 |  |  |  | Carrier | -20C Ret.-18.9C Sup.-23.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc. 0.4 bar Dis. 12.3bar | 13.7A 13.6A 13.4A | 430V 430V 430V | Not done | Pm service and general inspection | Attended routine checkup of container.Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1yPnwRkYxvZjEcK8pprLAA0n9X-Lf00-Z | https://drive.google.com/open?id=1vRAjNhJGNynXDz78pJ041LCCWT-a5jSD |  | 120 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP014/25 | 2025-09-03 09:59 | crm@crystalgroup.in | Chemplast Sanmar Limited | C. MOHAN | 04344 350400 2218 | JOINT MANAGER | HDMU5501938 |  |  | NA | BERIGAJ, HOSUR | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-03 12:49 | 2025-09-02 |  |  |  |  | HDMU5501938 |  |  |  | Daikin | 0.0C Ret.+2.5C Sup.-0.5C | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | LPT122 HPT 1561 | 11.6A 15.7A | 409V 409V 409V | Not done | Pm service and general inspection | I visited the site and found the container wasn't cooling. Upon inspection, I found no ice. After removing the cover, I noticed the evaporator motor blade had broken and fallen onto the coil, causing the issue. Additionally, the keypad and display are also damaged and will need to be replaced. | Yes | https://drive.google.com/open?id=1yMmUhQQ-GE3sOc87gPhdAKO8DGULrBfM | https://drive.google.com/open?id=1W42FgIx-2P836eUuXI5TCwj7X0rF6r5d |  | 121 | No | No | Can be done on next PM | No | 1)Evaporator motor with fan blade 2)Control panel with sheet key without display | technician@crystalgroup.in | REEFER
SEP015/25 | 2025-09-03 11:29 | crm@crystalgroup.in | ITC Ltd | Khaja / Sivakumar | 9493514469 | NA | MYRU4519748 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | Tadikonda.Sivakumar@itc.in | Bapatla | Running with issues | Container got malfunctioning | Email | Pushpa Mam | 2025-10-10 12:45 | technician@crystalgroup.in | ITC Ltd | MYRU4519748 | 40RF | Daikin | SERVICE-AT SITE | NA | NA | Unit not maintaining temperature | Need to fix | Inlet sensor Outlet sensor suction sensor | Yes | Unit not working properly due to sensor issu | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP015%2F25 |  | DAIKIN LXE10E | Na | Na | Na | Na | Na | RAMESH | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-17 12:00 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 12:01 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 12:01 | crm@crystalgroup.in | NO
SEP016/25 | 2025-09-03 11:34 | crm@crystalgroup.in | ITC Ltd | Khaja / Sivakumar | 9493514469 | NA | TRIU8214763 | FLUCTUATIONS IN TEMEPRATURE |  | Tadikonda.Sivakumar@itc.in | NELLORE | Running with issues | Container got malfunctioning | Email | PUSHPA MAM | 2025-10-10 17:41 | service@crystalgroup.in | ITC Ltd | TRIU8214763 | 40RF | CARRIER THINLINE | NA | LEASE | FOC | UNIT WAS HAVING ISSUES & CONTRACT HAS BEEN OVER SO CALLING BACK. | need to inspect the unit after callback |  | No | unit is calling back to depot as contract is over | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP016%2F25 | CARRIER THINLINE | CARRIER-THINLINE | 2308L36915 | MSB60272115 |  | USED | "JSGA623040194 " | Shubham | No | FLUCTUATIONS IN TEMEPRATURE | 2025-10-20 12:30 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 12:31 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 12:31 | crm@crystalgroup.in | NO
SEP017/25 | 2025-09-03 19:05 | crm@crystalgroup.in | Qwik Supply Bhiwadi | Ganesh Minde | 95107 75974 | NA | CICU1799161 | Water Leackage inside the container |  | ganesh.minde@ril.com | Bhiwandi | Running with issues |  | Call | Pushpa Mam | 2025-09-03 17:51 | service@crystalgroup.in | Crystal Depot | NA | NA | NA | NA | STOCK | NA | - | - |  | Yes | - | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP017%2F25 | NA | NA | NA | - | - | - | - | NO | No | Water Leackage inside the container | 2025-10-08 13:36 | service@crystalgroup.in | NO | [9 empty] | 2025-10-08 13:36 | service@crystalgroup.in | NO |  |  |  |  | 2025-10-08 13:37 | service@crystalgroup.in | NO
SEP018/25 | 2025-09-04 14:52 | crm@crystalgroup.in | Kirloskar Corrocoat | Santosh | 7796660071 | NA | TCLU1912006 | TRIPING |  | NA | Belhari | Running with issues | CONTAINER IS TIPING | Call | PUSHPA MAM | 2025-10-10 17:52 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | TCLU1912006 | 20RF | DAIKIN | SERVICE-ON CALL | LEASE | FOC | UNIT TRIPPING | UNIT IS WORKING FINE AS PER CUSTOMER | NA | No | UNIT TRIPPING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP018%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | No | TRIPING | 2025-10-20 12:32 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 12:32 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 12:32 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-09 21:39 | 2025-10-14 |  |  |  |  | TCLU1912006 |  |  |  | Carrier | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | On ca | Not done | Unit tripping | After video call details investigation found external tublight connecting faulty, remove light connecting restart unit working fine. Maintain temperature | No | https://drive.google.com/open?id=1ZzjeBlGZ_WZDceHgzAwbSPbEwQjK5Ms9 | https://drive.google.com/open?id=1NkYHSJQorB3_ZD9gp5U0ztr4vydcfu9- |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP019/25 | 2025-09-04 19:27 | crm@crystalgroup.in | Curia India Pvt.Ltd. | Purushottam Desai | 9637780772 | Manager - Electrical | TRIU6680649 | UNITS NOT WORKING |  | Purushottam.Desai@curiaglobal.com | Aurangabad | Complete Breakdown | CARRIER CONTROLLER REQUIRED | Email | PUSHPA MAM | 2025-09-29 16:32 | service@crystalgroup.in | Curia India Pvt.Ltd. | TRIU6680649 | 20RF | CARRIER THINLINE | SERVICE-ON CALL | LEASE | FOC | UNIT IS WORKING FINE AS PER CLIENT. | NAT | NA | No | UNIT IS WORKING FINE AS PER CLIENT. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP019%2F25 | CARRIER | CARRIER-THINLINE | NA | NA | NA | USED | NA | SITARAM | No | UNITS NOT WORKING | 2025-09-29 16:35 | crm@crystalgroup.in | NO | [9 empty] | 2025-09-29 16:36 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-29 16:37 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-17 14:16 | 2025-10-15 |  |  |  |  | TRIU6680649 |  |  |  | Carrier | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na Na Na | Na | Na | Not done | Na | Unit working fine as per clint | No | https://drive.google.com/open?id=1IM_x4SO6U-bOjQumfznfZKLI6icjtZw7 | https://drive.google.com/open?id=1f8biy4DAfB5Uwtim6hrel0lvb1yLvMFi |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP020/25 | 2025-09-05 16:57 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | ENGINEER | PCIU6008328 | REPAIRS & REPLACEMENT |  | madhusoodhana.k@sailife.com | Bidar | Running with issues | REEFER UNIT INSTALLATION | Call | PUSHPA MAM | 2025-09-06 15:38 | service@crystalgroup.in | SAI LIFE SCIENCE | PCIU6008328 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT NOT WORKING | REPLACEMENT OF REEFER UNIT | REEFER MACHINERY UNIT | MACHINERY UNIT SWAPPING | UNIT NOT WORKING | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP020%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | JSGA622340291 | SHAHBUDDIN | Yes | REPAIRS & REPLACEMENT | [29 empty] | 2025-09-11 19:38 | 05/09/0025 |  |  |  |  | PCIU6008328 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/180 psig | 12.8/12.4/12.8 | 402/403/402 | Short | Main unit before failure against recomnded carrier thin | New good one complit reefer unit Instalation completed | No | https://drive.google.com/open?id=1dcB-555wRIvWeeVpmOdouV-zn2aL3I1A | https://drive.google.com/open?id=1991YRZe5XWV5DdgsHFtWdfX3vGCQrafj |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP021/25 | 2025-09-06 09:51 | crm@crystalgroup.in | Scootsy Logistics Private Limited | Fasil Firos | 9633212918 | NA | CRIU4023016 |  |  | NA | Bangalore | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-06 17:32 | 2025-09-04 |  |  |  |  | CRIU4023016 |  |  |  | Thermo king | +2C Ret.+5.8C Sup.+1.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc. 0.4bar Dis. 17.4bar | R 6.0A B 6.5A Y 5.2A | 392V 392V 392V | Short | Pm service and general inspection CCTV camera installation | Attended routine checkup of container verified all operational are normal container functioning within range temperature | No | https://drive.google.com/open?id=1O_FPhrX-fP9Tpsl1e3CI6b-Z4K_BXhde | https://drive.google.com/open?id=1OxtVMiPqmnpUsS6oD3VL2Kgbug8UIIoW |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP022/25 | 2025-09-06 12:34 | crm@crystalgroup.in | Scootsy Logistics Private Limited | Fasil Firos | 9633212918 | NA | CRIU4023021 |  |  | NA | Bangalore | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-06 17:42 | 2025-09-06 |  |  |  |  | CRIU4023021 |  |  |  | Thermo king | -24C Ret.-7.6C Sup.-15.7C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc. 1.2bar Dis. 18.3bar | R 11.4A B 10.8A Y 10.9A | 380V 380V 380V | Not done | Pm service and general inspection CCTV camera installation | Attended unit at factory and observed alarm temperature deviation from set point due to frequent door openings. Unit is functioning properly, but excessive ice accumulation on the floor is noted. Removing ice without unloading cargo isn't feasible. | No | https://drive.google.com/open?id=1ZmP1Mxb5PMoBT_U_B7hxrXri7c2Mpulm | https://drive.google.com/open?id=1rf9YUR2mJpJZjfxdQdq_mDoZ4R8rvPDD |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP023/25 | 2025-09-06 13:30 | crm@crystalgroup.in | Devis Lab-Hyderabad | Surarchit | +91 96527 25368 | On Duty Officer | DC- SEZ UNIT I |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-08 22:55 | 02/09/0025 |  |  |  |  | DC- SEZ UNIT I |  |  |  | Carrier | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/180 psig | 12.4/12.5/12.4 | 414/415/414V | Short | Unit working as satisfactory | Spare power socket delever nos.6 female socket. And unit run & test with run found satisfactory. | No | https://drive.google.com/open?id=1YaQgIbl5eYUClQmtTsPs5VvUzHb1hyyA | https://drive.google.com/open?id=1cx1o8RY2nIcSg41axXOeVLpOYzVK3wnP |  | 115 | No | No | Can be done on next PM | Na | MA | technician@crystalgroup.in | REEFER
SEP024/25 | 2025-09-08 09:51 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | HDMU5542114 | REPAIRS & REPLACEMENT |  | Madhusoodhana.k@sailife.com | Bidar | Running with issues | HEATER CONTACTOR PROBLEM | Call | PUSHPA MAM | [54 empty] | 2025-09-10 18:54 | 06/09/0025 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/195 psig | 12.3/12.4/12.4 | 407/408/407 | Short | Duty Engineer reported for Heter alram reflection Al61, checked unit found Heter. Contactor internal points Defective, need to replaced . | Run unit observation and clean & fixed temperley heater contactor. | Yes | https://drive.google.com/open?id=1hCaQTSUwnxVHx8pmuFRcY7VYfw1f4G1T | https://drive.google.com/open?id=1WprQat1dP1WIJ_4EOpUnvW8GIHwr-crg |  | 115 | No | No | Can be done on next PM | Need to replaced HTR CONTACTOR | 12 A - HTR CONTACTOR | technician@crystalgroup.in | REEFER
SEP025/25 | 2025-09-08 09:56 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6031328 | FLUCTUATIONS IN TEMEPRATURE |  | Madhusoodhana.k@sailife.com | Bidar | Running with issues | CHANGE OF DISPLAY COVER & TEMPERATURE SENSPR CHANGE 3 UNITS | Call | PUSHPA MAM | [54 empty] | 2025-09-10 18:38 | 07/09/0025 |  |  |  |  | PCIU6031328 |  |  |  | Daikin | +21c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 9.5/185 psig | 10.0/10.1/10.0 | 408/407/408V | Short | Issue reported bySAILAB Duty Engineer- AlE402//Al E403/& Al E404 | Temperley reset & observe and test done & found need to replaced sensers. | No | https://drive.google.com/open?id=1DWvLOOUknnFqSd-_1LzMs5OAVhlbmIgp | https://drive.google.com/open?id=1TWx6FhzMhNk7iCJ1peEl3rWSwkMPAHSO |  | 115 | No | No | Can be done on next PM | Sensors replacement | Temp. Sensors for Daikin | technician@crystalgroup.in | REEFER
SEP026/25 | 2025-09-08 13:04 | crm@crystalgroup.in | UPS | Nadeem & K.Venkatesh | 9700137866 & 99517 80321 | CRM | SJKU4000110 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | nadeemuddin.mohammed@marken.com | Hyderabad | Running with issues | temp 2 to 8 - no power genset on but temp is not meeting | Call | PUSHPA MAM | 2025-09-29 17:30 | service@crystalgroup.in | UPS | SJKU4000110 | 40RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | SET TEMP ISSUE | SET TEMP WAS +20.0C & THE SAME WAS CHANGED TO +3.5C BY INCREASING THE DISPLAY BRIGHTNESS. | NO | No | SET TEMP ISSUE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP026%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-09-29 17:42 | service@crystalgroup.in | NO | [9 empty] | 2025-09-30 11:59 | crm@crystalgroup.in | NO |  |  |  |  | 2025-09-30 11:59 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-09 17:50 | 2025-09-22 |  |  |  |  | SJKU4000110 |  |  |  | Thermo king | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/19bar | 10.2/10.3/10.3 | 412413/412 | Short | Pm service,& clints request for set temperature changed. +20c to +4c | Pm service completed with checked unit operation & found working as satisfactory. Changed unit set temp.from +20c to +4c | No | https://drive.google.com/open?id=1F7ZlnLR5ao0NVHsrpaAz3FUaGpNLdLh0 | https://drive.google.com/open?id=14tsxzIM2bQ7cpeqcE-CLiLc6KOXrRMrp |  | 115-SHABUDIN - HYD | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP027/25 | 2025-09-08 17:39 | crm@crystalgroup.in | Devis science Pvt. Ltd | Surarchit | 9652725368 | On Duty Officer | CRIU4025024 | INSTALLATION AT SITE |  | NA | Hyderabad | Installation |  | Call | PUSHPA MAM | [54 empty] | 2025-09-10 23:17 | 08/09/0025 |  |  |  |  | CRIU4025024 |  |  |  | Thermo king | -25c & 2/8 c testing done | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19br | 9.8/9.9/9.8 | 380/382/382 V | Short | FOR INSTALATION QUALIFICATION | IQ- Instalation QUALIFICATIONto completed | No | https://drive.google.com/open?id=10lpJkFgR_QxX4F_ulGW8kedjWEhvM2mr | https://drive.google.com/open?id=12ihbWP1dLPnOlSGef9dwISTEGKkLHyKk |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP028/25 | 2025-09-08 17:41 | crm@crystalgroup.in | Devis science Pvt. Ltd | Surarchit | +91 96527 25368 | On Duty Officer | CRIU4025066 | INSTALLATION AT SITE |  | NA | Hyderabad | Installation |  | Call | PUSHMA MAM | [54 empty] | 2025-09-10 23:08 | 08/09/0025 |  |  |  |  | CRIU4025066 |  |  |  | Thermo king | -25c & 2/8 c test done for IQ | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/19br | 9.9//9.8/9.8 | 380/381/382 | Short | For IQ- INSTALATION QUALIFICATION | Instalation QUALIFICATION completed | No | https://drive.google.com/open?id=1WIhgu9AHaF5CrndnaB47z_g-DSIjk1ac | https://drive.google.com/open?id=1GxuZSxcah_HnnAikoiMCoE8CX7w9dmhT |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP029/25 | 2025-09-08 17:44 | crm@crystalgroup.in | Devis science Pvt. Ltd | Surarchit | +91 96527 25368 | On Duty Officer | CRIU4025050 | INSTALLATION AT SITE |  | NA | Hyderabad | Installation |  | Call | PUSHPA MAM | [54 empty] | 2025-09-10 22:59 | 08/09/0025 |  |  |  |  | CRIU4025050 |  |  |  | Thermo king | -25 & 2/8 testing | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19br | 10.1/10A/10A | 382/382/381V | Short | New container for Instalation | IQ- Instalation Qualification complit and test unit -25c & 2/8 c pass | No | https://drive.google.com/open?id=1llqMWZGVuwaaRjGMTV9mSRXXun-xAi59 | https://drive.google.com/open?id=1gUYn_1cJfvCi5rIrCVMAHerkTY-J-T8J |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP030/25 | 2025-09-08 17:46 | crm@crystalgroup.in | Devis science Pvt. Ltd | Surarchit | +91 96527 25368 | On Duty Officer | CRIU4025019 | INSTALLATION AT SITE |  | NA | Hyderabad | Installation |  | Call | PUSHPA MAM | [54 empty] | 2025-09-10 22:45 | 08/09/0025 |  |  |  |  | CRIU4025019 |  |  |  | Thermo king | -25c tested Instalation time with 2to 8 test | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18br | 9.9/10/9.9 | 380/381/381 v | Short | IQ | IQ - INSTALATION QUALIFICATION COMPLITED. | No | https://drive.google.com/open?id=1sgywTSqo-SDAk2JBu6wgO6xHtw3Y1vGX | https://drive.google.com/open?id=1vSHxQbc68YLwB29mZHuwOZoYkm_v-Qqn |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP031/25 | 2025-09-09 14:36 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd -Kutthur | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering | MYRU4500887 | REPAIRS & REPLACEMENT | container not working from 2 sep & still have problem | brahmaiah.g@hetero.com | KOTHUR | Running with issues | Daikin Thermoking Reefer Unit change | Call | Pushpa Mam | [54 empty] | 2025-09-20 00:23 | 2025-09-19 |  |  |  |  | MYRU4500887 TWO WAY |  |  |  | Daikin | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/190 psig | 12.2/12.4/12.2 | 398/399/398 | Short | Two way unit with side unit found completely break down | Two way side unit Instalation Done with good unit Daikin | No | https://drive.google.com/open?id=13EaXkKMFRgfcEj1ZVWCh9-mlRwWqgHm9 | https://drive.google.com/open?id=1zckMSGDzUyfA8_tPLqkGSY47Xtr4SG9i |  | 115-B | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP032/25 | 2025-09-09 15:11 | crm@crystalgroup.in | Transys Global Forwarding Private Limited-Sshamshabad | Venkata Sri Ranganath | +91 97037 36718 | Asst Manager – Air Freight | TITU8259378 | SERVICING |  | venkata.sriranganath@tgfworld.com | Hyderabad | Running with issues |  | Call | Pushpa Mam | 2025-10-14 12:39 | technician@crystalgroup.in | Transys Global Forwarding Private Limited-Sshamshabad | TITU8259378 | 20FT Spl RF with Wheels | Na | SERVICE-AT SITE | NA | NA | Temperature not maintain it set point | Need replacement | Evaporator coil sensor, 1 no's Supply sensor 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP032%2F25 | Thermo King MP-4000 | TK-MP4000 | Na | Na | Na | Used | Na | SHAHBUDDIN | Yes | SERVICING | [29 empty] | 2025-09-10 00:06 | 2025-09-09 |  |  |  |  | TITU8259378 |  |  |  | Thermo king | -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/28bar | 10.2/10.3/10.5 | 411/410/410 | Short | Unit temperature not archived set temp | Checked & found internal air flow way complit unit blocked with Ice.. Removed & ckean air flow after unit observe & working as satisfactory | No | https://drive.google.com/open?id=1E0hJB1--muXHOcRBH9yxDvx9kGvZ15Ex | https://drive.google.com/open?id=1GjPCNVeJllCJf8jmEAVtn3gY1emMQ9On |  | 115 HYD | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP033/25 | 2025-09-10 11:08 | sushma.poojari@crystalgroup.in | Jubliant Consumer Pvt Ltd | Gautam |  | wearehouse manager | TRIU6687350 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | Atul.Kumar@jubilantconsumer.com | Noida | Running with issues |  | Call | pushpa | [54 empty] | 2025-09-16 14:24 | 2025-09-13 |  |  |  |  | TRIU6687350 |  |  |  | Carrier | -25'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 11.4B | 6.4A 6.4A 6.4A | 404V 404V 404V | Not done | Visit on customer request | Unit working fine but compressor temperature going high due to economiser txv valve defective, during PTI test P6-6 faild, economiser valve defective. Unit giving supply sensor alaram but after checking and found sensor ok, alaram has been cleared, display not visible properly need to change | Yes | https://drive.google.com/open?id=1duVWCKIuEk--nX4iSEOmaaj3xF5YHbjw | https://drive.google.com/open?id=1kDHIsKqGLzFC1Ut7OH1NWN3MxCC54krZ |  | 118 | Yes | Yes | Urgent | Same above | Economiser valve (TXV) N2 test Gas charging 4.5kg Vacuum Filter drier Brizing work Display | technician@crystalgroup.in | REEFER
SEP034/25 | 2025-09-10 15:07 | operation@crystalgroup.in | Quick supply chain PVT LTD | blast | 7869533375 | Wearehouse Manager | CICU3876544 | container getting trip |  | dipak.verma@qwik.co.in | Bhopal | Container getting trip |  | Call | Pushpa maam | 2025-09-23 16:01 | service@crystalgroup.in | Quick supply chain PVT LTD | CICU3876544 | 10RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | unit has compressor ground | UNIT COVERS U/W & IT HAS COMPRESSOR GROUND | COMPRESSOR WILL BE PROVIDED BY KK TEAM | Yes | UNIT HAS COMPRESSOR GROUND | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP034%2F25 | Thermoking MP4000 | TK-MP4000 | NA | NA | NA | NEW | NA | SITARAM | Yes | container getting trip | 2025-10-15 14:59 | crm@crystalgroup.in | YES | IN234, IN265, IN271 | 2025-10-01 | FOC | Laurus Labs Limited-Unit 2 | Bhopal | GESU9454776 | SITE | FOC | TK-MP4000 | 2025-10-15 15:05 | crm@crystalgroup.in | YES | IN234, IN265, IN271 | YES | https://drive.google.com/open?id=1WoUkRsGzHGsRP4MfCgOJKvd_z6JPmH6S, https://drive.google.com/open?id=1zupvICHTEjvmfhdPQMODxyvHIIhMs6df, https://drive.google.com/open?id=1TBBqLQCwRVRW9cgHynRwHWez_LZGFT7I | Vendor | 2025-10-15 15:10 | crm@crystalgroup.in | YES | IN234, IN265, IN271 | 3 indents have been raised for this job order no. | [5 empty] | 2025-10-15 15:24 | 2025-10-10 |  |  |  |  | CICU3876544 |  |  |  | Thermo king | -4p'c supply-39.2'c, return -38'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2b 18.4b | 8.9a 8.9a 8 9a | 404v | Short | Compressor replenishment done | Unit working fine , 24 hours observation done but battery need to replenishment | Yes | https://drive.google.com/open?id=1gnoeuLLKF1bfDIT6z9CQqNE7AbCxuNVw | https://drive.google.com/open?id=1zInODS-lu-gaY90WNETaXys6AU7MdyVx |  | Na | Yes | No | Can be done on next PM | Same | Battery mp4000 | technician@crystalgroup.in | REEFER
SEP035/25 | 2025-09-10 15:14 | operation@crystalgroup.in | Aspiro pharma ltd | ramesh | 9959404803 | Wearehouse manager | CAIU5422720 | Container getting trip |  | SatyanarayanaReddy.V@aspiropharma.com | Hyderabad | Container getting trip |  | Call | PUSHPA MAAM | 2025-09-29 17:50 | service@crystalgroup.in | Aspiro pharma ltd | CAIU5422720 | 40FT STD RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT HAS SHEET KEY DEFECTIVE | NEED TO REPLACE THE SHEET KEY. | SHEET KEY | Yes | UNIT HAS SHEET KEY DEFECTIVE. | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP035%2F25 | DAikin | DAIKIN | NA | NA | NA | Used | JSGA622340482 | SHAHBUDDIN | Yes | Container getting trip | 2025-09-30 12:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-15 11:03 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 14:34 | crm@crystalgroup.in | NO
SEP036/25 | 2025-09-11 09:45 | crm@crystalgroup.in | BIOCON LTD -JIGANI | MANJUNATH KELUR | 9008176576 | ASSOCIATE MANAGER | TRIU6681542 | MOTOR MAKING NOISE |  | Manjunath.Kelur@biocon.com | Bangalore | Running with issues | EVAPORATOR MOTOR FAN REPLACED | Call | PUSHPA MAM | [54 empty] | 2025-09-11 21:15 | 2025-09-10 |  |  |  |  | TRIU6681542 |  |  |  | Carrier | +5C Sup.+5.2C Ret.+6.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc.0.4bar Dis. 12.3bar | R 17.1A B 16.9A Y 16.5A | 413V 413V 413V | Not done | Pm service and general inspection | Evaporator fan motor replaced | No | https://drive.google.com/open?id=1mC_Oo2Ws2cb2Mjb6T7rl2bIso3ubAoBh | https://drive.google.com/open?id=1XXEI0HQiFwPSw3bEZYqoPU5AWKSY6_Su |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP037/25 | 2025-09-11 09:50 | crm@crystalgroup.in | BIOCON LTD -JIGANI | MANJUNATH KELUR | 9008176576 | ASSOCIATE MANAGER | CCLU1035976 |  |  | Manjunath.Kelur@biocon.com | Bangalore | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-11 21:23 | 2025-09-10 |  |  |  |  | CCLU1035976 |  |  |  | Carrier | +5C Sup.+5.1C Ret.+6.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.5bar discharge 11.9bar | R 16.9A B 16.6A Y 16.2A | 413V 413V 413V | Not done | Pm service and general inspection | Attended routine checkup of container verified all operational are normal container functioning within range temperature. | No | https://drive.google.com/open?id=1UuOtBOKyd7yAAR4pjuWDwkUBlL9Iq-Gs | https://drive.google.com/open?id=1K-beRJprIp7f6jN1tumTi5dS6yM5UcF2 |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP038/25 | 2025-09-11 10:04 | crm@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | SJKU4000104 |  |  | dharmender.tiwari@dsv.com | Shamshabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-11 22:32 | 2025-09-10 |  |  |  |  | SJKU4000104 |  |  |  | Thermo king | +2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19br | 9.9/9.8/9.9 | 421/422/421 | Short | Pm service due | Pm service completed | Yes | https://drive.google.com/open?id=1PtP4-Q0f_d_uKWPI5E8bEsdVt9y4A6Vt | https://drive.google.com/open?id=1UZ4U93a1JktwUA80Rc-EuIJblfvBHkGO |  | 115 | No | No | Can be done on next PM | Na | TK MP 4000 DISPLAY DOOR | technician@crystalgroup.in | REEFER
SEP039/25 | 2025-09-11 10:08 | crm@crystalgroup.in | DSV LOGISTIC | DHARAMENDRA TIWARI | 9700033475 | DY. MANAGER | TITU9930006 |  |  | dharmender.tiwari@dsv.com | Shamshabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-11 22:44 | 10/09/0025 |  |  |  |  | TITU9930006 |  |  |  | Thermo king | ++1c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/18.3br | 10.1/10.2/10.1 | 421/422/421 | Short | Pm service due | Pm service completed | No | https://drive.google.com/open?id=1TeZGcAFwwfMCNKBMojtilGhvvSE4SOlV | https://drive.google.com/open?id=1EsuNNiOSLWFoCJQHs_tRS4dw-9bCS7HX |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP040/25 | 2025-09-11 10:16 | crm@crystalgroup.in | Shivamrut | ANIL WAGHMODE | 8408027721 | STORE INCHARGE | CXRU1032498 | DISPLAY NOT VISIBLE |  | shivamrutakluj@gmail.com | AKLUJ | Running with issues | DAIKING DISPALY CHANGE IN 40 FT REEFER CONTAINER | Call | PUSHPA MAM | [54 empty] | 2025-09-16 14:51 | 2025-09-11 |  |  |  |  | CXRU1032498 |  |  |  | Daikin | On call | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | On call | Not done | On call with customer | Unit breakdown, after connect with factory technician, under my supervision check and found display and key pad found defective need to replace | Yes | https://drive.google.com/open?id=1tGOga1hbu4s7MagZLMv3cl98NLDLEG1l | https://drive.google.com/open?id=1pEihc9TIuDEahiR6mC0l20oEqx2vaAUL |  | Na | Yes | Yes | Urgent | Same above | Display Sheet key | technician@crystalgroup.in | REEFER
SEP041/25 | 2025-09-12 10:07 | crm@crystalgroup.in | Aspiro pharma ltd | T. RAMESH REDDY | 9959404803 | TECHNICAL MANAGER | CGMU2991560 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-12 23:47 | 2025-09-11 |  |  |  |  | CGMU2991560 |  |  |  | Carrier | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/180 psig | 12.6/12.5/12.6 | 401/400/401 | Short | Two way unit both unit pm & main unit service call with ALARM 25 | Both two way unit pm completed and checked main unit alaram 25 & found condenser fan capacitor failure need to replaced . | Yes | https://drive.google.com/open?id=1Yn1nqO8tecq3wHw1gBmmSD0s01HMhJcP | https://drive.google.com/open?id=1HwVbjVROTRda4NZbSpT29J_b4oCwDpkI |  | 115 | Yes | No | Can be done on next PM | Need to replaced fan capacitors | Carrier condenser fan motor capacitor20 MFD / UF | technician@crystalgroup.in | REEFER
SEP042/25 | 2025-09-12 10:09 | crm@crystalgroup.in | Aspiro pharma ltd | Gatturayudu | 9100980301 | Manager | CAIU5422720 |  |  | rohanKumar.y@aspiropharma.com | Hyderabad | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-20 00:32 | 2025-09-11 |  |  |  |  | CAIU5422720 |  |  |  | Daikin | 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/200 psig | 10.1/10.2/10.1 | 400/401/400V | Short | Pm duec& found sheet key Defective | Pm service completed with checked unit operation and found as satisfactory | Yes | https://drive.google.com/open?id=1JcGx9R_1GO5X2c89ckX-FFAvLNNn7BE_ | https://drive.google.com/open?id=1vowE_5V17OD4kRnmT6wiVq7Tz88gqYqJ |  | 115-A | No | No | Can be done on next PM | Na | Sheet key | technician@crystalgroup.in | REEFER
SEP043/25 | 2025-09-13 10:05 | sales@crystalgroup.in | Dr.Reddy Biologics unit -II-Hyderabd | Harish / Arun | 9000660485 / 8159078756 | Manager | SEGU9055868 | INSTALATION & TRANNING WITH RUN TEST | container installation at dr.reddy site | harishca@drreddys.com | Hyderabad | Installation |  | Call | Pushpa Mam | [54 empty] | 2025-09-21 21:50 | 2025-09-12 |  |  |  |  | SEGU9055868 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/190 psig | 9.9/9.8/9.9 | 412/413/413 | Short | Unit for Instalation & service call door issue & power audit issue | Instalation completed & demo given for door open procedure with Technical tranning for duty Engineer and with them power audit done. | No | https://drive.google.com/open?id=1YjSfW01oKbGbXK_iMugu_jGPZxv5iQ9- | https://drive.google.com/open?id=1CmzB_pzskk4JaL8Gb6CGdHyQ62UknRnd |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP044/25 | 2025-09-13 10:14 | crm@crystalgroup.in | Dr.Reddy Biologics unit -II-Hyderabd | Harish / Arun | 9000660485 / 8159078756 | MANAGER | SEGU9107489 | INSTALATION & TRANNING WITH RUN TEST | container installation at dr.reddy site | harishca@drreddys.com | Hyderabad | Installation |  | Call | Pushpa Mam | [54 empty] | 2025-09-21 21:40 | 2025-09-12 |  |  |  |  | SEGU9107489 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/210 psig | 10.2/10.3/10.2 | 413/414/413 | Short | Unit for Instalation & door issue | Instalation completed & training given for operational with demo for door open producers | No | https://drive.google.com/open?id=1pdwr9seMJq6oNFKzcRQXb0rb2UTJuCzQ | https://drive.google.com/open?id=1JSHS7NFlbSoOhSx1hBSxGiqdzkJ9_x1B |  | 115 | No | No | Can be done on next PM | Door for greecing | Na | technician@crystalgroup.in | REEFER
SEP045/25 | 2025-09-13 12:35 | crm@crystalgroup.in | SOFT BOX- Samsabad | Satish K | 8977711235 | Manager | TITU8257288 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-20 00:18 | 2025-09-13 |  |  |  |  | TITU8257288 |  |  |  | Thermo king | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18br | 9.9/10/9.9 | 412/413/412V | Short | Pm due | Pm service completed with checked unit operation & working as satisfactory | No | https://drive.google.com/open?id=1ORiZi4xk-KEVERU6PRmnLi18CLkB5hSE | https://drive.google.com/open?id=1W_256S2fq7t75iIinREbkYjiGGbaWnlm |  | 115-A | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP046/25 | 2025-09-13 17:00 | crm@crystalgroup.in | Qwik Supply Chain Pvt Ltd -Hoskote | Suryakanth | 7899914947 | Manager | CICU1442235 |  |  | kommalapati.suryanarayana@qwik.co.in | Bangalore | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-13 20:09 | 2025-09-13 |  |  |  |  | CICU1442235 |  |  |  | Thermo king | -40C Ret.-35.1C Sup.-39.7C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.4bar Discharge 14.2bar | R 13.A B 12.4A Y 12.9A | 421V 421V 421V | Short | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. Door controller Damage need to replace | Yes | https://drive.google.com/open?id=1UOKBaBDvqe_FWj1IM1enJoEyG0KZhvbY | https://drive.google.com/open?id=1tseNngAZCjwEaVNlDJfX16F1M0FUvh1f |  | 121 | No | No | Can be done on next PM | No | Door controller | technician@crystalgroup.in | REEFER
SEP047/25 | 2025-09-13 17:03 | crm@crystalgroup.in | Qwik Supply Chain Pvt Ltd -Hoskote | Suryakanth | 7899914947 | Manager | CICU2779895 |  |  | kommalapati.suryanarayana@qwik.co.in | Bangalore | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-13 20:13 | 2025-09-13 |  |  |  |  | CICU2779895 |  |  |  | Thermo king | -39C Ret.-33.9C Sup.-40.8C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6bar Discharge 16.4bar | R 13.4A B 12.3A Y 12.8A | 421V 421V 421V | Short | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1cHf4VqiU2kU7ZnKcZefNxyA3RQwVl79T | https://drive.google.com/open?id=1iHUB_g1vpfq46tyUahEBnj8oTQBBRoAZ |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP048/25 | 2025-09-19 09:55 | sales@crystalgroup.in | ITC LTD FOOD DIVISION | NETHRA P. | 6364348214 | MANAGER | CXRU1032327 |  |  | Nethra.P@itc.in | MYSORE | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-19 14:10 | 2025-09-17 |  |  |  |  | CXRU1032327 |  |  |  | Daikin | -20C ret.-19.8C Sup.-22.3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 10LPT Discharge 1048HPT | 10.1A 7.9A | 409V 409V 409V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1GoGrGsLWffFbTty6XdelZjTQEQ6e7lvD | https://drive.google.com/open?id=1U5NCDA3rpZcCdhDaOenGhgmiBHz7yDFi |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP049/25 | 2025-09-19 10:26 | crm@crystalgroup.in | ITC LTD FOOD DIVISION | NETHRA P. | 6364348214 | MANAGER | PCIU6010243 |  |  | Nethra.P@itc.in | MYSORE | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-19 14:22 | 2025-09-17 |  |  |  |  | PCIU6010243 |  |  |  | Daikin | -22C Ret.-20.6C Sup.-22.7C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace | https://drive.google.com/open?id=1ZpgR6ybeizx_dg9JU5LVdCETRqWs9Y0i | Need to replace | https://drive.google.com/open?id=1eC19sajIkJ2Uj6PPCDYmq6bTpjQyYtvL | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Suction 31LPT Discharge 1262HPT | 11.7A 9.4A | 405V 405V 405V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. Keypad set with user panel and display need to replace. | Yes | https://drive.google.com/open?id=1uCjZ-YcVcyq0IG9kaQ_5VEU9FX9rL_pt | https://drive.google.com/open?id=1sL6In2KztdSdR5qhkh35VcP1mQjNHpBA |  | 121 | No | No | Can be done on next PM | No | Keypad set with user panel Display | technician@crystalgroup.in | REEFER
SEP050/25 | 2025-09-19 10:29 | crm@crystalgroup.in | ITC LTD FOOD DIVISION | NETHRA P. | 6364348214 | MANAGER | SEGU9052030 |  |  | Nethra.P@itc.in | MYSORE | Preventive Maintenance |  | Call | PUSHPA MAM | [54 empty] | 2025-09-19 14:26 | 2025-09-17 |  |  |  |  | SEGU9052030 |  |  |  | Carrier | -22C Ret.-21.7C Sup.-25.1C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.5bar Discharge 13.2bar | R 12.6A B13.2A Y 13.7A | 407V 407V 407V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1e7K2utDERpt-fki5vkJ1t3hDiGP8NV3S | https://drive.google.com/open?id=1uz_bJScgyE7NWbxOIEAfF3OXfAe8S55Y |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP051/25 | 2025-09-19 10:45 | crm@crystalgroup.in | OneSource Specialty Pharma Limited | Prem kumar | NA | Manager | CRIU4025087 | New Installation at client site in Karnataka |  | Premkumar.CK@onesourcecdmo.com | Karnataka | Installation | CRIU4025087 installation | Email | Pushpa Mam | [54 empty] | 2025-09-19 14:06 | 2025-09-18 |  |  |  |  | CRIU4025087 |  |  |  | Thermo king | +5C Sup.+5.1C Ret.+4.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6bar Discharge 18.6bar | R 12.3A B 12.8A Y 13.4A | 412V 412V 412V | Short | Installation | Installation new unit | No | https://drive.google.com/open?id=1OXjGyVE41OBcOxbrMukGCel4k_WVdQ7Z | https://drive.google.com/open?id=1M3UgeuMiDK2l9QH19AkiheKOo5KyAxdq |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP052/25 | 2025-09-19 10:51 | crm@crystalgroup.in | OneSource Specialty Pharma Limited | Prem kumar | NA | Manager | CRIU4025071 | New Installation at client site in Karnataka |  | Premkumar.CK@onesourcecdmo.com | Karnataka | Installation | CRIU4025071 installation | Email | Pushpa Mam | [54 empty] | 2025-09-19 14:01 | 2025-09-11 |  |  |  |  | CRIU4025071 |  |  |  | Thermo king | +5C sup.+5.1C Ret.+6.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.7bar Discharge 19.8bar | R 12.0A B12.9A Y 13.9A | 412V 412V 412V | Short | Installation | Installation new unit | No | https://drive.google.com/open?id=1uGwSbG6qk87RQKC7WPdA7ZMxqV3SIAl4 | https://drive.google.com/open?id=1zRKecxgWUVY7W6GGBPKW0cUF3z20Y_RD |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP053/25 | 2025-09-19 14:08 | crm@crystalgroup.in | Zenfold Sustainable Technologies Pvt Ltd / Losynth Labs Private Limited | Sripriya Kamath | 9591756414 ¦ 9980918430 | Head- SCM | TRIU6617250 |  |  | sripriya.k@zenfoldst.com | Bangalore | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-19 14:30 | 2025-09-19 |  |  |  |  | TRIU6617250 |  |  |  | Carrier | -0.1C Sup.-0.9C Sup.+0.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.4bar Discharge 12.6bar | R 12.4A B 12.3A Y 11.9A | 432V 432V 432V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=12c4-cROW16ZpoH4lo2tvgMo-1igV-ntd | https://drive.google.com/open?id=1SqOYg0b_KdvFpPFObgLvwmxPacj6UBCX |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP054/25 | 2025-09-19 14:20 | crm@crystalgroup.in | QUICK SUPPKY - RELIANCE BHOPAL | Ram Babu | 7869533375 | Manager | MYRU4515188 |  |  | ujjawal.pawar@qwik.co.in | Bhopal | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-22 08:24 | 2025-09-19 |  |  |  |  | MYRU4515188 |  |  |  | Carrier | 4.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4b 11.9b | 11.2a 11.2a 11.2a | 404v 404v 404v | Not done | Pm service | Unit working in good condition, keyboard need to change | Yes | https://drive.google.com/open?id=1QqHckPAniJj92qvBSCURZhdBPM-pFQbt | https://drive.google.com/open?id=1E4eSsE6Z_DjOoaNSnhKh2pouxuVFwMri |  | 117 | Yes | No | Can be done on next PM | Sam | Keypad | technician@crystalgroup.in | REEFER
SEP055/25 | 2025-09-19 14:23 | crm@crystalgroup.in | QUICK SUPPKY - RELIANCE BHOPAL | Ram Babu | 7869533375 | Manager | CRLU6220410 |  |  | ujjawal.pawar@qwik.co.in | Bhopal | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-26 10:22 | 2025-09-19 |  |  |  |  | CRLU6220410 |  |  |  | Carrier | 4.0c , supply 4.0c, Return 3.9C | Clean | Clean | https://drive.google.com/open?id=1VWkZlPvF23O-DcQM5xunKC6Th2TOGMnn | Okay | Clean | Okay | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 14.4B | 11.9A 11.9A 11.9A | 402V 402V 402V | Not done | Pm service | Unit working fine, but display not visible properly need to replace, ambent sensor out of calibration need to replace | Yes | https://drive.google.com/open?id=1mh4DR2a5MHkj9HX0zGILD_U3jjrFr3Ot | https://drive.google.com/open?id=1PUZY6rNqXLi5XSZT7O8oRSGhcg9TRjby |  | Na | Yes | Yes | Urgent | Same | Display Ambent sensor | technician@crystalgroup.in | REEFER
SEP056/25 | 2025-09-19 15:23 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | SHRINIVAS | 08916762247 , 0990812799 | MANAGER | GESU9454776 | MOTOR MAKING NOISE, ALARM CODE VISIBLE | CONTAINER NOT WORKING | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues | EVAPORATOR MOTOR NOT WORKING | Call | PUSHPA MAM | 2025-10-07 16:17 | crm@crystalgroup.in | Laurus Labs Limited-Unit 2 | GESU9454776 | 40 feet | Carrier | SERVICE-AT SITE | NA | NA | evaporator motor defective(single phase) | need to be changed | evaporator motor single phase | Yes | evaporator motor defective(single phase) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP056%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | NA | NA | SITARAM | Yes | MOTOR MAKING NOISE, ALARM CODE VISIBLE | 2025-10-24 22:48 | crm@crystalgroup.in | YES | IN240 | 2025-10-08 |  | Laurus Labs Limited-Unit 2 |  | GESU9454776 | SITE |  |  | 2025-10-24 22:49 | crm@crystalgroup.in | YES | IN240 | YES |  | Stock | 2025-10-24 22:50 | crm@crystalgroup.in | YES | IN240 | TECHNICIAN |  |  | Sitaram
SEP057/25 | 2025-09-19 15:40 | crm@crystalgroup.in | Kirloskar Corrocoat | Pundlik Dhope | 9881003659 / 9890385995 | MANAGER | PCIU5822411 | REPAIRS & REPLACEMENT | Parts required Controller llld PTCT bord RPP I/O bord | pundlik.dhope@kicopl.com | Ghatampur | Complete Breakdown | CONTAINER COMPLETELY BREAKDOWN | Call | PUSHPA MAM | 2025-09-23 12:21 | service@crystalgroup.in | KIRLOSKAR CORROCOAT PRIVATE LIMITED | PCIU5822411 | 20RF | DAIKIN | SERVICE-AT SITE | LEASE | CHARGEABLE | temperature not maintaining | need to refill the gas | R-134a Gas Required 5kg, Vaccume Pump Required | R-134a Gas Required 5kg, Vaccume Pump Required | gas found contaminated | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP057%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SITARAM | Yes | REPAIRS & REPLACEMENT
SEP058/25 | 2025-09-22 09:45 | crm@crystalgroup.in | BIOCON UNIT II | D. Nagaraja Reddy | 9959335767 | Sr. Manager | BMOU9748382 |  |  | dnagaraja.reddy@biocon.com | Bommsandra Bengaluru | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-29 19:09 | 2025-09-20 |  |  |  |  | BMOU9748382 |  |  |  | Daikin | +22C sup.+22.6C Ret.+23.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Suction LPT20 Discharge HPT833 | 14.6A 8.9A | 397V | Not done | Pm service and general inspection | I have inspected the unit and found issues. Return sensor and recorded sensor defective. All other functions are working properly container within range temperature | Yes | https://drive.google.com/open?id=1BrC8B4GlgVshngsE7_tLWmoVQsnbgAms | https://drive.google.com/open?id=13mlwnVAJ4n0B1uq0k66Rb8YUDVZV_w6p |  | 121 | No | No | Can be done on next PM | No | Return sensor (AL E403) Recorded sensor (AL H006) | technician@crystalgroup.in | REEFER
SEP059/25 | 2025-09-22 09:49 | crm@crystalgroup.in | BIOCON UNIT II | D. Nagaraja Reddy | 9959335767 | Sr. Manager | BMOU9759767 |  |  | dnagaraja.reddy@biocon.com | Bommsandra Bengaluru | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-29 19:17 | 2025-09-20 |  |  |  |  | BMOU9759767 |  |  |  | Daikin | +22C Sup.+22.8C Ret.+23.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | Suction LPT12 Discharge HPT887 | 12.0A 9.3A | 396V | Not done | Pm service and general inspection | I have inspected the unit and found issues Supply sensor, Evaporator outlet sensor and data recorder return sensor defective. All other functions are working properly | No | https://drive.google.com/open?id=1l5WmkGLbcGr9VwUOQN-zKOEEsCo_sSCK | https://drive.google.com/open?id=1ioHQAm3vUdSMuxpPP0Z65BdKg42mTZ_b |  | 121 | No | No | Can be done on next PM | No | Supply sensor Evaporator outlet sensor Data recorder return sensor | technician@crystalgroup.in | REEFER
SEP060/25 | 2025-09-22 09:58 | crm@crystalgroup.in | CELON LABORATORIES PRIVATE LIMITED | RAJA | 9848807590 | MANAGER | TRIU6616871 |  |  | NA | TELANGANA | Preventive Maintenance |  | Call | Pushpa Mam | 2025-09-22 10:11 | technician@crystalgroup.in | CELON LABORATORIES PRIVATE LIMITED | TRIU6616871 | 20FT STD RF | Carrier | SERVICE-AT SITE | LEASE | FOC | Pm service due | Tech. On the way | Na | No | Pm due | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP060%2F25 | Carrier - Thinline | CARRIER-THINLINE | NA | NA | NA | Used | NA | SHAHBUDDIN | Yes | [30 empty] | 2025-09-23 21:39 | 2025-09-20 |  |  |  |  | TRIU6616871 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/195psig | 12.6/12.712.6 | 417/416/416 | Short | Pm due for unit | Pm completed with checked unit operation & found unit working as satisfactory | No | https://drive.google.com/open?id=1VznaVDn8lP1IlMOqKZO56qVgqXsUftW8 | https://drive.google.com/open?id=1Ikc30EL-fWOXcV2YVugpIwWh_AuNDQD0 |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP061/25 | 2025-09-22 10:12 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | APRU5091041 | SERVICING, keypad required |  | vishnu.m@hetero.com | Hyderabad | Running with issues |  | Call | Pushpa Mam | 2025-10-30 16:40 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | APRU5091041 | 40FT | 2008 | MACHINE INSPECTION | NA | NA | temprature not meet setpoint | technician need at site for observation | na | No | temprature not meet set point | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP061%2F25 | Carrier-Primeline | DAIKIN | KSU60094860 | 541308SN | na | Used | JSGA623040287 | SHAHBUDDIN | Yes | SERVICING, keypad required | 2025-11-10 12:20 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-10 12:21 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-10 12:21 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=SEP061%2F25
SEP062/25 | 2025-09-22 10:17 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1326276 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-24 21:47 | 2025-09-21 |  |  |  |  | CXRU1326276 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/180psig | 10.2/10.4/10.4 | 414/415/414 | Short | Pm service due | Pm service completed with checked unit operation & found unit working as satisfactory | No | https://drive.google.com/open?id=1LFnKO7VLXGycCIkdtlEoYbKfHcRvujWl | https://drive.google.com/open?id=1OA1cvKQ3qFvK1IAb0eAh42SWERg8jzdI |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP063/25 | 2025-09-22 10:20 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1550769 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-24 21:40 | 2025-09-21 |  |  |  |  | CXRU1550769 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/190 psig | 10.4/10.5/10.4 | 414/415/414 | Short | Pm service due | Pm service completed with checked unit operation& found unit as working satisfactory | No | https://drive.google.com/open?id=1YVAkVqVjEVRQJuFnw4ty3uY261awI4J5 | https://drive.google.com/open?id=1G8lRtqAaj_3uRmsaRE2Eh7kOR3B9Uh5P |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP064/25 | 2025-09-22 10:23 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1026520 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-24 21:31 | 2025-09-21 |  |  |  |  | CXRU1026520 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/190 psig | 10.410.5/10.4 | 414/415/414 | Short | Pm service due | Pm service completed with checked unit operation & working as satisfactory. | No | https://drive.google.com/open?id=1IcbP1dukCScloLUrk1WVaGiEWnGpuXXq | https://drive.google.com/open?id=1ZC5pTsvkoEpHRKuOJ882iPfDGzW8mbBt |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP065/25 | 2025-09-22 10:29 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | CXRU1030427 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-24 21:23 | 2025-09-21 |  |  |  |  | CXRU1030427 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/190 psig | 10.3/10.4/10.4 | 415/416/416 | Short | Pm duep | Pm service completed with checked unit operation & found working as satisfactory | No | https://drive.google.com/open?id=1vJcTu-zWo3YwiQg9wqnIe_1lOHZDY2RI | https://drive.google.com/open?id=196V_Kg6nmW5D8nMRuWvG-xM5V0YCi7Zd |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP066/25 | 2025-09-22 10:31 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | NA | PCIU6016370 |  |  | vishnu.m@hetero.com | Hyderabad | Preventive Maintenance |  | Call | Pushpa Mam | [54 empty] | 2025-09-24 21:14 | 2025-09-21 |  |  |  |  | PCIU6016370 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .9/200 psig | 10.4/10.4/10.3 | 416/415/415 | Short | Pm due with all sensors reading abnormal temp. | Pm service completed with observe mostly sensers reading abnormal temp. Need to replaced before issue is expected. | Yes | https://drive.google.com/open?id=1do-OUV72TueOvZl25EBNA4Fde-tWIjW0 | https://drive.google.com/open?id=1wE0iOmQoYIDEh_o50vme7NLdyr9F17HV |  | 115 | No | No | Can be done on next PM | Need to replaced sensors before next pm due | DAIKIN UNIT : EVP INLET SENSOR EVP OUT LET SENSOR RTS / STS DRS SENSOR | technician@crystalgroup.in | REEFER
SEP067/25 | 2025-09-24 15:42 | technician@crystalgroup.in | Quick supply chain PVT LTD | Ranveer ji | +91 98726 09126 | Maintenence department | SJKU4000022 | MOTOR MAKING NOISE |  | Na | Rajpura, Punjab | Running with issues | Condensor motor noisy need repair | Call | Sita ram | 2025-09-25 18:07 | service@crystalgroup.in | Quick supply | SJKU4000022 | 40RF | CARRIER PRIMELINE | SERVICE-AT SITE | LEASE | FOC | unit has condenser motor noisy | need to repairs | bearing | bearing required | condenser motor noisy | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP067%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | SITARAM | Yes | MOTOR MAKING NOISE | 2025-10-17 14:09 | crm@crystalgroup.in | YES | IN243 | 2025-10-08 |  | Quick supply |  | SJKU4000022 | SITE |  |  | 2025-10-17 14:10 | crm@crystalgroup.in | YES | IN243 | YES |  | Stock
SEP068/25 | 2025-09-25 11:57 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhoosudan | 7259366532 | Service Person | PCIU600832 845R1 | DOOR NOT CLOSING |  | madhusoodhana.k@sailife.com | Bidar | Running with issues | Door not closing | Call | Pushpa | 2025-10-10 14:49 | service@crystalgroup.in | Sai Life Science | PCIU600832 845R1 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | DOOR NOT CLOSING | NEED TO ALIGN FABRICATION TEAM | NA |  | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP068%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | JSGA622340291 | FABRICATION TEAM | Yes | DOOR NOT CLOSING | 2025-10-20 12:34 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-20 12:34 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-20 12:34 | crm@crystalgroup.in | NO
SEP069/25 | 2025-09-25 12:07 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025024 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation | Installation | Email | Pushpa | [54 empty] | 2025-10-09 13:19 | 08/09/0025 |  |  |  |  | CRIU4025024 |  |  |  | Thermo king | Test -25 & 2to 8c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/19br | 9.8/9.9/9.8 | 403/404/403 | Full | New unit Tk MP 4000 for Instalation | Instalation completed with test unit -25 & 2 to 8 c . With operational TRANNING and practice. | No | https://drive.google.com/open?id=1oGtzMHfMBkdTuBbre5CCKu15UCOuiZiB | https://drive.google.com/open?id=1UT3v63-5dZ3IK953a2RrTKG_1-9uPflg |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP070/25 | 2025-09-25 12:10 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025066 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 18:05 | 08/09/0025 |  |  |  |  | CRIU4025066 |  |  |  | Thermo king | -25 c And 2c to 8 c test | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/19bar | 9.9/9.8/9.9 | 403/402/403 v | Full | New box TK MP 4000 FOR INSTALATION | Instalation completed | No | https://drive.google.com/open?id=12qP8jYo1DoOo1QaTF8mclrQLKVMm4ZEB | https://drive.google.com/open?id=1-2U1jYGHiiN5wReq8tEklvCwEn452dWY |  | 115-SHABUDIN -HYD | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP071/25 | 2025-09-25 12:12 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025050 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 13:28 | 08/09/0025 |  |  |  |  | CRIU4025050 |  |  |  | Thermo king | -25 & 2 c to 8 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19br | 10.1/10/10 | 405/404/404 | Full | New unit MP-4000 TK FOR INSTALATION | Instalation completed | No | https://drive.google.com/open?id=1P1pHs2IHbYztFjjdyz_NwgfZVYz1lFqk | https://drive.google.com/open?id=1h3no12Fjk5BAsVc_gppmcGegOB47aLef |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP072/25 | 2025-09-25 12:16 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025019 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 13:38 | 08/09/0025 |  |  |  |  | CRIU4025019 |  |  |  | Thermo king | -25 and,2c to 8c test | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18br | 9.9/10/9.9 | 403/404/403 | Full | New unit TK MP 4000 FOR INSTALATION | New unit Instalation completed | No | https://drive.google.com/open?id=1rgJSpe30LIsPXzlytQFXhazSj67llzG- | https://drive.google.com/open?id=1Ir0dRSVOE902UPApMuHW4vqld5LGkFW- |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP073/25 | 2025-09-25 12:18 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025030 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 13:46 | 24/09/0025 |  |  |  |  | CRIU4025030 |  |  |  | Thermo king | -25c & 2c to 8c test | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/18br | 10.4/10.5/10.4 | 405/406/405 | Full | New unit for Instalation | New unit TK MP 4000 FOR INSTALATION | No | https://drive.google.com/open?id=1fv2p2XHTUQiXEpvxPbT0GIAqB7_vGJvk | https://drive.google.com/open?id=18dqq852z2MnQbWXYZ8NQATN0CuyaK8PP |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP074/25 | 2025-09-25 12:20 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025045 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 13:55 | 23/09/0025 |  |  |  |  | CRIU4025045 |  |  |  | Thermo king | -25c & 2c to 8c test done | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/19br | 10.4/10.5/10.4 | 403/402/403 | Full | New TK MP 5000 UNIT FOR INSTALATION | New unit Instalation completed | No | https://drive.google.com/open?id=1C1ASlzeH4Xv4sZRF0AbQIjHCHM22rf3g | https://drive.google.com/open?id=1cLm9q3-FuNynwCo5Ufjo2S2lkQ2pjv_G |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP076/25 | 2025-09-25 12:25 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025235 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa
SEP077/25 | 2025-09-25 12:27 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025174 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 14:17 | 24/09/0025 |  |  |  |  | CRIU4025174 |  |  |  | Thermo king | -25c and, 2c to 8c test completed | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .8/19br | 9.9/10/10 | 404/405/404 | Full | New UNIT TK MP 5000 FOR INSTALATION | New box instalation completed | No | https://drive.google.com/open?id=1_M3E3oEfnW_fNUYmJ5H3iiVevQwzrwhG | https://drive.google.com/open?id=1pjFRUdj34uDAMHb3kcanNdIfDwJ_ldmr |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP078/25 | 2025-09-25 12:28 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna Maguluri | -66966321 | Service Person | CRIU4025220 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-09 14:24 | 2025-09-23 |  |  |  |  | CRIU4025220 |  |  |  | Thermo king | -25c and 2c to 8c test done | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/18 br | 10.4/10.3/10.3 | 404/405/405 | Full | New unit tk 5000 for Instalation | Instalation completed | No | https://drive.google.com/open?id=1cywYdmDBht5LcuimSPAsOY1jmvTdUZ2O | https://drive.google.com/open?id=1WSGeeq-bh0VesDuwKWvYSKD0in-CjRqT |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP079/25 | 2025-09-25 18:18 | technician@crystalgroup.in | Quick supply chain PVT LTD | Ranveer | +91 98726 09126 | Maintenance department | CICU3876631 | compressor making noise |  | Na | Rajpura, Punjab | Running with issues | compressor making noise | Call | Sita ram | 2025-09-27 11:52 | service@crystalgroup.in | Quick supply | CICU3876631 | 10FT STD RF | Thermoking MP 4000 | SERVICE-ON CALL | LEASE | FOC | unit wasn't working | resolved the error by rectifying the power supply issues | na | No | due to improper power supply | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP079%2F25 | Thermoking | TK-MP4000 | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New | NA | SITARAM | No | compressor making noise | 2025-09-27 11:53 | service@crystalgroup.in | NO | [9 empty] | 2025-09-27 11:54 | service@crystalgroup.in | NO |  |  |  |  | 2025-09-27 11:56 | service@crystalgroup.in | NO | [7 empty] | 2025-10-16 13:27 | 2025-09-16 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b 18.2b | 8.9a 8.9a 8.9a | 402v | Short | Pm | Unit working fine but battery need to change | Yes | https://drive.google.com/open?id=1KeMiw5QxG7ThH3Qo0LvY6wACrNVw9Sdi | https://drive.google.com/open?id=1kjL6sMdYXXMS4bc-UpPlHeToy3A_8Mfs |  | N | No | Yes | Urgent | Na | Battery mp 4000 | technician@crystalgroup.in | REEFER
SEP080/25 | 2025-09-26 10:41 | crm@crystalgroup.in | UPS | Nadeem & Venkat | 9700137866 / 99517 80321 | CRM | HDMU5220720 |  |  | Nadeemuddin.mohammed@marken.com | Hyderabad | Preventive Maintenance |  | Email | Pushpa Mam | [54 empty] | 2025-09-27 22:45 | 22/09/0025 |  |  |  |  | HDMU5220720 |  |  |  | Carrier | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/210psig | 13.2/13.1/13.2 | 413/414/413 | Short | Pm service due & light issue | Pm service completed & checked unit operation & found as satisfactory. And resolved light issue with set temp. Given TRANNING again for reset set temp. | No | https://drive.google.com/open?id=1lJT2oGk_HhGq8DpyEx0kpphy2iKmqXbG | https://drive.google.com/open?id=1c81PpCLsc1or2a1KM64SvUAsaKH8Y8T6 |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP081/25 | 2025-09-26 11:10 | crm@crystalgroup.in | Divis labs DC- SEZ# 01 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | CGMU4984529 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM | [54 empty] | 2025-09-27 21:14 | 2025-09-25 |  |  |  |  | CGMU4984529 |  |  |  | Carrier | +21c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/190 psig | 12.9/12.8/12.8 | 411/412/411 | Short | Unit for pm & PTI | Pm service completed with checked unit operation & PTI - PREE TRIP INSPECTION DONE & PASS | No | https://drive.google.com/open?id=1BEV4PocFFp2Gk5YZz0EsZzIBTY0fsrQ2 | https://drive.google.com/open?id=1k7AxtAhqeWQX7mUCnXBTiDIgiCSyiJOF |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP082/25 | 2025-09-26 11:16 | crm@crystalgroup.in | Divis labs DC- SEZ# 03 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | TRIU8387141 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM
SEP083/25 | 2025-09-26 11:20 | crm@crystalgroup.in | Divis labs DC- SEZ# 04 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | TRIU8363258 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM | [54 empty] | 2025-09-27 21:35 | 26/09/0025 |  |  |  |  | TRIU8363258 |  |  |  | Carrier | +4.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/210 psig | 12.9/13/12.9 | 413/414/413 | Short | Unit for pm service & water complian | Pm service completed with checked unit operation & found working as satisfactory, water drain issue is container kept complit bottam Lavelle & that drain bottom excess pipe twest & water not get down. & second T - flor pendent & twest need to straightness.. | No | https://drive.google.com/open?id=11QOnjlXpbz9jY-F_UZdLBr-3O2Jtp2TJ | https://drive.google.com/open?id=1uqSQ_ii9xyoCPp49Z6HgzPqgfl922Cpm |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP084/25 | 2025-09-26 11:25 | crm@crystalgroup.in | Divis labs DC- SEZ# | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | CRLU1703263 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM | [54 empty] | 2025-10-09 21:00 | 26/09/0025 |  |  |  |  | CRLU1703263 |  |  |  | Carrier | 5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/200psig | 12.8/12.9/12.8 | 413/414/413 v | Short | Pm service due | Pm service completed with checked unit operation And found working as satisfactory | No | https://drive.google.com/open?id=1jh0aNDlCJ2hhl94xmcvGpyPZu9P8Xd3k | https://drive.google.com/open?id=10pAz61WiQB6Uq-qqjZs6sBJYdwQlZNVA |  | HYD-SHAHABUDDIN-115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP085/25 | 2025-09-26 11:29 | crm@crystalgroup.in | Divis labs DC- SEZ#07 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | TDRU7152244 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM | [54 empty] | 2025-10-09 21:13 | 2025-09-25 |  |  |  |  | TDRU7152244 |  |  |  | Daikin | -12.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/210psig | 10.4/10.5/10.4 | 412/413/412 v | Short | Pm service due | Pm service completed with checked unit operation And found working as satisfactory | No | https://drive.google.com/open?id=1gkf116MJqWjrOY31WSQNAukc2tUsyO6N | https://drive.google.com/open?id=1ulLlhjl_1cAd2iyw-nSCtspXHg2SSbh9 |  | HYD-SHABUDIN-115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP086/25 | 2025-09-26 11:35 | crm@crystalgroup.in | Divis labs DC- SEZ#08 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | TCLU1003229 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA MAM | [54 empty] | 2025-10-09 20:46 | 25/09/0025 |  |  |  |  | TCLU1003229 |  |  |  | Thermo king | -13.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/250psig | 11.5/12/11.8 | 412/413/413 | Short | Pm service due | Pm service completed with checked unit operation And found working a | No | https://drive.google.com/open?id=1FjxAS-0KUsvXxbiSTLzlTB9LzYeWoXc9 | https://drive.google.com/open?id=1OAnhXC_AmkDtKLe5-TyMGXaatGZ7Cmm4 |  | HYD-SHABUDIN-115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP087/25 | 2025-09-26 11:41 | crm@crystalgroup.in | Divis labs DC- SEZ#09 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | TRIU8431985 | INSTALLATION |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | PUSHPA | [54 empty] | 2025-10-09 20:31 | 26/08/0025 |  |  |  |  | TRIU8431985 |  |  |  | Carrier | -12.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/220psig | 12.7/12.8/12.8 | 412/413/412 v | Short | Pm service due | Pm service completed with checked unit operation and found working as satisfactory | No | https://drive.google.com/open?id=1zTmOSp-2LqHv4Lrvcx7tJLZ5Dd-vv9Yz | https://drive.google.com/open?id=19wDR5w2Iu2ZTvrHYodOojcrcXh_U6QF2 |  | 115-SHABUDIN-HYD | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP088/25 | 2025-09-26 15:25 | crm@crystalgroup.in | Divis labs DC- SEZ#6 | Ramakrishna Maguluri | 9652725368 | ON Duty Officer | APRU5090955 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa Mam | [54 empty] | 2025-10-10 10:27 | 26/09/0025 |  |  |  |  | APRU5090955 |  |  |  | Carrier | 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/200 psig | 13.1/13.2/13.1 | 414/415/414 | Short | Pm service due | Pm service completed with checked unit operation And found working as satisfactory . | No | https://drive.google.com/open?id=1NFizKirwcHKp62UZRVPPQPYxMZ33a6O_ | https://drive.google.com/open?id=11g54hWJER_RV_IQZHDId7vqhwVOznCUg |  | 115-SHABUDIN | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
SEP089/25 | 2025-09-26 15:36 | crm@crystalgroup.in | Qwik Supply | PALLAVTAY KUMAR | 6303778806 | EXECUTIVE | CICU1799156 |  |  | NA | Neelamangala,Karnataka | Preventive Maintenance |  | Email | PUSHPA MAM | [54 empty] | 2025-09-29 19:44 | 2025-09-21 |  |  |  |  | CICU1799156 |  |  |  | Thermo king | -40C Ret.-20.6 Sup.-30.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6bar Discharge 16.8bar | R 10.9A B 9.8A Y 11.0A | 414V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1eLlAVmuDeHl4pmn4Ot1vXcjRpDCYCgBt | https://drive.google.com/open?id=1MiKHPb2STMStFPS2Be9VUf4vzeV71smk |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP090/25 | 2025-09-26 15:39 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | KANTHURUTUS | 8497901917 | SENIOR EXECUTIVE | TRIU6681671 |  |  | NA | Kolar, Karnataka | Preventive Maintenance |  | Email | PUSHPA MAM | [54 empty] | 2025-09-29 19:38 | 2025-09-22 |  |  |  |  | TRIU6681671 |  |  |  | Carrier | +5C sup.+5.0C Ret.+5.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6bar Discharge 12.8bar | R12.1A B 12.0A Y 11.8A | 406V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1fSxc_MnPfHQysKkF8VD852Guu4K3Fvdu | https://drive.google.com/open?id=1uxlFR8cxQ4FhiZ4aWaDZVxo3VWZ07WKN |  | 121 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
SEP091/25 | 2025-09-29 09:50 | crm@crystalgroup.in | Aspiro pharma ltd | Ranosh T | 9959404803 | Manager | CAIU5422720 | SERVICING | Replaced sheetkey and display cover | rohanKumar.y@aspiropharma.com | Hyderabad | Running with issues |  | Call | PUSHPA MAM | 2025-10-06 17:22 | service@crystalgroup.in | ASPIRO PHARMA - KARKAPATLA | CAIU5422720 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | UNIT HAS SHEET KEY DEFECTIVE | NEED TO REPLACE SHEET KEY | SHEET KEY | Yes | USED | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP091%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | SERVICING | 2025-11-05 10:06 | crm@crystalgroup.in | YES | IN335 | 2025-11-04 |  |  |  |  | SITE |  |  | 2025-11-05 10:06 | crm@crystalgroup.in | YES | IN335 | YES |  | Stock | 2025-11-13 12:57 | crm@crystalgroup.in | YES | NA | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=SEP091%2F25
SEP092/25 | 2025-09-29 10:10 | crm@crystalgroup.in | Aspiro pharma ltd | Ranosh T | 9959404803 | Manager | MWCU2991560 | SERVICING | Two way carrier main unit break down , repair burnt wiring condenser fan motor & replaced condenser Fan Capacitor | rohanKumar.y@aspiropharma.com | Hyderabad | Running with issues |  | Email | PUSHPA MAM | 2025-10-06 17:20 | service@crystalgroup.in | ASPIRO PHARMA - KARKAPATLA | MWCU2991560 | 40RF | CARRIER THINLINE | SERVICE-AT SITE | LEASE | FOC | UNIT NOT WORKING | NEED TO REPLACE THE CAPACITOR | CONDENSER CAPACITOR | Yes | UNIT HAS CONDENSER CAPACITOR DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP092%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | SHAHBUDDIN | Yes | SERVICING | 2025-11-11 11:34 | crm@crystalgroup.in | NO
SEP093/25 | 2025-09-29 11:23 | crm@crystalgroup.in | BEJAPURI DAIRY | LAKHWINDER SINGH | 9876772453 | MAINTAINENCE MANAGER | MYRU4503459 |  |  | lakhwindersingh@countrydelight.in | Patanchuru | Preventive Maintenance |  | Call | shahbudin | [54 empty] | 2025-10-09 20:15 | 2025-09-28 |  |  |  |  | MYRU4503459 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/180psig | 10.3/10 4/10.3 | 412/411/412 v | Short | Pm servic due | Pm service completed with checked unit operation and found working as satisfactory. Pls find the attached job orders for details | Yes | https://drive.google.com/open?id=17VPc7-9Jx5497EU5CDUPBTFNGNbs1Nbh | https://drive.google.com/open?id=15IFq6gjnQ6gQ0m17HUkUofx0SV0FA24r |  | 115-SHABUDIN- HYD | No | No | Can be done on next PM | Na | Sheet key - Daikin / Condenser Fan Grill daikin / suction low side cap | technician@crystalgroup.in | REEFER
SEP094/25 | 2025-09-29 12:42 | crm@crystalgroup.in | Shivamrut | Anil Waghmode | 8408027721 | Site in-charge | CXRU1032498 | Issue with display |  | shivamrutakluj@gmail.com | Solapur | Running with issues |  | Call | Sushma | 2025-10-07 16:13 | crm@crystalgroup.in | Shivamrut | CXRU1032498_40RF | 40 feet | Daikin | SERVICE-ON CALL | NA | NA | display issue and sheet key issue ,need to change both | both need to be changed as soon as possible | 1)display 2)Sheet key |  | Display and key sheet not working properly | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP094%2F25 | NA | DAIKIN | NA | NA | NA | NA | NA | SITARAM | Yes | Issue with display | 2025-11-11 11:30 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-11 11:30 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-11 11:30 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=SEP094%2F25
SEP095/25 | 2025-09-30 11:24 | crm@crystalgroup.in | Zenfold Pharma | Harshavardhan | 94935 60304 | Manager | TRIU6618637 |  |  | harshavardhan@zenfoldst.com | Hyderabad | Preventive Maintenance |  | Call | Shahbudin | [54 empty] | 2025-10-09 20:01 | 2025-09-30 |  |  |  |  | TRIU6618637 |  |  |  | Carrier | -20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 12/210 psig | 12.8/12.9/12.8 | 413/413/412 | Short | Pm service due | Pm service completed with checked unit operation & found working as satisfactory | Yes | https://drive.google.com/open?id=1VKCSyp0WYxPgl9O0q4MeWn7EXDGQ0fI6 | https://drive.google.com/open?id=1JFexN_S56lhQRt_TuyIY8HKPUq6iWBjy |  | HYD- 115-SHABUDIN | No | No | Can be done on next PM | Na | Supply sensornos.2/ key pad/ internal tube light nos.2 | technician@crystalgroup.in | REEFER
SEP096/25 | 2025-09-30 15:42 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | SUBBA REDDY | 8106009300 | WAREHOUSE MANAGER | BMOU9787239 | Sheet key problem with display | display Sheet key required | Subbareddy.Mandadi@apitoria.com | Vishakapatnam | Running with issues |  | Call | SHUBHAM | 2025-10-08 13:52 | service@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | BMOU9787239 | 40RF | DAIKIN | SERVICE-AT SITE | LEASE | FOC | Unit has display & sheet key defective | NEED TO REPLACE THE DISPLAY & SHEET KEY | DAIKIN SHEET KEY & DISPLAY | Yes | UNIT HAS DISPLAY & KEYPAD DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=SEP096%2F25 | DAIKIN | DAIKIN | NA | NA | NA | USED | NA | VIRENDRA | Yes | Sheet key problem with display | 2025-10-18 15:10 | crm@crystalgroup.in | YES | IN249 | 2025-10-09 |  | Apitoria Pharma Pvt Ltd, Unit - 4U |  | BMOU9787239 | SITE |  |  | 2025-10-18 15:11 | crm@crystalgroup.in | YES | IN249 | YES |  | Stock
OCT001/25 | 2025-10-03 12:10 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | SHRINIVAS | 08916762247 , 0990812799 | MANAGER | CSRU6101910 | Display issue |  | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues | issue with the display | Call | Sitaram | 2025-10-08 13:48 | service@crystalgroup.in | Lauras unit 2 | CSRU6101910 | 40RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | UNIT HAS DISPLAY DEFECTIVE | NEED TO REPLACE THE DISPLAY | DISPLAY THERMOKING MP4000 | Yes | UNIT HAS DISPLAY DEFECTIVE | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT001%2F25 | THERMOKING MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | SITARAM | Yes | Display issue | 2025-10-16 15:32 | crm@crystalgroup.in | YES | IN300 | 2025-10-16 |  | Lauras unit 2 |  | CSRU6101910 | SITE |  |  | 2025-10-18 14:51 | crm@crystalgroup.in | YES | IN300 | YES |  | Stock | 2025-10-18 14:55 | crm@crystalgroup.in | YES | IN300 | COURIER | NA | NA
OCT002/25 | 2025-10-03 12:18 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | SHRINIVAS | 08916762247 , 0990812799 | Manager | PGRU4958724 | Showing al 59 HTT |  | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues | Showing al 59 HTT | Call | Sitaram | 2025-10-07 16:31 | crm@crystalgroup.in | Lauras unit 2 | PGRU4958724 | 40 feet | Carrier | SERVICE-AT SITE | NA | NA | Heat termination thermostat (HTT) need to be replaced | need to be replaced | 1)Heat termination thermostat (HTT) | Yes | Heat termination thermostat (HTT) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT002%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | Na | Na | SITARAM | Yes | Showing al 59 HTT | 2025-10-17 13:12 | crm@crystalgroup.in | YES | IN304 | 2025-10-17 |  | Lauras unit 2 |  | PGRU4958724 | SITE |  |  | 2025-10-18 14:55 | crm@crystalgroup.in | YES | IN304 | YES |  | Stock | 2025-10-18 14:56 | crm@crystalgroup.in | YES | IN304 | COURIER | NA | NA
OCT003/25 | 2025-10-03 13:49 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | SHRINIVAS | 9908127999 | Manager | BMOU9782197 | Issue with sensor |  | murthy.ss@lauruslabs.com | Vishakapatnam | Running with issues | ISSUE WITH SENSOR | Call | SITARAM | 2025-10-07 16:28 | crm@crystalgroup.in | Lauras lab unit 2 | BMOU9782197 | 40FT STD RF | Daikin | SERVICE-AT SITE | NA | NA | Data recorder sensor and return sensor need tone replaced | need to be replaced | 1)Data recorder sensor 2)return sensor | Yes | Data recorder sensor and return sensor | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT003%2F25 | DAikin | DAIKIN | NZ | DECOSIIIF/2553/1 | NA | Used | NA | SITARAM | Yes | Issue with sensor | 2025-10-16 15:37 | crm@crystalgroup.in | YES | IN301 | 2025-10-16 |  | Lauras lab unit 2 |  | BMOU9782197 | SITE |  |  | 2025-10-18 14:50 | crm@crystalgroup.in | YES | IN301 | YES |  | Stock | 2025-10-18 14:51 | crm@crystalgroup.in | YES | IN301 | COURIER | NA | NA
OCT004/25 | 2025-10-03 15:27 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | SIte in-charge | TITU9930222 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-05 08:24 | 2025-10-02 |  |  |  |  | TITU9930222 |  |  |  | Thermo king | 21c, s. 21.2, ret. 21.7c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4b 17.4b | 7.1a 7.1a 7.1a | 400 400 400 | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1q4SF-x5fW62rDwfHw0O5nHf6qtECiBjw | https://drive.google.com/open?id=1cMVVFA-2LYFAKILFYPZgC3hfgQFaJOeD |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT006/25 | 2025-10-03 16:22 | crm@crystalgroup.in | Dr. REDDY FTO 9 | K Ram | 9966816434 | FM TEAM | CICU1920740,CICU1920735 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-05 08:28 | 2025-10-03 |  |  |  |  | CICU1920740,CICU1920735 |  |  |  | Thermo king | 2.0c 2.0c ,supp. 3.7c, 3.6c, return 2.0c, 2.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4b 16.4b | 6.9a 6.9a 6.9a | 402 402 402 | Not done | Pm service two vay unit | Both unit working in good condition | No | https://drive.google.com/open?id=1s9k6_GniWEHl3KL1S4pPVwm5Sfyc3V19 | https://drive.google.com/open?id=1BqTYhqvhUuiPeLm1Y9Ip2900neZ54Ntt |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT007/25 | 2025-10-03 16:30 | crm@crystalgroup.in | Dr Reddy FTO 9 | Sai Babu | 96188 49181 | Manager | TRIU6616969 |  |  | mavulurisaibabu@drreddys.com | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-04 18:00 | 2025-10-03 |  |  |  |  | TRIU6616969 |  |  |  | Carrier | 5.0c, s. 4.9c, 5.2c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0. 2b 13.4b | 11.9a 11.9a 11.9a | 400 400 400 | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1UVkFq0cLeTzoslXoyi7pwSZBViuP1YEF | https://drive.google.com/open?id=14TitqPoudt-45adollCddoSluc4LLyjo |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT008/25 | 2025-10-03 16:40 | crm@crystalgroup.in | DR REDDY FTO 7 | FAWAD | 8484936735 | Manager | CICU1938117 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-04 17:57 | 2025-10-03 |  |  |  |  | CICU1938117 |  |  |  | Thermo king | 2.0,c sup. 3.7c, ret. 2.0c, two bay unit | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4b, 0.4b 16.4b 17.2b | 6.9a 6.9a 6.9a | 402 402 402 | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1RwrogkdY2LpvYTxGN-83pg1PbDBMPCAs | https://drive.google.com/open?id=1lVT8XxPtwcEs02riaYweNgJZbTJyBiMd |  | Na | No | No | Can be done on next PM | Na | Nan | technician@crystalgroup.in | REEFER
OCT009/25 | 2025-10-03 16:43 | crm@crystalgroup.in | DR REDDY FTO 7 | Ajit Kumar Sahu | 98228 84152 | Manager | PCIU6025808 |  |  | NA | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-04 17:49 | 2025-10-03 |  |  |  |  | PCIU6025808 |  |  |  | Daikin | 20'c supply 20.1c, return 19.9c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4b, 16.4b | 6.9a 6.9a 6.9a | 402 402 402 | Not done | Pm service | Unit working finen | No | https://drive.google.com/open?id=1eXJpcSi6F1rfnTro8DFI9WvF1SMqfnSV | https://drive.google.com/open?id=1zapRVCgLFySCYVW8Tvq9709vQh3Ik6Al |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT010/25 | 2025-10-04 10:31 | crm@crystalgroup.in | BIOLOGICAL | Marthanda | 9949033007 | Manager | CICU1441645 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-09 17:02 | 2025-10-03 |  |  |  |  | CICU1441645 |  |  |  | Thermo king | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/27br | 10.2/10.3/10.2 | 402/403/402 | Short | Pm due | Pm service completed with checked unit operation & found working as satisfactory | No | https://drive.google.com/open?id=1HIhFRZx3Ch0oi5HcdqFOF9ADj97vwkRn | https://drive.google.com/open?id=1vLE-yWfCGTGP9rhn88kndvFB5VchkRUV |  | 125/ SHABUDIN- HYD | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT011/25 | 2025-10-04 11:07 | crm@crystalgroup.in | Parle Biz | Supreet Singh Lamba | 9917480215 | Manager | MYRU45067345R1 | E401, E402, H006. Error codes |  | supreet.lamba@parle.biz | Sitarganj | Running with issues | Errror codes E401, E402, H006. | Email | Pushpa
OCT017/25 | 2025-10-04 12:32 | crm@crystalgroup.in | LAURUS UNIT -1 | Somireddy | 8916601423 | Manager | CICU1442209 | FLUCTUATIONS IN TEMEPRATURE |  | somireddy.k@lauruslabs.com | Parvada USP | Running with issues |  | Email | Pushpa | 2025-10-04 17:55 | crm@crystalgroup.in | Lauras lab unit 1 | CICU1442209 | 40-RF 2 bay unit | 2021 | SERVICE-ON CALL | SALE |  | Deforestation issue | NA |  | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT017%2F25 |  | TK-MP4000 | NA | Na | NA | Na | Na | SITARAM | No | FLUCTUATIONS IN TEMEPRATURE | 2025-10-04 17:57 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-04 17:57 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-04 17:58 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-04 18:09 | 2025-10-04 |  |  |  |  | CICU1442209 |  |  |  | Thermo king | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | NA | NA | NA | Not done | NA | Handled over call | No | https://drive.google.com/open?id=1ngzVVButkRBhNpig9bz2Sa0fiXhAWtjV | https://drive.google.com/open?id=1FGexHoOLl0D2IuIvbcoWRD6vWUHMRz2M |  | NA | No | No | Can be done on next PM | NA | Na | crm@crystalgroup.in | REEFER
OCT019/25 | 2025-10-04 14:47 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Executive-projects | PCIU6008328 | DOOR NOT CLOSING | Request for photos | naveedahmed.m@sailife.com | Bidar | Running with issues | received on 18th September -Door is not closing properly | Email | Pushpa | [54 empty] | 2025-10-09 16:53 | 05/09/0025 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 20/180psig | 22.8/12.9/12.8 | 402/403/402 | Not done | Unit for Instalation and removed main unit | Reefer unit for Instalation | No | https://drive.google.com/open?id=1CmYgXFjA8wigvfQMdCULFzgSAAEp0-oo | https://drive.google.com/open?id=19LAW9H1D-qUOqNvFKq7ECs6is3gMvYef |  | 125- | No | No | Can be done on next PM | Unit bolts securing | Na | technician@crystalgroup.in | REEFER
OCT027/25 | 2025-10-06 10:32 | crm@crystalgroup.in | DR. REDDY LAB CTO-5 | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | SIte in-charge | CXRU1032564 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Shabudin | [54 empty] | 2025-10-09 16:33 | [54 empty] | technician@crystalgroup.in | DRY/Others
OCT028/25 | 2025-10-06 10:47 | crm@crystalgroup.in | DR. REDDY LAB CTO-5 | T.Sreeram Naik | 7036305829 | Site in-charge | CXRU1045896 |  |  | sreeramnt@drreddys.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-09 16:23 | 04/10/0025 |  |  |  |  | CXRU1045896 |  |  |  | Daikin | +4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/190psig | 10.4/10.5/10.4 | 403/404/404 v | Short | Pm service & internal Audit company | P. M. Service completed with checked unit operation & found working as satisfactory | No | https://drive.google.com/open?id=1DbtzH3gqKlT5DpTVByDasMtdYgtY_qmM | https://drive.google.com/open?id=1P4pFmVwNSoxpHK-i6zAXyLkaAMji4Uqg |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT029/25 | 2025-10-06 11:14 | crm@crystalgroup.in | DR. REDDY LAB CTO-5 | Krishna Thoutam ¦ Sreeram Naik | 9704500721 ¦ 9392986929 | Site in -charge | GSOU6384153 |  |  | krishnathoutam@drreddys.com ¦ sreeramnt@drreddys.com | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-09 16:12 | 2025-10-04 |  |  |  |  | GSOU6384153 |  |  |  | Carrier | +18.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/210psig | 13.2/13.3/13.2 | 404/403/403 v | Short | Pm due | Pm service completed with checked unit operation & found as satisfactory. Need to replaced Three phase Evaprator motor. | Yes | https://drive.google.com/open?id=1bQgecXVA5QKSfVXh2u9z5e57mhTFCviw | https://drive.google.com/open?id=1kbMcmLLgUIYyyESofZVXS1huu7yzh9DM |  | 115 | Yes | No | Can be done on next PM | Next pm need to replaced Evaprator motor | Three phase Evaprator motor left side | technician@crystalgroup.in | REEFER
OCT036/25 | 2025-10-06 14:02 | crm@crystalgroup.in | Quick supply chain PVT LTD | Ranveer | +91 98726 09126 | Maintenence department | SJKU400002 | MOTOR MAKING NOISE |  | NA | Rajpura, Punjab | Running with issues |  | Email | ERIC | 2025-10-07 16:23 | crm@crystalgroup.in | Quick supply | SJKU400002 | 40 feet | Carrier | SERVICE-ON CALL | NA | NA | Condensor motors bearing need to be replaced | need to be replaced | condensor motor bearing | Yes | condenser motor bearing issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT036%2F25 | 2016 | CARRIER-PRIMLINE | NA | NA | NA | NA | NA | SITARAM | Yes | MOTOR MAKING NOISE | 2025-10-17 14:30 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 14:30 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 14:31 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-04 17:33 | 2025-11-04 |  |  |  |  | SJKU400002 |  |  |  | Carrier | +2 Ret.+2.9C Sup.+1.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 1.7bar Discharge 10.8bar | R 8.6A B 9.2A Y 8.6A | 395V 395V 395V | Not done | Pm service and general inspection | Condenser motor bearing replaced and service | No | https://drive.google.com/open?id=1SFU2I8pwRVMXZrNRAkl28Z75TSrODFvN | https://drive.google.com/open?id=1phwSg1GuXGP0znpAhKSLGIyLkE6WcGJk |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
OCT037/25 | 2025-10-06 16:04 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 9154037279 | Site in-charge | CXRU1035861 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 12:53 | 2025-10-05 |  |  |  |  | CXRU1035861 |  |  |  | Daikin | 22.0c, supply 21.9C, return 22.2c | Clean | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 11.2B | 7.9A 7 9A 7.9A | 420v | Not done | Pm service | Unit working fine but some of sensor not working properly | Yes | https://drive.google.com/open?id=1MljjidfzcxXOVXKfXvgUPeFc-NhLf1lL | https://drive.google.com/open?id=1f7SOLJgmFDlKowm7tG1smBJFKx_5gOJa |  | Na | Yes | Yes | Can be done on next PM | Same | Supply sensor Outlet sensor Inlet sensor Return sensor User panel without display | technician@crystalgroup.in | REEFER
OCT038/25 | 2025-10-06 16:07 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 91540 37279 | Site in -charge | GESU9469328 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 12:13 | 2025-10-05 |  |  |  |  | GESU9469328 |  |  |  | Carrier | 23.0C, supply 23.9c, return 23.6c | Clean | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 14.3B | 7 2A 7 2A 7.2A | 422v | Not done | Pm service | Unit working in good condition, condensor coil need to wash | No | https://drive.google.com/open?id=16dW0HjTL3Z5Dha-Sx1VVLG9U7D703YvY | https://drive.google.com/open?id=1HAy9tPGffMcvUr-613snAAfEpNGD40_l |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT039/25 | 2025-10-06 16:11 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 91540 37279 | Site in-charge | GESU9379498 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 12:09 | 2025-10-05 |  |  |  |  | GESU9379498 |  |  |  | Carrier | 0.1b, 14.4B | Clean | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1B 14.4B | 9.2A 9.2A 9.2A | 425v | Not done | Pm service | Unit working in good condition, but discharge sensor out of calibration need to change | Yes | https://drive.google.com/open?id=1zhOB848EIPsu12a-Lo1-zIAVEcUMJnL2 | https://drive.google.com/open?id=1SkLJpyWqAOHfdGlVIFpZXOGIOkOSij3U |  | Na | Yes | Yes | Can be done on next PM | Discharge sensor | Discharge sensor | technician@crystalgroup.in | REEFER
OCT040/25 | 2025-10-06 16:16 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 91540 37279 | Site in-charge | CXRU1031758 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 12:05 | 2025-10-05 |  |  |  |  | CXRU1031758 |  |  |  | Daikin | 23.0c, supply 22.2C, return 23.6c | Clean | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3B 11.9B | 8.1A 8.1A 8.1A | 450v | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1eSobJhScwIYV801JqwK0-HWqouVCMHJk | https://drive.google.com/open?id=1dd1uYWiAakxPo9YNS6oPgnhpxVLxFgmI |  | Na | Yes | Yes | Can be done on next PM | User panel without display | User panel without display | technician@crystalgroup.in | REEFER
OCT041/25 | 2025-10-06 16:18 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 91540 37279 | Site in-charge | TRIU8731339 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 12:00 | 2025-10-05 |  |  |  |  | TRIU8731339 |  |  |  | Carrier | 22.0c, supply 22.0c , 21.9c | Clean | Rusty |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3B 14.4b | 13.9A 13.1A 13.9A | 440v | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1sTCTO7dGXNLz81AzTTZxizyraQZPqKiQ | https://drive.google.com/open?id=1Aa2UTzVd-01D3DSPostBbOV3IC_Y649d |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT042/25 | 2025-10-06 16:19 | crm@crystalgroup.in | Divis Lab unit 3 | Choudhary | 91540 37279 | Site in-charge | CSRU6101925 | AMC |  | M.Ramakrishna@divislabs.com | Kakinada | AMC |  | Call | Pushpa | [54 empty] | 2025-10-10 11:56 | 2025-10-05 |  |  |  |  | CSRU6101925 |  |  |  | Carrier | 20.0c, supply 19.5c, return 20.3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B 13.9B | 13.9A 13.6A 13.9a | 450v, | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1MmOnzjgbwl1XOZNVScy6kPg6CyqHU0Bg | https://drive.google.com/open?id=1-DKQQCNK4UNJNeI7WGvSpCWmtbQlCixr |  | Na | No | No | Can be done on next PM | Nan | Na | technician@crystalgroup.in | REEFER
OCT043/25 | 2025-10-06 17:19 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site in charge | TITU9930222 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-10 11:53 | 2025-10-02 |  |  |  |  | TITU9930222 |  |  |  | Thermo king | 21.0C, supply 21.3, return 21.7c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 17.4B | 7.1A 7.1a 7.1a | 400v | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=11gVrdmnpRNp2scVpfW9dumIpWKk9LacD | https://drive.google.com/open?id=1-kVguDlmsUX9mb7IZ-BE_0lG3m6FPtqX |  | Nan | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT044/25 | 2025-10-06 17:21 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | Site in charge | HDMU5586473 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-07 10:36 | 2025-10-02 |  |  |  |  | HDMU5586473 |  |  |  | Thermo king | 22.8C, supply 23.4C, return 21.2C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 14.9B | 7.9A 7.9a 7.9A | 407V | Not done | Pm service | Unit working in good condition | No | https://drive.google.com/open?id=1Ac8TINyUid-UJw3ptE_O0f9asZUyDj35 | https://drive.google.com/open?id=13VCDxmpslehbMzoY7V9A7v6QRSzOj7sR |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT045/25 | 2025-10-06 17:23 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | site in charge | HDMU5584444 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-07 10:12 | 2025-10-02 |  |  |  |  | HDMU5584444 |  |  |  | Thermo king | 22.8C, supply 23.4C, , return 21.2C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9B 14.4B | 7.9A 7 9A 7 9A | 407V | Not done | Pm | Unit working in good condition | No | https://drive.google.com/open?id=1Je-oaXTZK8I6VpoXDLqIC6nlGxzFCEEN | https://drive.google.com/open?id=1IDDjbOiVC2cholL5E5TavXnh2ea1l8ef |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT046/25 | 2025-10-06 17:24 | crm@crystalgroup.in | LAURUS LAB UNIT 2 | Murthy | 9908127999 | site in charge | GESU9529290 |  |  | murthy.ss@lauruslabs.com | Vishakapatnam | Preventive Maintenance |  | Call | Sitaram | [54 empty] | 2025-10-10 11:33 | 2025-10-02 |  |  |  |  | GESU9529290 |  |  |  | Carrier | 22.0c, supply 21.7c, return 22.1c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0 4B 11.4B | 6.8A 6.8A 6.8A | 401V 401V 401V | Not done | Pm service | Unit working fine | No | https://drive.google.com/open?id=1wnT7aFlGd0EQaF879L_FdYO8iuamfgT0 | https://drive.google.com/open?id=1DeQiDvPG1xrcCsh1KWQiTjU4F5JsnodW |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT049/25 | 2025-10-07 10:41 | crm@crystalgroup.in | Prayagh Consumer Care Pvt LTD | Ravi | 9849719841 | Site in charge | MYRU4500552 |  |  | NA | Hyderabad | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-09 11:47 | 2025-10-06 |  |  |  |  | MYRU4500552 |  |  |  | Thermo king | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18 br | 10.2/10.3/10.2 | 412/413/412 | Short | Pm service due | Pm service completed with checked unit operation & found working as satisfactory | No | https://drive.google.com/open?id=1V8Mn4PXN4qoWb9mHbUUjI3VJfmQqqrWt | https://drive.google.com/open?id=1x03X9IaOT77r3LhpIm7GIpMUJqE55A34 |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT050/25 | 2025-10-07 16:49 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | MYRU4518356 | Sensor Issue |  | gopal5.krishna@qwick.co.in | Lucknow | Complete Breakdown |  | Call | Sitaram
OCT051/25 | 2025-10-08 15:47 | crm@crystalgroup.in | Switz International | Vijay | +91 98202 23249 | Site in-charge | TITU8259465 | Commpressor not working |  | vijayj@india.switzgroup.com | Kadaiya,nani Daman | Running with issues | Compressor not working | Call | Shubham | 2025-10-10 14:41 | service@crystalgroup.in | Switz International | TITU8259465 | 20RF | THERMOKING MP4000 | SERVICE-AT SITE | LEASE | FOC | unit not working | NEED TO VISIT THE SITE | NA | WILL CONFIRM AFTER INSPECTION | COMPRESSOR IS GETTING OVERHEATED (SUSPECTED FAILURE) | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT051%2F25 | Thermoking MP4000 | TK-MP4000 | NA | NA | NA | USED | NA | Avinash | Yes | Commpressor not working | 2025-10-24 22:54 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-24 22:55 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-24 22:56 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-03 09:09 | 2025-11-02 |  |  |  |  | TITU8259465 |  |  |  | Thermo king | -22.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2/22.3 | 11.1/10.9/11.1 | 407/405/407 | Full | Reparing | Impaction valve replace | No | https://drive.google.com/open?id=1S7YcSV-86fDInXDrhcCSfxurX08JK-2l | https://drive.google.com/open?id=1rUcdst0cIRedsoOsyRGdW66DuIWX0GHB |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT052/25 | 2025-10-08 21:21 | crm@crystalgroup.in | Indradeep Infra India Private Limited | Hitesh | 7756804448 | Site in charge | MYRU4513729 | Container going in defrost mode |  | NA | Wadala | Running with issues |  | Call | Sushma | 2025-10-08 22:36 | technician@crystalgroup.in | Indradeep Infra India Private Limited | MYRU4513729 | 40FT STD RF | Daikin | SERVICE-ON CALL | NA | CHARGEABLE | Sensor issue | Sensor out of range | Inlet sensor Sheet key | Yes | Sensor issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT052%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes | Container going in defrost mode | 2025-10-22 15:16 | crm@crystalgroup.in | YES | IN248 | 2025-10-09 |  |  |  |  | SITE |  |  | 2025-10-22 15:17 | crm@crystalgroup.in | YES | IN248 | YES |  | Stock | 2025-10-22 15:18 | crm@crystalgroup.in | YES | IN248 | COURIER | NA | NA
OCT053/25 | 2025-10-09 11:16 | crm@crystalgroup.in | GMR | JAGDISH | 9665253099 | Site in charge | CCLU1030439 | DISPLAY NOT VISIBLE |  | Jagadeesh.Tallur@gmrgroup.in | Goa | Running with issues | Display not working | Email | Pushpa | 2025-10-09 11:22 | crm@crystalgroup.in | GMR | CCLU1030439 | 20 feet reefer | Carrier (thin line) | SERVICE-AT SITE | SALE | CHARGEABLE | complete breakdown | part needs to be replaced and also the display | 1)Carrier controller (ml3) 2)Carrier Display | Yes | Carrier ml3 controller black out | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT053%2F25 | NA: CARRIER; NA: CARRIER-THINLINE; NO: SHAHBUDDIN; No: Yes | DISPLAY NOT VISIBLE | 2025-11-04 12:10 | crm@crystalgroup.in | YES | IN318 | 2025-10-24 |  |  |  |  | SITE |  |  | 2025-11-04 12:25 | crm@crystalgroup.in | YES | IN318 | YES |  | Stock
OCT054/25 | 2025-10-09 14:51 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | Subba Reddy | 81060-9300 | Site in charge | ACRU4530720 | Complete breakdown |  | NA | Vishakapatnam | Running with issues |  | Call | Shubham | 2025-10-09 16:02 | service@crystalgroup.in | Apitoria | ACRU4530720 | 40RF | CARRIER | SERVICE-AT SITE | LEASE | FOC | unit has condenser capacitor defective | NEED TO REPLACE CONDENSER CAPACITOR | CONDENSER CAPACITOR | Yes | UNIT WAS DISPLAYING ALARM 25 | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT054%2F25 | CARRIER THINLINE | CARRIER-THINLINE | NA | NA | NA | USED | NA | AVINASH | Yes | Complete breakdown
OCT055/25 | 2025-10-09 17:17 | crm@crystalgroup.in | Dr.Reddy | Arun | 8159078756 | Site in charge | SEGU9107489 | SERVICING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-14 12:42 | technician@crystalgroup.in | Dr.Reddy | SEGU9107489 | Na | Na | SERVICE-AT SITE |  |  | Door issue | Na | Na | No | Door issues has been rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT055%2F25 | Nan | DAIKIN | Na | Na | Na | Na | Na | Not required | No | SERVICING | 2025-10-22 15:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-22 15:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-22 15:04 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-14 14:33 | 07/10/0025 |  |  |  |  | SEGU9567638 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/200 psig | 11.3/11.4/11 3 | 413/412/413 | Short | Instalation & door issue | Instalation completed with door issue resolved | No | https://drive.google.com/open?id=1QLUcnDy2zpsBMyq6PWTBvWGuqt71tvew | https://drive.google.com/open?id=1rXy4FaJq8uIRxNeLr_a2yUnVjAcJ2_WC |  | 115 | No | No | Can be done on next PM | Na | Greace& oil | technician@crystalgroup.in | REEFER
OCT056/25 | 2025-10-09 17:20 | crm@crystalgroup.in | Dr.Reddy | Arun | 8159078756 | Site in charge | SEGU9055868 | SERVICING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-14 12:49 | technician@crystalgroup.in | Dr.Reddy | SEGU9055868 | Na | Na | SERVICE-AT SITE | NA | NA | Door not close smoothly | Greasing required on door hinges | Greas and oil 1kg | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT056%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | SERVICING | 2025-10-22 15:24 | crm@crystalgroup.in | YES | IN287 | 2025-10-14 |  |  |  |  | SITE |  |  | 2025-10-22 15:26 | crm@crystalgroup.in | YES | IN287 | YES |  | Stock | 2025-10-22 15:27 | crm@crystalgroup.in | YES | IN287 | COURIER | NA | NA |  |  |  | 2025-10-11 21:53 | 05/10/0025 |  |  |  |  | SEGU9107489 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 6/200psig | 10.2/10.3/10.3 | 413/414/414 | Short | Unit Instalation & Main Door servicing with oil & greace | Instalation done with main door servicing completed | Yes | https://drive.google.com/open?id=1MniMopCuW1S5bHsaP5z9YU2fkm5hsh69 | https://drive.google.com/open?id=1hbf9JWWF3xpymMjH8oa6-QiFR2NsWu-U |  | 115 | No | No | Can be done on next PM | Na | Greace,& oil - job done | technician@crystalgroup.in | REEFER
OCT057/25 | 2025-10-09 17:22 | crm@crystalgroup.in | Dr. Reddy | Arun | 8159078756 | Site in charge | SEGU9569820 | SERVICING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-14 12:51 | technician@crystalgroup.in | Dr. Reddy | SEGU9569820 | Na | Na | SERVICE-AT SITE | NA |  | Door not operating smoothly need greasing | Greasing required on door hinges | Greas 1kg 300ml oil | Yes | Greasing required on door hinges | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT057%2F25 | Na | DAIKIN | Na | Nan | Na | Na | Na | SHAHBUDDIN | Yes | SERVICING | 2025-10-22 15:30 | crm@crystalgroup.in | YES | IN288 | 2025-10-14 |  |  |  |  | SITE |  |  | 2025-10-22 16:31 | crm@crystalgroup.in | YES | IN288 | YES |  | Stock | 2025-10-22 16:32 | crm@crystalgroup.in | YES | IN288 | COURIER | NA | NA |  |  |  | 2025-10-11 22:01 | 07/10/0025 |  |  |  |  | SEGU9055868 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/210psig | 12.1/12.2/12.1 | 414/415/414 | Short | Instalation & door servicing | Instalation completed with door oil & grecing service done | No | https://drive.google.com/open?id=1iWs8OlI1alETL6Xmf3XhRpMjp3aH_Uaj | https://drive.google.com/open?id=1MMuzXzYZieISBXjb4p3YhEsiJ_z1QEbV |  | 115 | No | No | Can be done on next PM | Na | Oil & greace | technician@crystalgroup.in | REEFER
OCT058/25 | 2025-10-09 17:24 | crm@crystalgroup.in | Dr.Reddy | Arun | 8159078756 | Site in charge | CXRU1309957 | SERVICING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-14 12:52 | technician@crystalgroup.in | Dr.Reddy | CXRU1309957 | Na | Nan | SERVICE-AT SITE | NA | NA | Door issues has been rectified | Rectified |  | No | Rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT058%2F25 | Na | DAIKIN | Na | Nan | Na | Na | Na | No need | No | SERVICING | 2025-10-22 15:06 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-22 15:07 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-22 15:07 | crm@crystalgroup.in | NO
OCT059/25 | 2025-10-09 17:26 | crm@crystalgroup.in | Dr.Reddy | Arun | 8159078756 | Site in charge | SEGU9567638 | SERVICING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-14 15:00 | technician@crystalgroup.in | Dr.Reddy | SEGU9567638 | Na | Na | SERVICE-AT SITE | NA | NA | Unit working fine, door issues has been rectified | Rectified |  | No | Rectified | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT059%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | No need | No | SERVICING | 2025-10-22 15:09 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-22 15:09 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-22 15:09 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-11 22:16 | 07/10/0025 |  |  |  |  | CXRU1309957 |  |  |  | Carrier | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/215 psig | 11.2/11.3/11.3 | 412/413/412 | Short | Instalation & door service | Instalation completed with door service with oil & greace | No | https://drive.google.com/open?id=1TgrTghTSIs6_am5NbGe4LerT0FGMzUrz | https://drive.google.com/open?id=1OW9AT7vubph3gmwWxc01xPIT1wMXOBwK |  | 115 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT063/25 | 2025-10-10 18:22 | crm@crystalgroup.in | Kirloskar Corrocoat | Kunal | 9881003659/9890385995 | Site in charge | PCIU5822411 | complete breakdown |  | NA | GHATAMPUR | Running with issues |  | Call | Sitaram | 2025-10-10 18:26 | technician@crystalgroup.in | KIRLOSKAR | PCIU5822411 | 20FT STD RF | Daikin | SERVICE-ON CALL | NA | NA | Unit giving alaram 101, | Short-out on call, unit working properly | Na | No | Giving alaram 101, on call issues has been rectified, unit working fine | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT063%2F25 | Daikin | DAIKIN | LXIDEA33A | Na | Na | Used | JSGA623040170 | SITARAM | No | complete breakdown | 2025-10-22 15:11 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-22 15:11 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-22 15:12 | crm@crystalgroup.in | NO
OCT065/25 | 2025-10-11 12:38 | crm@crystalgroup.in | RELIANCE | Himanshu | 7862848707 | Site in charge | CCLU1031918 | SERVICING |  | NA | Jamnagar | Running with issues |  | Call | Sitaram | 2025-10-16 15:08 | technician@crystalgroup.in | Reliance | CCLU1031918 | 20FT | Na | SERVICE-ON CALL | NA | NA | Compressor grounded need to replenishment | Immediate | Compressor thin line 1 no's Oil 3.5 ltr, Gas 5kg R134a, Gas kit suction 1 no's Gas kit discharge 1 no's Filter drier 1 no's Compressor terminal kit 1 no's, Compressor contractor 30A 1 no's, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT065%2F25 | Na | CARRIER-THINLINE | Nan | Na | Na | Na | Na | Avinash | Yes | SERVICING | 2025-10-22 15:33 | crm@crystalgroup.in | YES | IN262 | 2025-10-11 |  |  |  |  | SITE |  |  | 2025-10-22 15:34 | crm@crystalgroup.in | YES | IN262 | YES |  | Stock | 2025-10-22 15:35 | crm@crystalgroup.in | YES | IN262 | COURIER | NA | NA |  |  |  | 2025-10-29 09:40 | 2025-10-28 |  |  |  |  | CCLU1031918 |  |  |  | Carrier | +7.0 sup7.0 ret 9.10c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.3/15.9 | 18.1/17.9/18.1 | 402/402/402v | Short | Reparing | Compressor replace | No | https://drive.google.com/open?id=163cKgaat8ejzXeOHSjLvP7iaN_lywZAR | https://drive.google.com/open?id=1DAIHAJq6GbmzavZPEMt4ykhTURP7MsTE |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT066/25 | 2025-10-11 15:06 | crm@crystalgroup.in | Tata Advanced Systems Ltd | Sachin | 7337832756 | Site in charge | CZZU6009100 | DISPLAY NOT VISIBLE, Evaporator broken |  | NA | Bangalore | Running with issues | I visited the site and found the container wasn't cooling. Upon inspection, I found no ice. After removing the cover, I noticed the left side evaporator motor blade had broken and fallen onto the coil, causing the issue. Additionally, the keypad and display are also damaged and will need to be replaced. | Call | Sitaram | 2025-10-11 15:33 | technician@crystalgroup.in | Tata Advanced Systems Ltd | CZZU6009100 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Evaporator motor defective need to change, Fan blade need to replace, Sheet key not working properly need to change Display not visible properly | Na | Evaporator motor Fan blade Sheet key Display | Yes | Repair required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT066%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes | DISPLAY NOT VISIBLE, Evaporator broken | 2025-10-22 16:47 | crm@crystalgroup.in | YES | IN266 | 2025-10-11 |  |  |  |  | SITE |  |  | 2025-10-22 16:48 | crm@crystalgroup.in | YES | IN266 | YES |  | Stock | 2025-10-22 16:49 | crm@crystalgroup.in | YES | IN266 | COURIER | NA | NA
OCT068/25 | 2025-10-11 15:26 | crm@crystalgroup.in | Chemplast Sanmar Limited | C. MOHAN | 04344 350400 2218 | Site in charge | HDMU5501938 | DISPLAY NOT VISIBLE, I visited the site and found the container wasn't cooling. Upon inspection, I found no ice. After removing the cover, I noticed the evaporator motor blade had broken and fallen onto the coil, causing the issue. Additionally, the keypad and display are also damaged and will need to be replaced. |  | Na | BERIGAJ, HOSUR | Running with issues |  | Call | Sitaram | 2025-10-11 15:41 | technician@crystalgroup.in | CHEMPLAST SANMAR LTD | HDMU5501938 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Evaporator motor defective need to change, Fan blade need to change User panel need to change Sheet key need to change | Na | Evaporator motor 01, Fan blade 01, Sheet key 01, User panel 01, | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT068%2F25 | Daikin | DAIKIN | Na | Na | Na | brand New | JSGA623040307 | SITARAM | Yes | DISPLAY NOT VISIBLE, I visited the site and found the container wasn't cooling. Upon inspection, I found no ice. After removing the cover, I noticed the evaporator motor blade had broken and fallen onto the coil, causing the issue. Additionally, the keypad and display are also damaged and will need to be replaced. | 2025-10-22 17:10 | crm@crystalgroup.in | YES | IN267 | 2025-10-11 |  |  |  |  | SITE |  |  | 2025-10-22 17:10 | crm@crystalgroup.in | YES | IN267 | YES |  | Stock | 2025-10-22 17:11 | crm@crystalgroup.in | YES | IN267 | COURIER | NA | NA
OCT069/25 | 2025-10-11 15:29 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | SUBBA REDDY | 8106009300 | Site in charge | BMOU9787239 | DISPLAY NOT VISIBLE |  | Subbareddy.Mandadi@apitoria.com | Vishakapatnam | Complete Breakdown | Sheet key problem with display | Call | Sitaram | 2025-10-11 15:57 | technician@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | BMOU9787239 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Visited site found, both return sensor out of calibration need to replace, user panel need to change, Sheet key need to change | Na | Display, Sheet key, User panel Return sensor 2 no's | Yes | Same above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT069%2F25 | Daikin | DAIKIN | Na | Na | Na | Refurbished | Na | SITARAM | Yes | DISPLAY NOT VISIBLE | 2025-10-22 17:15 | crm@crystalgroup.in | YES | IN268 | 2025-10-11 |  |  |  |  | SITE |  |  | 2025-10-22 17:15 | crm@crystalgroup.in | YES | IN268 | YES |  | Stock | 2025-10-22 17:16 | crm@crystalgroup.in | YES | IN268 | COURIER | NA | NA |  |  |  | 2025-11-07 09:31 | 2025-11-05 |  |  |  |  | BMOU9787239 |  |  |  | Daikin | Plus 4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B, 15.4B | 8.9A | 410v | Short | Service call | Display has been replaced, unit working fine , maintain required temperature | No | https://drive.google.com/open?id=1m_lpVIvTWrMFpp5Cr0ZVZncQc3ddyIRX | https://drive.google.com/open?id=1jkpZVMTGEytLHHTh3Y38zXl6XW-Xjd_U |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT070/25 | 2025-10-11 15:33 | crm@crystalgroup.in | Apitoria Pharma Pvt Ltd, Unit - 4U | SUBHA REDDY | 8106009300 | Site in charge | ARCU4530720 | DISPLAY NOT VISIBLE |  | NA | Vishakapatnam | Running with issues | Unit power supply, circuit breaker, input output voltage chek, sensor and contractor resistance check were all checked and found ok, unit working properly, found display blank condition need to replace | Call | Sitaram | 2025-10-11 15:43 | technician@crystalgroup.in | APITORIA | ARCU4530720 | 40FT STD RF | Na | SERVICE-AT SITE | NA | CHARGEABLE | Display not visible properly need to change | Na | Display | Yes | Display not visible | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT070%2F25 | Carrier - Thinline | CARRIER-THINLINE | 3403U01819 | JSL90656199 | Na | Used | Na | SITARAM | Yes | DISPLAY NOT VISIBLE | 2025-10-17 14:43 | crm@crystalgroup.in | YES | IN269 | 2025-10-11 |  |  |  |  | SITE |  |  | 2025-10-17 14:44 | crm@crystalgroup.in | YES | IN269 | YES |  | Stock | 2025-11-09 13:48 | service@crystalgroup.in | YES | IN269 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT070%2F25 | 2025-11-09 21:27 | 2025-11-05 |  |  |  |  | ARCU4530720 |  |  |  | Carrier | 3.0, supply 3c, return 3.2C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.2B, 16.7B | 11.4A 11.4A 11.4A | 410v | Short | Display defective | Display has been changed, unit working fine maintain required temperature | No | https://drive.google.com/open?id=1k4rNuD4NOzvSLKa5pbigYR5V8L9mAM2u | https://drive.google.com/open?id=1TLQrzoupPlu2Vr4POjhLne6U8tPgsOwg |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT071/25 | 2025-10-13 09:45 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6032622 | Sensor issue |  | Madhusoodhana.k@sailife.com | Bidar | Running with issues |  | Call | Sitaram | 2025-10-16 14:52 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6032622 | 40FT | Na | SERVICE-AT SITE | NA | NA | Door not closing | Immediate | Na | No | Door issues | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT071%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Sensor issue | 2025-10-22 15:13 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-22 15:13 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-22 15:14 | crm@crystalgroup.in | NO
OCT072/25 | 2025-10-13 10:20 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Madhusoodhan KV | 7259366532 | Executive | PCIU6034374 | DISPLAY NOT VISIBLE |  | Madhusoodhana.k@sailife.com | Bidar | Running with issues |  | Call | Sitaram | 2025-10-24 08:30 | service@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6034374 | 40FT | na | SERVICE-AT SITE | NA | NA | no issue | na | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT072%2F25 | na | DAIKIN | na | na | na | na | ns | SHAHBUDDIN | No | DISPLAY NOT VISIBLE | 2025-10-24 12:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-24 12:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-24 12:04 | crm@crystalgroup.in | NO
OCT073/25 | 2025-10-13 10:39 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | TDRU7151675 | Sensors ned to be replaced |  | gopal5.krishna@qwick.co.in | Lucknow | Running with issues |  | Call | Shubham | 2025-10-14 14:42 | technician@crystalgroup.in | Qwik Supply | TDRU7151675 | Na | Na | SERVICE-AT SITE | NA | NA | Unit running with issue, Inlet sensor , ambent sensor and return sensor out of calibration need replace. | Repair immediate | Inlet sensor 1 no's, Ambent sensor 1 no's, Return sensor 1 no's | Yes | Samme as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT073%2F25 | Na | DAIKIN | Na | Na | Nan | Na | Na | SITARAM | Yes | Sensors ned to be replaced | 2025-10-14 16:21 | crm@crystalgroup.in | YES | IN275 | 2025-10-13 | Spares | Qwik Supply | Lucknow | TDRU7151675 | SITE | FOC | DAIKIN | 2025-10-15 11:06 | crm@crystalgroup.in | YES | IN275 | YES |  | Stock | 2025-10-18 12:27 | crm@crystalgroup.in | YES | IN275 | COURIER | NA | NA |  |  |  | 2025-10-20 07:35 | 2025-10-18 |  |  |  |  | TDRU7151675 |  |  |  | Daikin | Not working | Clean | Clean |  | Okay | Clean | Okay | Need to top up |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | Not working | Na Na | Na | Not done | Breakdown | Compressor not pumping need to replace | Yes | https://drive.google.com/open?id=1BXp3z_Dc07rf5c5Cwo877dGIGPNWJSCA | https://drive.google.com/open?id=1jHSgBRoX6EnAVONtSURxtrUlH7vwyPNo |  | Na | Yes | Yes | Urgent | Same | Compressor daikin Gas 5 kg R134a Filter drier Vacuum Compressor oil 3 ltr | technician@crystalgroup.in | REEFER
OCT074/25 | 2025-10-13 10:42 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store Manager | TCLU1903088 | Need to change sensors |  | gopal5.krishna@qwick.co.in | Lucknow | Running with issues |  | Call | Shubham | 2025-10-14 14:38 | technician@crystalgroup.in | Qwik Supply | TCLU1903088 | Na | Na | SERVICE-AT SITE | NA |  | Unit running with issue, Inlet ,outlet and supply sensor out of range need to replace | Repair immediate | Inlet sensor 1 no's , Outlet sensor 1 nos, Supply sensor 1 no's | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT074%2F25 | Na | DAIKIN | Nan | Na | Na | Na | Na | SITARAM | Yes | Need to change sensors | 2025-10-14 16:25 | crm@crystalgroup.in | YES | IN276 | 2025-10-13 | Spares | Qwik Supply | Lucknow | TCLU1903088 | SITE | FOC | DAIKIN | 2025-10-18 12:28 | crm@crystalgroup.in | YES | IN276 | YES |  | Stock | 2025-10-18 12:29 | crm@crystalgroup.in | YES | IN276 | COURIER | Na | NA |  |  |  | 2025-10-20 07:39 | 2025-10-18 |  |  |  |  | TCLU1903088 |  |  |  | Daikin | -25'c, supp23.1c, return-22.4c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1B 15.7B | 8.9A 8.9a 8.9a | 410v | Not done | Sensor replace | Unit working fine, Inlet, outlet, supply sensor has been replaced | No | https://drive.google.com/open?id=1w7mUPOx-YHenuZPASyF6mL2oIdQ0N_VB | https://drive.google.com/open?id=1lrd-yfEgMxp405zkeaFw5AqrTz7KssuM |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT075/25 | 2025-10-13 10:46 | crm@crystalgroup.in | Qwik Supply | Gopal Krishna | 630 73 73 723 | Store manager | MYRU4518356 | Need to change sensors |  | gopal5.krishna@qwick.co.in | Lucknow | Running with issues |  | Call | Shubham | 2025-10-14 14:35 | sitaramsaran65@gmail.com | Qwik Supply | MYRU4518356 | Na | Na | SERVICE-AT SITE | NA | NA | Compressor contractor burnt out need to replace, phase contractor need to replace, Sheet key not working need to replace, ambent and suction SENSOR out of calibration need to replace | Unit breakdown need repair | Compressor contractor 1 no's, Phase contractor 2 no's Suction SENSOR 1 no's Ambent sensor 1 no's Sheet key 1 no's | Yes | Same as above, unit breakdown | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT075%2F25 | Na | DAIKIN | Nan | Na | Na | Na | Nan | SITARAM | Yes | Need to change sensors | 2025-10-20 10:28 | crm@crystalgroup.in | YES | IN306 | 2025-10-18 |  |  |  |  | SITE |  |  | 2025-10-20 10:29 | crm@crystalgroup.in | YES | IN306 | YES |  | Stock | 2025-10-20 10:54 | crm@crystalgroup.in | YES | IN306 | COURIER | NA | NA |  |  |  | 2025-10-20 14:03 | 2025-10-18 |  |  |  |  | MYRU4518356 |  |  |  | Daikin | +18'c supply 18.2c, return 18.0 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b 17b | 8.9a 8 9a 8 9a | 425v | Short | Repairing | Compressor contractor, phase contractor, sensors has been replaced and unit working fine | No | https://drive.google.com/open?id=1ikPQdRJ3dMCi6Sc6QnBMAgByrxPqLklZ | https://drive.google.com/open?id=1n6PFpH3Sjlkil86ZXJC_O3uzrY0KQVS0 |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT076/25 | 2025-10-13 11:09 | crm@crystalgroup.in | Qwik Supply | VEER SINGH | 9813816264 | Supervisor | TRIU6618391 | Senosor needs to be replaced |  | NA | Sonipat | Running with issues |  | Call | Shubham | 2025-10-13 11:16 | technician@crystalgroup.in | Qwik Supply | TRIU6618391 | 20FT STD RF | Na | SERVICE-AT SITE |  | FOC | I have checked and found, return sensor, condensor pressure transducer need to replace, 2kg gas top up, software configuration need | N | Return sensor 1 no's, condensor pressure transducer 1 no's, 2 kg gas R134a , software update | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT076%2F25 | Carrier - Thinline | CARRIER-THINLINE | Na | Na | Na | Used | Na | SITARAM | Yes | Senosor needs to be replaced | 2025-10-14 16:37 | crm@crystalgroup.in | YES | IN280 | 2025-10-13 | Spares | Qwik Supply Chain Pvt Ltd | Sonipat | TRIU6618391 | SITE | FOC | CARRIER-PRIMLINE | 2025-10-20 11:37 | crm@crystalgroup.in | YES | IN280, IN286 | YES |  | Stock | 2025-10-20 11:48 | crm@crystalgroup.in | YES | IN280, IN286 | COURIER | NA | NA
OCT077/25 | 2025-10-13 11:13 | crm@crystalgroup.in | Qwik Supply | VEER SINGH | 9813816264 | Supervisor | TITU9927240 | DISPLAY NOT VISIBLE |  | NA | Sonipat | Running with issues |  | Call | Shubham | 2025-10-13 11:18 | technician@crystalgroup.in | Qwik Supply | TITU9927240 | 40FT Spl RF | 2018 | SERVICE-AT SITE | NA | FOC | Display not visible properly, battery need to change | Need replenishment | Display mp4000, battery mp4000 | Yes | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT077%2F25 | Thermoking MP-4000 | TK-MP4000 | Na | Na | Na | Used | Nan | SITARAM | Yes | DISPLAY NOT VISIBLE | 2025-10-14 16:38 | crm@crystalgroup.in | YES | IN281 | 2025-10-13 | Spares | Qwik Supply | Sonipat | TITU9927240 | SITE | FOC | TK-MP4000 | 2025-10-20 11:29 | crm@crystalgroup.in | YES | IN281 | YES |  | Stock | 2025-11-13 12:10 | crm@crystalgroup.in | YES | IN281 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT077%2F25
OCT078/25 | 2025-10-13 11:21 | crm@crystalgroup.in | Qwik Supply | Surjit Singh | 9779944073 | Store manager | CICU3876631 | Battery |  | NA | Rajpura, Punjab | Running with issues |  | Call | Shubham | 2025-10-13 15:30 | technician@crystalgroup.in | Qwik Supply | CICU3876631 | 10FT STD RF | 2023 | SERVICE-AT SITE | NA | NA | Battery need to change | Nan | Better mp 4000 | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT078%2F25 | Thermoking | TK-MP4000 | 22B3319ET | ABC782800322040773 | ABC782900322060443 | Brand New | Na | SITARAM | Yes | Battery | 2025-10-14 16:31 | crm@crystalgroup.in | YES | IN277 | 2025-10-13 | Spares | Qwik Supply | RAJPURA | CICU3876631 | SITE | FOC | TK-MP4000 | 2025-10-20 11:38 | crm@crystalgroup.in | YES | IN277 | YES |  | Stock | 2025-11-09 13:42 | service@crystalgroup.in | YES | IN277 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT078%2F25 | 2025-11-12 17:55 | 2025-11-04 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40C Ret.-34.3C Sup.-40.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.7bar Discharge 14.9bar | 9.8A 9.8A 9.8A | 395V | Not done | Pm service and general inspection | Battery replaced | No | https://drive.google.com/open?id=14GhL74IL0HQ1TK2ebla19xbnzOCGzIYX | https://drive.google.com/open?id=1mb6OWjVuQG81xfrrUrP_f3oCUz7YS0Ol |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
OCT079/25 | 2025-10-13 12:18 | crm@crystalgroup.in | Lauras Labs | Somi Reddy | 9963198979 | Site in charge | CXRU1037308 | ALARM CODE VISIBLE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, E107 alarm code |  | somireddy.k@lauraslabs.com | Vizag | Running with issues |  | Email | Eric | 2025-10-14 14:52 | technician@crystalgroup.in | Lauras Labs | CXRU1037308 | Na | Nan | SERVICE-AT SITE | NA | NA | Temperature not maintain, giving alaram e107, need service engineer at site to rectify actual issue | Arranging service engineer at site |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT079%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | VIRENDRA | Yes | ALARM CODE VISIBLE, TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE, E107 alarm code | 2025-10-17 11:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 11:44 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 11:44 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-30 09:34 | 2025-10-29 |  |  |  |  | CXRU1037308 |  |  |  | Daikin | -0.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 15.2b | 8.1A 8.1A 8.1a | 430v | Short | Service call | Checked all parameters were found all ok, no alaram visible, unit working fine | No | https://drive.google.com/open?id=1Vf-jHIicrcPn9Svda4XT2uP-GeOP61LB | https://drive.google.com/open?id=1JNQ42rHG_ecacjrLYU7rcmeICQuqZS00 |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT080/25 | 2025-10-13 12:54 | crm@crystalgroup.in | TGF world | Tulasi d.Prasad | 9177500026 | Director Pharma | TITU8259378 | Evap & supply sensor, Filter drier, n2 & gas top up, compressor check | Client reported problem on 21 sep | dp.tulasi@tgfworld.com | Sikandarabad | Running with issues | As per pm via job order no.SEP032/25 | Email | Eric | 2025-10-16 14:55 | technician@crystalgroup.in | TGF world | TITU8259378 | 20FT | Na | SERVICE-AT SITE | NA | NA | Compressor noisy need to replenishment, evaporator sensor defective need to replenishment, supply sensor defective need to replenishment | Immediate | Compressor mp4000 Gas R404 - 4.5kg Oil 2kg Evaporator sensor 1 no's Supply sensor 1 no's Vacuum pump required Filter drier 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT080%2F25 | Na | TK-MP4000 | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Evap & supply sensor, Filter drier, n2 & gas top up, compressor check | 2025-10-17 14:27 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 14:27 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 14:28 | crm@crystalgroup.in | NO
OCT081/25 | 2025-10-13 13:05 | crm@crystalgroup.in | Dr.Reddy Biologics | Suresh Kasam | 9154097808 | Plant Engineer | TITU9930114 | COMPRESSOR MAKING NOISE, Gas top up |  | sureshkasam@drreddys.com | Hyderabad | Running with issues | CSM card re-registration req prior attending to the service request | Email | Pushpa | 2025-10-13 16:57 | technician@crystalgroup.in | Dr.Reddy Biologics | TITU9930114 | 40FT Spl RF -Dual Machine TK MP3000 _ Ante Room with IDU_ODU | Na | REPAIR | NA | NA | Compressor making noise Client need to replace | Y | 5 kg R134a gas, Filter drier, Vacuum, | Yes | Replacement | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT081%2F25 | Thermoking | DAIKIN | 14E219055 | EOG1000667 | Na | Na | JSGA622180063 ¦ JSGA622180011 | SHAHBUDDIN | Yes | COMPRESSOR MAKING NOISE, Gas top up | 2025-10-17 14:20 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 14:21 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 14:22 | crm@crystalgroup.in | NO
OCT082/25 | 2025-10-14 09:37 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd -Kutthur | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering | CXRU1030387 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Kutthur | Running with issues |  | Email | Eric | 2025-10-14 09:50 | technician@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd -Kutthur | CXRU1030387 | 40FT STD RF with Anteroom | Na | NA | NA | NA | Temperature not maintain due to ice frosting on floor, service engineer required at site | Technician required at site for inspection |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT082%2F25 | DAikin | DAIKIN | M001571 | K31350547926 | DECOS 3F 2668 / 1 | used | Na | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-17 14:17 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 14:19 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 14:19 | crm@crystalgroup.in | NO
OCT083/25 | 2025-10-14 09:40 | crm@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | Brahmaiah.G | 7095177094 | Asst. Manager – Engineering | MYRU4500887 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Kutthur | Running with issues |  | Email | Eric | 2025-10-14 09:47 | technician@crystalgroup.in | Hetero Plasma Sciences Pvt Ltd | MYRU4500887 | 40FT STD RF | Na | NA | NA | NA | Temperature not maintain due to ice frosting on floor , service required at side | Technician required at site |  | No | Same as above | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT083%2F25 | Daikin | DAIKIN | Na | LXE10E136A | Na | Refurbished | Na | SHAHBUDDIN | Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-10-17 12:18 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 12:19 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 12:20 | crm@crystalgroup.in | NO
OCT084/25 | 2025-10-15 15:18 | crm@crystalgroup.in | Switz International | Vilas/ Nitin Y Pagar | 98194 73839 ¦ 8511131793 | Site in charge | TITU8259465 | Complete Breakdown |  | NA | Daman | Complete Breakdown |  | Call | Sitaram | 2025-10-15 15:30 | technician@crystalgroup.in | Switz Intenational | TITU8259465 | 20FT Spl RF | 2013 | SERVICE-AT SITE | NA | NA | Technician visit and find out leakage from vapor injection valve need to replace, | Repair required | Vapor injection body valve 1 no's, Gas R404a - 4.5kg, N2 test required , Brizing work required , Filter drier 1 no's, Vacuum pump required, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT084%2F25 | Thermoking MP-4000 | TK-MP4000 | Na | Na | Na | Brand New | Na | Avinash | Yes | Complete Breakdown | 2025-10-17 12:15 | crm@crystalgroup.in | YES | IN290 | 2025-10-16 |  |  |  |  | SITE |  |  | 2025-10-20 11:49 | crm@crystalgroup.in | YES | IN290 | YES |  | Stock | 2025-10-20 11:50 | crm@crystalgroup.in | YES | IN290 | COURIER | NA | NA |  |  |  | 2025-11-05 16:03 | 2025-11-02 |  |  |  |  | TITU8259465 |  |  |  | Thermo king | -22.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2/22.3 | 11.1/10.9/11.1 | 405/405/405v | Full | Reaper | Inspection valve replace | No | https://drive.google.com/open?id=10Cd-NJw2qW1N-3I7VJdzYiycwJ1Em2NZ | https://drive.google.com/open?id=1sk3C4z2DrsG2qrdhrcTZfDuKOM4DsiSb |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT085/25 | 2025-10-16 12:24 | crm@crystalgroup.in | Instakart Services Private Limited | Rakesh Reddy | 7732088884 | SIte in Charge | APRU5093234 | Wiring issue |  | NA | JNPT | Running with issues |  | Call | Sitaram | 2025-10-16 13:09 | crm@crystalgroup.in | Instakart Services Private Limited | APRU5093234 | 40FT | Carrier | REFURBISHMENT OF CONTAINER | LEASE |  | LED Light, Strip Curtains, crystalSMART | LED Light, Strip Curtains, crystalSMART |  | Yes | Additional accessories required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT085%2F25 | NO: THAKUR; No: No | Wiring issue | 2025-10-16 13:53 | crm@crystalgroup.in | YES | 292 | 2025-10-16 |  |  |  |  | DEPOT |  |  | 2025-10-16 14:27 | crm@crystalgroup.in | YES | 292 | YES |  | Stock | 2025-10-16 14:33 | crm@crystalgroup.in | YES | 292 | ARRENGING AT SITE | [5 empty] | 2025-10-16 13:27 | [11 empty] | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean | [12 empty] | No |  |  |  |  | technician@crystalgroup.in | REEFER
OCT086/25 | 2025-10-16 14:21 | crm@crystalgroup.in | Kirloskar Corrocoat | Shailendra Patil | 9881230615 | Site in charge | MYRU4515260 | ALARM CODE VISIBLE |  | NA | Ghatampur | Running with issues |  | Call | Sitaram | 2025-10-16 18:24 | technician@crystalgroup.in | Kirloskar | MYRU4515260 | 40FT STD RF | Nan | SERVICE-ON CALL | NA | NA | Evp Motor need to replace | Immediate | Evaporator motor 1 no's decos III D model | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT086%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | Na | Avinash | Yes | ALARM CODE VISIBLE | 2025-10-17 13:03 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-17 13:04 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-17 13:05 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-17 13:57 | 2025-10-15 |  |  |  |  | MYRU4515260 |  |  |  | Daikin | 12.0c | Clean | Clean |  | Okay | Clean | Need to replace | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | Na | Na | Not done | Evaporator motor getting heat, bypas with Local electrician now unit working fine with singal motor | Na | Yes | https://drive.google.com/open?id=1u6sq8pmoIVBtj9LvaAFdfTf9KsniMOR7 | https://drive.google.com/open?id=1yQ14Kz5IMeWVX681Z6VYORV0mutiZ3MI |  | Na | Yes | Yes | Urgent | Yas | Evaporator motor old model | technician@crystalgroup.in | REEFER
OCT087/25 | 2025-10-16 15:58 | crm@crystalgroup.in | Quick supply chain PVT LTD | Prasant | 9817930289 | Site in charge | CICU3876605 | Controller hang |  | NA | Lucknow | Complete Breakdown |  | Call | Sitaram | 2025-10-16 16:05 | technician@crystalgroup.in | Quick supply | CICU3876605 | 10FT STD RF | 2023 | SERVICE-AT SITE | NA | NA | Controller hang after 5,6 hours need to replenishment, power modul also suspected, battery need to replace | Immediate | Controller mp 4000, Power module mp 4000, Battery mp4000 | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT087%2F25 | Thermoking | TK-MP4000 | E0GM031489 | 0422GM031489 | ABC782800322110158 | Brand New | Na | SITARAM | Yes | Controller hang | 2025-10-16 16:23 | crm@crystalgroup.in | YES | IN302 | 2025-10-16 |  | Lauras unit 2 |  | PGRU4958724 | SITE |  |  | 2025-10-20 11:51 | crm@crystalgroup.in | YES | IN302 | YES |  | Stock | 2025-10-20 11:52 | crm@crystalgroup.in | YES | IN302 | COURIER | NA | NA |  |  |  | 2025-11-07 18:27 | 07/11/0025 |  |  |  |  | CICU3876605 |  |  |  | Thermo king | -40C Ret.-40.1C Sup.-43.2C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.5bar Discharge 13.3bar | R 8.7A B 8.6A Y 8.5A | 404V 404V 404V | Full | Pm service and general inspection | After observation of 36 hours, unit working fine , controller has been changed, unit maintain -40'c . Full PTI has been passed | No | https://drive.google.com/open?id=10wxlr0Hd7fAx6uwyCyOY9Tu0C2XPjVgW | https://drive.google.com/open?id=1upAiVN2YZF-A5_obE01SCpRMPi4teYm4 |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
OCT088/25 | 2025-10-16 16:58 | crm@crystalgroup.in | PI Industries Limited | Mahendra Dhatarwal | 9919910763 | Site in Charge | MYRU4502299 |  |  | mahendra.dhatarwal@piind.com | Panoli | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-17 14:50 | 2025-10-17 |  |  |  |  | MYRU4502299 |  |  |  | Daikin | -4.0'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b 14.4b | 8.8a 8.8a 8.8a | 410v | Not done | Unit working fine | Pm | No | https://drive.google.com/open?id=1YYpaUfpq8G7YnnASf_NnXspArSGWqmO1 | https://drive.google.com/open?id=1G0Xtn5C-RS2R3eH2NTpNu1NFuxyF3e2r |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT089/25 | 2025-10-16 17:01 | crm@crystalgroup.in | Qwik Supply | Mohit | 9023419864 | Site in Charge | TDRU5815332 |  |  | mohit2.rai@qwik.co.in | Ahmedabad | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-22 08:27 | 2025-10-18 |  |  |  |  | TDRU5815332 |  |  |  | Carrier | -21.0c sup.-22.0 ret.-18.3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8b /12.3b | 12.7/11.9/12.7 | 402/401/402v | Not done | Pm service | Unit working good condition | No | https://drive.google.com/open?id=1xe9-myYQcjTI1jOPgTgAZUMfOVE5ldsd | https://drive.google.com/open?id=1mR-3yKbQT4OUk1cm_u9C5EzLHilK-LIJ |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT090/25 | 2025-10-16 17:02 | crm@crystalgroup.in | Qwik Supply | Mohit | 9023419864 | Site in Charge | CICU2779935 |  |  | mohit2.rai@qwik.co.in | Ahmedabad | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-22 08:11 | 2025-10-18 |  |  |  |  | CICU2779935 |  |  |  | Thermo king | -40.0c, ret-39 sup._41c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b /18.5b | 8.9/8.9/8.9A | 410/410/410 v | Not done | Pm service | Unit working gud condition | No | https://drive.google.com/open?id=14uTcJuKWoNllr73OT1Nnwrl0DBv0q1ii | https://drive.google.com/open?id=1maBndSXwBwPVTCYgydB_l7rzZL0BayEt |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT091/25 | 2025-10-16 17:04 | crm@crystalgroup.in | Qwik Supply | Mohit | 9023419864 | Site in Charge | CICU2779909 |  |  | mohit2.rai@qwik.co.in | Ahmedabad | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-22 08:19 | 2025-10-18 |  |  |  |  | CICU2779909 |  |  |  | Thermo king | -40.0c ret.-30.0c sup.-40.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suc 0.9b/19.0b | 10.0/10.1/10.0A | 402/401/402 | Not done | Pm service | Unit working good condition | No | https://drive.google.com/open?id=1IAYl4iJpLDDTzMpZt2yt4zKG7TkIO7P8 | https://drive.google.com/open?id=1yiNhTVXJKm859w2Hqx-__51Ey79nwXop |  | 123 | No | No | Can be done on next PM | Ns | Na | technician@crystalgroup.in | REEFER
OCT092/25 | 2025-10-16 17:07 | crm@crystalgroup.in | Qwik Supply | Atul Verma | 9274394889 | Site in Chrage | APRU5066497 |  |  | Atul.varma@qwik.co.in | Surat | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-17 14:53 | 2025-10-16 |  |  |  |  | APRU5066497 |  |  |  | Carrier | -16'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1b 11b | 8.4 8.4 8.4 | 420v | Not done | Pm | Unit working fine | No | https://drive.google.com/open?id=1Gn1J36EFo8b_n09vZFUwetS2HFXkbpCa | https://drive.google.com/open?id=1936LlAgCQpuxSteEzYo1GM0oWKo5ScoA |  | Na | Yes | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT093/25 | 2025-10-16 17:12 | crm@crystalgroup.in | Qwik Supply | Atul varma | 927439889 | SIte in Charge | GESU9454950 |  |  | Atul.varma | Surat | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-17 15:12 | 2025-10-16 |  |  |  |  | GESU9454950 |  |  |  | Carrier | -22 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5b 14 4b | 11.9a 11.9a 11.9a | 415v | Not done | Pm | Unit working fine | No | https://drive.google.com/open?id=1jy5d8V3EWfDmlRbdJ84-mxvRqBgsJs7z | https://drive.google.com/open?id=1mKxq0ukl1AQYm84ztvxOfAP_QRnYELaJ |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT094/25 | 2025-10-16 17:14 | crm@crystalgroup.in | RELIANCE | J.Anbu Ezhilan | 9004071567 | Site in Charge | CGMU2991679 |  |  | anbu.EZHILAN@ril.com | jamnagar | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-25 21:21 | 2025-10-25 |  |  |  |  | CGMU2991679 |  |  |  | Carrier | +7.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.9/13.9 | 11.9/12.1./11.9 | 402/402/402 | Not done | Pm | Keypad df. Unit working good condition | Yes | https://drive.google.com/open?id=1lyASqYg6x5zgerl2vmmJUg4x37aZHlys | https://drive.google.com/open?id=1_G_S6GunHUE46EuroRykJnm_sDD857cd |  | 123 | No | No | Can be done on next PM | Na | Keypad carrier (thinline) | technician@crystalgroup.in | REEFER
OCT095/25 | 2025-10-16 17:16 | crm@crystalgroup.in | RELIANCE | J.Anbu Ezhilan | 9004071567 | Site in Charge | CCLU1031918 |  |  | anbu.EZHILAN@ril.com | Jamnagar | Complete Breakdown |  | Email | NA | 2025-10-22 08:25 | technician@crystalgroup.in | RELIANCE | CCLU1031918 | 20FT | 2009 | SERVICE-AT SITE | NA | NA | Pm | Pm | Na | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT095%2F25 | Pm | CARRIER-THINLINE | Na | Na | Na | Na | Na | A | No | Preventive Maintenance | 2025-10-24 12:02 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-24 12:02 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-24 12:03 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-30 08:32 | 2025-10-29 |  |  |  |  | CCLU1031918 |  |  |  | Daikin | -0.5 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.3B 17B | 8.1a 8.1a 8.1a | 420v | Short | Service call | Checked properly unit working fine now alaram visible. Working in good condition | No | https://drive.google.com/open?id=1YrwyQw7coRd71dV5Lv9KMwkic9dR0b0h | https://drive.google.com/open?id=1Y83EWyMboGJP_kxJ7kDMxokkRg1OAedz |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT096/25 | 2025-10-16 17:18 | crm@crystalgroup.in | RELIANCE | J.Anbu Ezhilan | 9004071567 | Site in Charge | TRIU6618663 |  |  | anbu.EZHILAN@ril.com | Jamnagar | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-25 17:43 | 2025-10-25 |  |  |  |  | TRIU6618663 |  |  |  | Carrier | +7.0c /sup.+5.7/ ret.+7.2 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2/16.4 | 17.2/16.0/17.2 | 415/415/415 | Not done | Pm | Good condition | No | https://drive.google.com/open?id=1Fu38R0bZ_9cbeY_vUjI7kaqaL5nCv6n6 | https://drive.google.com/open?id=1ZPnMmI69nVB2QdsihBrBl197UfFK1Hl6 |  | 123 | No | No | Can be done on next PM | 0 | 0 | technician@crystalgroup.in | REEFER
OCT097/25 | 2025-10-16 17:20 | crm@crystalgroup.in | Switz International | Vilas | 9819473839 | Site in Chrage | TITU8259465 |  |  | vilasp@india.switzgroup.com | Daman | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-17 15:17 | 2025-10-16 |  |  |  |  | TITU8259465 |  |  |  | Thermo king | Not working | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Need to top up |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Need to replace |  | Na | Na | 420v | Not done | Breakdown | Leakage from vapour injection valve need to replace body valve, | Yes | https://drive.google.com/open?id=1eLUwuVsMmX66WXirqahbPyYKa5dAV1Mo | https://drive.google.com/open?id=1CcORtSRZ119DCAv61KxWLl_5s_2-KrNQ |  | 123 | Yes | Yes | Urgent | Same | Vapouriser injection valve Gas R404a 4.5 kg Filter drier Brizing set N2 test Vacuum pump | technician@crystalgroup.in | REEFER
OCT098/25 | 2025-10-16 17:23 | crm@crystalgroup.in | Kirloskar Corrocoat | Shailendra Patil | 9881230615 | Site in Charge | ARCU4530799 |  |  | shailendra.patil.kicopl.com | Jamnagar | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-31 09:11 | 2025-10-29 |  |  |  |  | ARCU4530799 |  |  |  | Carrier | 13 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.1/13.7 | 11.8/12.1/11.9 | 411/411/411 | Not done | Technician | Keypad df. | Yes | https://drive.google.com/open?id=1SyMBmWx8136ldBLoHRU7bG0Iq-wHg86G | https://drive.google.com/open?id=1aXSEuri7qC6dvnZCwqXvewUEwoTP9pgk |  | 123 | No | No | Can be done on next PM | Na | Keypad | technician@crystalgroup.in | REEFER
OCT099/25 | 2025-10-16 17:25 | crm@crystalgroup.in | NFASL | Nilesh Patel | 9726578780 | Site in Charge | CCLU1031878 |  |  | nilesh.patil@nfil.in | Dahej | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-31 09:29 | 2025-10-30 |  |  |  |  | CCLU1031878 |  |  |  | Carrier | +15.0 sup+15.1 ret.+16.4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9/10.7 | 13.0/13.3/13.8 | 415/415/415v | Short | Technician | Service | No | https://drive.google.com/open?id=1XEVYjsOxqafrClgqYp11A0BnfFlELhnN | https://drive.google.com/open?id=12hKhGf1uMZekDxDDjYcRPnLAobq-oKbg |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT100/25 | 2025-10-16 17:27 | crm@crystalgroup.in | PI Industries Limited | Ravi Mishra | 6357242039 | Site in Charge | CXRU1035856 |  |  | ravi.mishra@piind.com | Panoli | Preventive Maintenance |  | Email | NA
OCT101/25 | 2025-10-16 17:29 | crm@crystalgroup.in | DHL Supply Chain pvt Ltd | Shailesh Patil | 9909986653 | Site in Charge | TCLU1912270 |  |  | niranjan.kanthe@dhl.com | Sanad | Preventive Maintenance |  | Email | NA | [54 empty] | 2025-10-22 08:35 | 2025-10-18 |  |  |  |  | TCLU1912270 |  |  |  | Daikin | +4.0c sup.4.5 ret5.1c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 100/1000 | 11.9/11.9/11.9 | 406/407/406 | Not done | Pm service | Unit working good condition | No | https://drive.google.com/open?id=1HtoeAQxe3n5P31MeWfJUfsXmUVqFAzBl | https://drive.google.com/open?id=19mzsnAvT5245oTh98hY8rVZhT63kHAfZ |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT103/25 | 2025-10-17 15:51 | crm@crystalgroup.in | Kirloskar | Shailendra Patil | 9881230615 | Site in charge | MYRU4515260 | Evaporator motor defective |  | Na | Dhanbad | Running with issues |  | Call | Sitaram | 2025-10-17 15:54 | technician@crystalgroup.in | Kirloskar | MYRU4515260 | 40FT STD RF | 2012 | SERVICE-ON CALL | NA | NA | Motor getting heat. Evaporator motor defective need to change | Immediate | Evaporator motor old model type 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT103%2F25 | Daikin | DAIKIN | M0001112 | LXECOE136A2 | 24C2 | Used | Na | Avinash | Yes | Evaporator motor defective | 2025-10-22 17:21 | crm@crystalgroup.in | YES | IN305 | 2025-10-18 |  |  |  |  | SITE |  |  | 2025-10-22 17:23 | crm@crystalgroup.in | YES | IN305 | YES |  | Stock | 2025-10-22 17:25 | crm@crystalgroup.in | YES | IN305 | COURIER | NA | NA
OCT104/25 | 2025-10-18 11:14 | crm@crystalgroup.in | Qwik Supply | Karthikeyan, Dhanasekaran | 9715393950, 6374711250 | Site technician | MYRU4519753 | Machine isnt switching on |  | kathikeyan7.m@ril.com, dhanasekaran.subramaniam@ril.com | Chennai | Running with issues |  | Call | Pushpa | 2025-10-23 15:25 | service@crystalgroup.in | Qwik Supply | MYRU4519753 | 40FT | 2012 | SERVICE-ON CALL | NA | NA | Controller configuration | On call resolved | Na | No | Controller configuration required | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT104%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Na | No | Machine isnt switching on | 2025-10-23 15:27 | technician@crystalgroup.in | NO | [9 empty] | 2025-10-23 15:28 | technician@crystalgroup.in | NO |  |  |  |  | 2025-10-23 15:28 | technician@crystalgroup.in | NO | [7 empty] | 2025-11-09 21:14 | 2025-11-09 |  |  |  |  | MYRU4519753 |  |  |  | Daikin | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | Na | Na | Not done | On call with clint unit not getting on | After video call controller configuration done, unit working fine nd maintain temperature | No | https://drive.google.com/open?id=1Y1iapOO0i_ue9z0QrtK0JxxC4PNT3nGZ | https://drive.google.com/open?id=1cEkbYIMOLirpWqf-n5XhO8CFY5nWnS2v |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT105/25 | 2025-10-18 15:46 | crm@crystalgroup.in | Quick supply | Upainder yadav | 9838271843 | Site in charge | TDRU7151675 | Compressor not pumping |  | NA | Lucknow | Complete Breakdown |  | Call | Sitaram | 2025-10-18 15:51 | technician@crystalgroup.in | Quick supply | TDRU7151675 | 40FT Spl RF | Compressor not working, unit breakdown | SERVICE-AT SITE | NA | NA | Compressor need to replace | Immediate | Compressor daikin 1 no's, Compressor oil 3 ltr, Filter drier 1 no's, R134a gas 5 kg, Vacuum pump | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT105%2F25 | Daikin | DAIKIN | Na | Na | Na | Na | JSGA622180053 | SITARAM | Yes | Compressor internally damage not pumping need to replace | 2025-10-24 11:21 | crm@crystalgroup.in | YES | IN313 | 2025-10-22 |  |  |  |  | SITE |  |  | 2025-11-07 11:27 | crm@crystalgroup.in | YES | IN313 | YES |  | Stock | 2025-11-07 11:29 | crm@crystalgroup.in | YES | IN313 | COURIER | 53610980824 | Blue dart |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT105%2F25 | 2025-11-09 19:06 | 2025-11-09 |  |  |  |  | TDRU7151675 |  |  |  | Daikin | +18C Sup.+18.6C Ret.+19.5C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 68LPT Discharge 1532HPT | 14.7A 10.6A | 445V | Short | Pm service and general inspection | After observation of 36 hours, unit working fine , compressor, filter drier, Return sensor, inlet sensor and outlet sensor has been changed, unit maintain +18’C . Short PTI has been passed | No | https://drive.google.com/open?id=1M2PSDZrFMjVYks8DaSlsj8sHsZOL-y9A | https://drive.google.com/open?id=1GNsJ7Fuv9AFqBfeF2vmUnB3kf33RXsSO |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
OCT106/25 | 2025-10-20 14:35 | crm@crystalgroup.in | Devyani Food Industries Ltd | Ravi Kumar Singh | 9088047482 | NA | KKFU6712675 | MOTOR MAKING NOISE |  | ravikumar.singh@creambell.com | Burdhman | Running with issues | NEED TO REPLACE | Call | PUSHPA MAM | 2025-11-05 15:06 | service@crystalgroup.in | Devyani Food Industries Ltd | KKFU6712675 | NA | NA | SERVICE-ON CALL | NA | NA | RUNNING WITH ISSUE SOME SENSOR AND MOTOR NEED TO REPLACE | NEED REPAIR | DISCHARGE VALVE AND SUCTION VALVE 1 NOS, KING VALVE 1 NOS, COMPRESSOR HEAD CENTER AND SIDE GAS KIT, VALVE PLATE GAS KIT, CONTRACTOR 30A AND 12A 1 NOS, EVP MOTOR SINGL PHASEAĀ | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT106%2F25 | NA | CARRIER-THINLINE | NA | NA | NA | NA | NA | NA | No | MOTOR MAKING NOISE | 2025-11-10 10:58 | crm@crystalgroup.in | YES | IN308 | 2025-10-20 |  |  |  |  | SITE |  |  | 2025-11-10 10:59 | crm@crystalgroup.in | YES | IN308 | YES |  | Stock
OCT107/25 | 2025-10-20 14:39 | crm@crystalgroup.in | Adhya Dairy-ITC | Raja Bhunia | 9230676077 | Site in charge | BMOU9729398 | DISPLAY NOT VISIBLE |  | NA | Kolkata | Running with issues |  | Email | Pushpa | 2025-10-22 08:18 | technician@crystalgroup.in | Adhya Dairy-ITC | BMOU9729398 | 40FT | 2012 | SERVICE-AT SITE | NA | NA | Display not visible properly and sheet key not working need to replace | Repair needed | Display 1 no's, Sheet key 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT107%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Other | Yes | DISPLAY NOT VISIBLE | 2025-10-24 12:11 | crm@crystalgroup.in | YES | IN312 | 2025-10-22 |  |  |  |  | SITE |  |  | 2025-11-13 11:08 | crm@crystalgroup.in | YES | IN312 | YES |  | Stock | 2025-11-13 11:09 | crm@crystalgroup.in | YES | IN312 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT107%2F25 | 2025-11-14 08:17 | 2025-11-12 |  |  |  |  | BMOU9729398 |  |  |  | Daikin | +4'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.8B, 14.9B | 8.2A | 403V | Short | Controller defative | After replacing controller unit working fine | No | https://drive.google.com/open?id=16RMlVc8_lRw4yzhzRs9MmITWporRjfhf | https://drive.google.com/open?id=1LXTmCSyqt8RzAuEvsd2RngIPehCbqF-F |  | 130 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT108/25 | 2025-10-20 14:40 | crm@crystalgroup.in | Adhya Dairy-ITC | Raja Bhunia | 9230676077 | Site in Charge | CXRU1033719 | Return sensor issue |  | NA | Kolkata | Running with issues |  | Email | Pushpa | 2025-10-22 08:16 | technician@crystalgroup.in | Adhya Dairy-ITC | CXRU1033719 | 40FT | Daikin | SERVICE-AT SITE | NA | FOC | Return sensor need to replace | Repair needed | Rerun sensor 1 no's | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT108%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | Other | Yes | Return sensor issue | 2025-10-24 12:08 | crm@crystalgroup.in | YES | IN311 | 2025-10-22 |  |  |  |  | SITE |  |  | 2025-11-13 11:11 | crm@crystalgroup.in | YES | IN311 | YES |  | Stock | 2025-11-13 11:12 | crm@crystalgroup.in | YES | IN311 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT108%2F25 | 2025-11-14 08:14 | 2025-11-12 |  |  |  |  | CXRU1033719 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B, 16.4B | 7.2A 7.2A 7.2A | 404v | Short | Giving supply sensor alaram | After change supply sensor wiring, unit working fine as per setpoint | No | https://drive.google.com/open?id=1WL_wknuNs3eSwg6xgeBs_gleFLgPC-jA | https://drive.google.com/open?id=1hfwBlIgE040sMO7yq3IYvfAik2a23SDf |  | 130 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT109/25 | 2025-10-20 14:43 | crm@crystalgroup.in | Adhya Dairy-ITC | Raja Bhunia | 9230676077 | Site in charge | KKFU5706142 | Supply sensor issue |  | NA | Kolkata | Running with issues |  | Email | Pushpa | 2025-10-22 08:14 | service@crystalgroup.in | Adhya Dairy-ITC | KKFU5706142 | 40RF | Carrier | SERVICE-AT SITE | NA | NA | supply sensor and defrost sensor need to replace | need repair | supply sensor 2 nos , defrost sensor 1 nos | Yes | same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT109%2F25 | na | CARRIER-THINLINE | na |  |  | na | na | other | Yes | Supply sensor issue | 2025-10-24 23:08 | crm@crystalgroup.in | YES | IN317 | 2025-10-24 |  | Adhya Dairy-ITC |  | KKFU5706142 | SITE |  |  | 2025-10-24 23:18 | crm@crystalgroup.in | YES | IN317 | YES |  | Stock | 2025-11-13 11:13 | crm@crystalgroup.in | YES | IN317 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT109%2F25
OCT110/25 | 2025-10-22 09:09 | crm@crystalgroup.in | Qwik SUpply Chain | Atul Varma | 9273494889 | Site in charge | APRU5066497 | Complete Breakdown |  | Atul.varma@qwik.co.in | Surat | Complete Breakdown |  | Call | SItaram | 2025-10-22 09:34 | technician@crystalgroup.in | Qwik Supply | APRU5066497 | 40FT STD RF | 2011 | SERVICE-ON CALL | NA | NA | Compressor need to replace | Immediate repair | Compressor thin line 1 no's Oil 3.5 ltr, Gas 5kg R134a, Gas kit suction 1 no's Gas kit discharge 1 no's Filter drier 1 no's Compressor terminal kit 1 no's, Compressor contractor 30A 1 no's, | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT110%2F25 | Carrier - Thinline | CARRIER-THINLINE | Na | Na | Na | Na | JSGA623040296 | Avinash | Yes | Compressor ground need to replace | 2025-10-24 11:18 | crm@crystalgroup.in | YES | IN314 | 2025-10-22 |  |  |  |  | SITE |  |  | 2025-11-03 21:21 | crm@crystalgroup.in | YES | IN314 | YES |  | Stock | 2025-11-03 21:22 | crm@crystalgroup.in | YES | IN314 | TECHNICIAN |  |  | Avinash |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT110%2F25 | 2025-11-04 09:45 | 2025-11-03 |  |  |  |  | APRU5066497 |  |  |  | Carrier | -21.0c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 1.2/16.9 | 13.7/14.3/13.7 | 401/401/401v | Short | Reaper | Compressor replace | No | https://drive.google.com/open?id=1IyKdt39IBezo0PkGduaO2gBOC7aCI5c2 | https://drive.google.com/open?id=1Pi9ZIAWm0pokQ50Xf-Pd6iCz_VkDpkQi |  | 123 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT111/25 | 2025-10-22 09:28 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | PCIU6008328 | DOOR NOT CLOSING |  | NA | Bidar | Running with issues |  | Call | Shabuddin | 2025-10-23 17:55 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6008328 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Door issues | Na | Na | No | Repaired | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT111%2F25 | Daikin | CARRIER-THINLINE | NA | NA | NA | used | JSGA622340291 | SHAHBUDDIN | No | Door issues | 2025-10-24 11:51 | crm@crystalgroup.in | NO | [9 empty] | 2025-10-24 11:51 | crm@crystalgroup.in | NO |  |  |  |  | 2025-10-24 11:51 | crm@crystalgroup.in | NO | [7 empty] | 2025-10-24 19:31 | 19/10/0025 |  |  |  |  | PCIU6008328 |  |  |  | Daikin | +5 c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/200 psig | 12.9/12.8/12.8 | 405/406/405 | Short | Door issue damaged & closing issue/ instalation process/ user training | Damaged door repaired and door allinement and all door service with greaceing. Instalation completed with all electrical wiring connections completed. User TRANNING DONE. Door open close training done Handed over to Eng team.and project team.Mr. Naveed | No | https://drive.google.com/open?id=1gOM-FNYdG2OhJmEp4n1UA-Aa7lA8xLTW | https://drive.google.com/open?id=14Pa2AvODcERqDYuCK_NUMrXzHzO8dzn6 |  | 124 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT112/25 | 2025-10-22 09:30 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | CRLU3604920 | AMC |  | NA | Bidar | AMC |  | Call | Shabuddin | 2025-11-09 12:31 | service@crystalgroup.in | Sai Life Science Pvt Ltd | CRLU3604920 |  | na | SERVICE-AT SITE | NA | NA | supply sensor need to chnge | ys | supply sensor 2 nos | Yes | need to change | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT112%2F25 | NA: DAIKIN; NO: AVINASH; No: Yes | AMC | [29 empty] | 2025-10-23 11:27 | 21/10/0025 |  |  |  |  | CRLU3604920 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/200 psig | 10.2/10.1/10.2 | 412/413/412 | Short | AMC - Unit for pm service. | In AMC pm service completed with checked unit operation And found.. Display letters cut & Eos reading abnormal temp. Checked unit other operation And found working as satisfactory . Display replaced- spare taken our spare unit in sai lab. | Yes | https://drive.google.com/open?id=1TtOkjIoW3qD3_oHa7gJ_1uUiqnZTS2uY | https://drive.google.com/open?id=1wcRa9noH5QkwgaBYh4R1YZZtIu_JBfGh |  | 124 | No | No | Can be done on next PM | Na | Temp. Sensor daikin nos.2 | technician@crystalgroup.in | REEFER
OCT113/25 | 2025-10-22 09:36 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | MYRU4507120 | AMC |  | NA | Bidar | AMC |  | Call | Shabuddin | [54 empty] | 2025-10-23 11:21 | 20/10/0025 |  |  |  |  | MYRU4507120 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/205 psig | 10.2/10.3/10.3 | 412/413/413 | Short | AMC Unit for pm service. R/H Evaprator motor stkup. | AMC unit pm service completed with checked unit operation And found working as satisfactory. Need to replaced Evaprator motor right side. Temperley unit working with one motor. | Yes | https://drive.google.com/open?id=1speWxJwK1dr455w5BH71iG_4y3I3GkTF | https://drive.google.com/open?id=1JDxnMMCBOXkM3jvBcU9HGXuS4bnRcfw3 |  | 124-bidar | No | No | Can be done on next PM | Evp. Motor | Evaprator motor single phase with complit bracket | technician@crystalgroup.in | REEFER
OCT114/25 | 2025-10-22 09:38 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | MYRU4518042 | AMC |  | NA | Bidar | AMC |  | Call | Shabuddin | [54 empty] | 2025-10-23 11:00 | 20/10/0025 |  |  |  |  | MYRU4518042 |  |  |  | Daikin | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/197 psig | 10.4/10.3/10.3 | 412/413/412 | Short | For AMC unit pm service | In Amc unit pm service completed with checked unit operation And found working as satisfactory. | No | https://drive.google.com/open?id=1pmn0CufPl0_lezC8Kiw1az3jmZqVhfAV | https://drive.google.com/open?id=1GLlsEa6NCg9WCZmRCpRLH-79U5jSm4Xq |  | 124 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT115/25 | 2025-10-22 09:43 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | NYKU7931149 | AMC |  | NA | Bidar | AMC |  | Call | Shabuddin | [54 empty] | 2025-10-23 10:55 | 20/10/0025 |  |  |  |  | NYKU7931149 |  |  |  | Carrier | +5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 8/210 psig | 12.8/12.7/12.7 | 412/413/413 | Short | AMC UNIT FOR PM SERVICE . | Pm service completed with checked unit operation And found Al 54 . Checked other unit operationAnd found working as satisfactory. For Alaram 54 need to replaced supply data & controller senser. | Yes | https://drive.google.com/open?id=1G1yUC9AHJAJYb7oNoDoGi23IGI0-sdqa | https://drive.google.com/open?id=19DUp3GO927O8q1XFdOxZnC-YczQ9ku3n |  | 124-bidar | No | No | Can be done on next PM | Na | Supply sensor carrier nos.2 | technician@crystalgroup.in | REEFER
OCT116/25 | 2025-10-22 09:45 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | GESU9460634 |  |  | NA | Bidar | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-23 10:48 | 21/10/0025 |  |  |  |  | GESU9460634 |  |  |  | Carrier | +3.6c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/215 psig | 12.3/12.4/12.3 | 412/413/412 | Short | Unit for pm service with Dal 87 | Pm service completed with checked unit operation And found working as normal.. For dal 87 need to replaced ML3 Controller - Elite Line unit | Yes | https://drive.google.com/open?id=1Qrzi6OkCpFd0WeC6qx_m6yhj9bh_DDP7 | https://drive.google.com/open?id=1_8kOO70V-55DntwZg4nHhaFj28Oeb5Dp |  | 124-bidar | No | No | Can be done on next PM | Next | ML- 3 controller with elite line scroll comp. Software | technician@crystalgroup.in | REEFER
OCT117/25 | 2025-10-22 09:46 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | TITU9930032 |  |  | NA | Bidar | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-23 10:40 | 22/10/0025 |  |  |  |  | TITU9930032 |  |  |  | Thermo king | +3.1c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/210 psig | 13.1/13.2/13.1 | 413/413/414 | Short | Unit pm due | Pm service completed with checked unit operation And found working as satisfactory. | No | https://drive.google.com/open?id=1VQsljLEZ1QO3kATZe3ekd4QoFpSjwOf1 | https://drive.google.com/open?id=1qJ-HVXxHWLh68C5-VlKcIfcVMD-GVFHn |  | 124-bidar | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT118/25 | 2025-10-22 09:48 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | PCIU6034374 |  |  | NA | Bidar | Preventive Maintenance |  | Call | Shabuddin | [54 empty] | 2025-10-23 10:35 | 22/10/0025 |  |  |  |  | PCIU6034374 |  |  |  | Daikin | +22c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 7/190 psig | 10/9.9/9.9 | 413/412/412 | Short | Pm due | Pm service completed with checked unit operation And found working as satisfactory. | No | https://drive.google.com/open?id=1Gh1oWbO1pgeCmPdNlS2fRaTmpXg34oGE | https://drive.google.com/open?id=1S2Ev6hyGXcQ3djaGYiCO5A8W5NkuayEe |  | 124- bidar | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT119/25 | 2025-10-22 09:50 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | SIte in charge | PCIU6032622 | Running with issue |  | NA | Bidar | Running with issues |  | Call | Shabuddin | 2025-10-23 17:53 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6032622 | 40FT | Na | SERVICE-AT SITE | NA | NA | Door issues, display dmg | Immediate repair | Display 1 no's | Yes | Need to replace display | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT119%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Running with issue | [29 empty] | 2025-10-23 10:15 | 18/10/0025 |  |  |  |  | PCIU6032622 |  |  |  | Daikin | +20c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/210 psig | 11.2/11.3/11.2 | 413/412/412 | Short | DOOR ISSUE & PM DUE WITH DISPLAY COVER SHEET KEY DMG | Door issue is resolved with using site crane and given bottom packing. Pm service completed with replaced damaged display. Checked unit operation & found working as normal with maintain set temp.and no alarm . | No | https://drive.google.com/open?id=1xdjXAeOrHHaHIVrfI8fY3lAAkNuZuBNx | https://drive.google.com/open?id=1M7whcpu9Apw7iLAB4eDJ9E7vjP_aCINM |  | 124 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT120/25 | 2025-10-22 09:51 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | PCIU6031328 |  |  | NA | Bidar | Preventive Maintenance |  | Call | Shabuddin | 2025-11-09 12:29 | service@crystalgroup.in | Sai Life Science Pvt Ltd | PCIU6031328 | 40FT | na | SERVICE-AT SITE | NA | NA | na | pm |  | No | pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT120%2F25 | NA: DAIKIN; NO: SHAHBUDDIN; No: No | Preventive Maintenance
OCT121/25 | 2025-10-22 09:53 | crm@crystalgroup.in | Sai Life Science Pvt Ltd | Mohammad Naved Ahmed | 8892037752 | Site in charge | HDMU5542114 | Running with issue |  | NA | Bidar | Running with issues |  | Call | Shabuddin | 2025-10-23 17:50 | technician@crystalgroup.in | Sai Life Science Pvt Ltd | HDMU5542114 | 40FT | 2011 | SERVICE-AT SITE | NA | NA | Display defective, Heter contractor defective | Immediate repair | Heter contractor 12A, display | Yes | Running with issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT121%2F25 | Na | CARRIER-THINLINE | Na | Na | Na | Na | Na | SHAHBUDDIN | Yes | Running with issue | 2025-11-04 12:04 | crm@crystalgroup.in | YES | IN319 | 2025-10-24 |  |  |  |  | SITE |  |  | 2025-11-04 12:17 | crm@crystalgroup.in | YES | IN319 | YES |  | Stock | [10 empty] | 2025-10-23 11:42 | 18/10/0025 |  |  |  |  | HDMU5542114 |  |  |  | Carrier | 3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/220 psig | 12.3/12.4/12.3 | 412/413/412 | Short | Unit for pm service Display daded. Heater contactor 12A burnt | * Replaced Faded Display. * Replaced Hter contactor 12A All material taken with me from Depo Pm service complited with clean condendenser coil & unit. Run unit checked operation and found working as normal. | No | https://drive.google.com/open?id=16kiQ7yGIaHF7MwmX8UzAex39jedHhpZM | https://drive.google.com/open?id=1QY5NaVn0tkL8XlJybCrfNU-KP3S4IBdY |  | 124-bidar | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT122/25 | 2025-10-22 14:24 | crm@crystalgroup.in | Qwik Supply | Lalit Saini | 9928034131 | Site in charge | TRIU6680335 | COMPRESSOR MAKING NOISE |  | NA | Jaipur | Running with issues |  | Email | Pushpa | 2025-10-31 16:38 | technician@crystalgroup.in | Qwik Supply | TRIU6680335 | 20FT | 2011 | SERVICE-AT SITE | NA | NA | compressor is making an abnormal sound at the time of shutdown. The noise is due to compressor back pressure, indicating that the compressor is faulty and needs to be replaced. | Running with issue | Compressor daikin, Gas R134a 5 kg Filter drier, Ambent sensor, Supply sensor 2 nos, Vacuum pump required | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT122%2F25 | Na | DAIKIN | Na | Na | Na | Na | Na | NEMICHAND | Yes | COMPRESSOR MAKING NOISE | 2025-11-04 12:00 | crm@crystalgroup.in | YES | IN328 | 2025-11-03 |  |  |  |  | SITE |  |  | 2025-11-04 12:16 | crm@crystalgroup.in | YES | IN328 | YES |  | Stock | 2025-11-13 12:17 | crm@crystalgroup.in | YES | IN328 | COURIER | 53613449374 | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT122%2F25
OCT123/25 | 2025-10-22 16:24 | crm@crystalgroup.in | Offshore Canning | Mohammad Nehal | 8697104745 | Site in charge | MCRF4907002 | ALARM CODE VISIBLE |  | NA | Andaman | Complete Breakdown | AL-58 error code visible | Email | Pushpa | 2025-10-23 17:57 | technician@crystalgroup.in | Offshore Canning | MCRF4907002 | 20 | 2009 | SERVICE-ON CALL | NA | NA | Hp switch not connected | Immediate repair | Hp switch | Yes | Hp switch need to install | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT123%2F25 | Na | CARRIER-THINLINE | Na | Na | Na | Na | Na | Na | No | ALARM CODE VISIBLE | 2025-11-01 10:52 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-01 10:53 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-01 10:53 | crm@crystalgroup.in | NO | [7 empty] | 2025-11-07 11:40 | 2025-11-01 |  |  |  |  | MCRF4907002 |  |  |  | Carrier | -20'c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.9b 17.4b | 13.5A | 415v | Short | Compressor Installation on call | Unit working fine, | No | https://drive.google.com/open?id=1aoaznwhsaPztbQH9k3OIQM829lUsRsc7 | https://drive.google.com/open?id=1vrm5aCC8atPD3yDPGBsDpGfSO_4i_HEO |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT124/25 | 2025-10-27 15:08 | crm@crystalgroup.in | Lupin | Aakaash | 93705 88166 | Site in charge | CCLU1036859 | COMPRESSOR MAKING NOISE |  | NA | Bhiwandi | Running with issues |  | Email | Pushpa | 2025-10-30 16:45 | service@crystalgroup.in | Lupin | CCLU1036859 | 20FT | 2008 | MACHINE INSPECTION | NA | NA | compressor makig abnormal sound, technician at site for observation | technican need at site | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT124%2F25 | na | CARRIER-THINLINE | na | na | na | na | na | aman | Yes | COMPRESSOR MAKING NOISE | 2025-11-04 16:24 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-04 16:25 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-04 16:25 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT124%2F25
OCT125/25 | 2025-10-28 09:44 | crm@crystalgroup.in | Divis lab | Ramakrishna M | 96527 25368 | ON duty officer | CRIU4025195 | installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-29 22:50 | 26/10/0025 |  |  |  |  | CRIU4025195 |  |  |  | Thermo king | +2c,to 8c and -25 c test for Instalation | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/18 br | 9.8/9.8/9.9 | 402/403/402 | Short | New unit TK mp5000 for Instalation | Instalation process with unit brief PTI DONE. | No | https://drive.google.com/open?id=1YPsIjnx1KXu2Ptz15xfQrHzqiir827ec | https://drive.google.com/open?id=1FdpU9v9xupH5254HRwtDG4Z0_C1jSKTC |  | 124 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT126/25 | 2025-10-28 09:46 | crm@crystalgroup.in | Divis Lab | Ramakrishna M | 96527 25368 | ON duty officer | CRIU4025209 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-29 21:58 | 28/10/0025 |  |  |  |  | CRIU4025209 |  |  |  | Thermo king | +2c to + 8c & -25c for Instalation test done | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/17 bar | 9.0/9.1/ 9.0 | 403/402/402 | Short | New unit TK 5000 for Instalation | Instalation process complit and unit PTI ( Brief) done & with user TRANNING completed | No | https://drive.google.com/open?id=1Q84hAzeokzE3dC2mdV6EZagTiq1Kb3iU | https://drive.google.com/open?id=1TpuA6NiIbI0OebnSGugiSeHGJbx0ZQjL |  | 124 | No | No | Can be done on next PM | MOM - Claierance | Na | technician@crystalgroup.in | REEFER
OCT127/25 | 2025-10-28 09:48 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CRIU4025180 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-29 22:57 | 25/10/0025 |  |  |  |  | CRIU4025180 |  |  |  | Thermo king | For Instalation test 2/8 & -25c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/17 br | 9.8/9.9/9.8 | 502/401/402 | Short | New tk mp 5000 for Instalation | Instalation process has been completed with unit brief PTI PASS. | No | https://drive.google.com/open?id=1IHOdeXXm-ahpb6pTIU3bQ4PLOoFLcTGE | https://drive.google.com/open?id=1mTAjq701iK6osweqnWA_QBC3uE1s5Zph |  | 134 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT128/25 | 2025-10-28 09:50 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | CRIU4025214 | Installation |  | M.Ramakrishna@divislabs.com | Hyderabad | Installation |  | Email | Pushpa | [54 empty] | 2025-10-29 23:05 | 27/10/0025 |  |  |  |  | CRIU4025214 |  |  |  | Thermo king | 2/8c & -25c test for Instalation | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 8/18br | 9.9/9.8/9.9 | 402/402/401 | Short | New tk mp 5000 unit for Instalation | Instalation process has been completed with unit brief PTI PASS . Attached job order for reference | No | https://drive.google.com/open?id=16GVrTp43RxQI6pIzn1HscRovy-fnTpMJ | https://drive.google.com/open?id=17psl9DHV1ChT2S9-2v8UJGK5EkEZSfqd |  | 124 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
OCT129/25 | 2025-10-28 09:52 | crm@crystalgroup.in | DIVIS LAB | Ramakrishna M | 96527 25368 | ON duty officer | TRIU8339605 | AMC |  | M.Ramakrishna@divislabs.com | Hyderabad | AMC |  | Email | Pushpa | [54 empty] | 2025-10-29 23:12 | 26/10/0025 |  |  |  |  | DC SEZ -1 TRIU8339605 |  |  |  | Carrier | +3c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 10/200 psig | 12.8/12.7/12.8 | 402/401/402 | Short | Re instalation & pm service completed | Re instalation process completed and pm service completed. Attached job order | Yes | https://drive.google.com/open?id=1LkqqoG4KY7_xldDLEd0GSI43CZGCyJCR | https://drive.google.com/open?id=1BhnlQL9KNeH1v8QvQGVfiAGH1zu51jGg |  | 124 | No | No | Can be done on next PM | Na | ML 3 Controller Dts & htt sensors for Thin Line | technician@crystalgroup.in | REEFER
OCT130/25 | 2025-10-29 12:20 | crm@crystalgroup.in | Swiggy | Abhilash | 9000991909 | Site in charge | CRIU4023021 | Freezer rubber volve is not fitting into the door. Due to this air is released out temp will not be maintained. |  | NA | Banglore | Running with issues |  | Email | Pushpa | 2025-10-30 18:05 | service@crystalgroup.in | Swiggy | CRIU4023021 | 40FT | na | SERVICE-ON CALL | NA | NA | door gaskit need to refix | need to fix |  | No | door gaskit issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT130%2F25 | na | TK-MP4000 | na | na | na | na | na | other | Yes | Freezer rubber volve is not fitting into the door. Due to this air is released out temp will not be maintained. | 2025-11-04 16:27 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-04 16:28 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-04 16:28 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT130%2F25
OCT131/25 | 2025-10-29 16:25 | crm@crystalgroup.in | Swadesh Milk | RAJESH UPADHYAY | 8077759700 | NA | GESU9290991 | Evaporator coil leakage |  | NA | Lucknow | Complete Breakdown |  | Call | Sitaram | 2025-10-30 18:12 | service@crystalgroup.in | Swadesh Milk | GESU9290991 | 40FT | na | SERVICE-AT SITE | NA | NA | coil need to replace | urjent replace | evporator coil 1 nos, filter drier 1 nos | Yes | coil need replace | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT131%2F25 | na | CARRIER-THINLINE | nna | na | na | na | na | NEMICHAND | Yes | Evaporator coil leakage | 2025-11-10 15:48 | crm@crystalgroup.in | YES | IN343 | 2025-11-07 |  |  |  |  | SITE |  |  | 2025-11-10 15:49 | crm@crystalgroup.in | YES | IN343 | YES |  | Stock | 2025-11-11 11:24 | crm@crystalgroup.in | YES | IN343 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT131%2F25 | 2025-11-14 16:04 | 2025-11-10 |  |  |  |  | GESU9290991 |  |  |  | Carrier | -24C Ret.-23.4C Sup.-30.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Need to replace |  | Okay |  | Okay | Okay | Okay | Not done | Clean |  | 0.5bar 12.3bar | 12.3A 12.3A 12.3A | 414V | Not done | Breakdown | After observation of 36 hours, unit working fine , Evaporator coil and filter driver has been changed, unit maintain -24'c . Heat termination thermostat and defrost sensor defective need to be replaced | Yes | https://drive.google.com/open?id=1_wHcDbN9z_01coTC0AIXhN7KYtHhKqkI | https://drive.google.com/open?id=1fhTPwde5NcxmdQ9VOQrQ3S1pi4cbrSnK |  | 127 | Yes | Yes | Urgent | Heat termination thermostat Defrost sensor defective Compressor contactor | Heat termination thermostat Defrost sensor defective Compressor contactor | technician@crystalgroup.in | REEFER
OCT132/25 | 2025-10-30 09:30 | crm@crystalgroup.in | GMR Airport | Manoj kumar | 8008097255 | Site in charge | TITU9930006 | DISPLAY NOT VISIBLE |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-30 18:00 | service@crystalgroup.in | GMR Airport | TITU9930006 | 40FT | na | SERVICE-AT SITE |  |  | display need to replac | need to replace | mp4000 display | Yes | display issue | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT132%2F25 | na | TK-MP4000 | na | na | na | na | na | SHAHBUDDIN | Yes | DISPLAY NOT VISIBLE
OCT133/25 | 2025-10-30 10:06 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255/9154268772 | Site in charge | APRU5091041 | KEYPAD NOT WORKING |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-30 17:49 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | APRU5091041 | 40FT | na | SERVICE-AT SITE | NA | NA | keypad not working | need to visit | keypad 1 nos, silicone sealant 1 nos | Yes | keypd need to replce | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT133%2F25 | na | CARRIER-THINLINE | na | na | na | na | na | SHAHBUDDIN | Yes | KEYPAD NOT WORKING | 2025-11-13 12:06 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-13 12:06 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-13 12:07 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT133%2F25
OCT134/25 | 2025-10-30 10:13 | crm@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | Vishnu Vardhan | 9948366255 | Site in charge | PCIU6016370 | Sensors need to be replaced |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-30 17:40 | service@crystalgroup.in | Hetero Labs Ltd - Unit 3 (EOU) | PCIU6016370 | 40FT | na | SERVICE-AT SITE | NA | NA | sensor out of range | need to replace | temprature sensor daikin 4 nos, inlet sensor 1 nos, outlet sensor 1 nos | Yes | sensor out of range | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT134%2F25 | na | DAIKIN | na | na | na | na | a | SHAHBUDDIN | Yes | Sensors need to be replaced
OCT135/25 | 2025-10-30 10:21 | crm@crystalgroup.in | BEJAPURI DAIRY | LAKHWINDER SINGH | 9876772453 | Site in charge | MYRU4503459 | Pan grill needs to be replaced |  | NA | Patanchuru | Running with issues |  | Call | Shabuddin | 2025-10-30 17:34 | service@crystalgroup.in | BEJAPURI DAIRY | MYRU4503459 | 40FT | na | SERVICE-AT SITE | NA | NA | spare need to change | na | sheet key 1 nos, condensor fan grill (daikin) low side cap 1 nos | Yes | need to change | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT135%2F25 | na | DAIKIN | na | na | na | na | na | SHAHBUDDIN | Yes | Pan grill needs to be replaced | 2025-11-10 15:36 | crm@crystalgroup.in | YES | IN341 | 2025-11-06 |  | BEJAPURI DAIRY |  | MYRU4503459 | SITE |  |  | 2025-11-10 15:36 | crm@crystalgroup.in | YES | IN341 | YES |  | Stock
OCT136/25 | 2025-10-30 10:32 | crm@crystalgroup.in | ZENFOLD PHARMA PVT.LTD. | Harshavardhan | 9493560304 | Site in charge | TRIU6618637 | Sensors need to be replaced |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-30 17:30 | service@crystalgroup.in | ZENFOLD PHARMA PVT.LTD. | TRIU6618637 | 20FT | na | SERVICE-AT SITE | NA | NA | sensor out of calibration need to replace | ned to replace | supply sensor 2 nos, key pad 1 nos, internal tube light 1 nos | Yes | sensor out of range | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT136%2F25 | na | CARRIER-THINLINE | na | na | a | na | na | SHAHBUDDIN | Yes | Sensors need to be replaced | [12 empty] | 2025-11-18 11:57 | crm@crystalgroup.in | YES | IN359 | YES |  | Stock
OCT138/25 | 2025-10-30 17:17 | crm@crystalgroup.in | ASPIRO PHARMA | Tammar | 9959404803 | Site in charge | CAIU5422720 | Switch tripping |  | NA | Hyderabad | Running with issues |  | Call | Shabuddin | 2025-10-30 19:02 | service@crystalgroup.in | ASPIRO PHARMA | CAIU5422720 | 40FT | na | SERVICE-AT SITE | NA | NA | leak found from filter line | need repair | R134a gas 4.5kg, filter drier 1 nos, discharge sensor 1 nos, | Yes | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT138%2F25 | na | DAIKIN | na | na | na | na | na | SHAHBUDDIN | Yes | Switch tripping | 2025-11-07 10:38 | crm@crystalgroup.in | YES | IN342 | 2025-11-06 |  |  |  |  | SITE |  |  | 2025-11-13 15:28 | crm@crystalgroup.in | YES | IN342 | YES |  | Stock | 2025-11-13 15:32 | crm@crystalgroup.in | YES | IN342 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT138%2F25
OCT140/25 | 2025-10-31 17:42 | crm@crystalgroup.in | Flipkart | Piyush | 7020599174 | Site in charge | HDMU5537036 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Pune | Running with issues |  | Call | Sitaram | 2025-10-31 17:57 | service@crystalgroup.in | Flipkart | HDMU5537036 | 40FT STD RF + Dual Machine + Anteroom | 2011 | SERVICE-ON CALL | NA | NA | tmprature not meet setpoint, evporator motor giving alaram | need technicia at site | na | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=OCT140%2F25 | Carrier | DAIKIN | nna | n | na | used | na | aman | Yes | tmprature not meet setpoint, evporator motor giving alaram | 2025-11-04 16:32 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-04 16:33 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-04 16:33 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=OCT140%2F25
NOV001/25 | 2025-11-01 15:10 | crm@crystalgroup.in | Tan 90 Thermal Solutions | Abhishek | 8925800796 | Site in charge | CICU1625914 | ICE FORMATION |  | NA | Taloja | Running with issues |  | Email | Pushpa
NOV002/25 | 2025-11-01 16:42 | crm@crystalgroup.in | Kiaranakart Wholesale Private Limited | Tushar Bhogale | 919930209385 | Site in charge | TITU9928040 |  |  | NA | Pune | Preventive Maintenance |  | Email | Pushpa | 2025-11-08 22:36 | service@crystalgroup.in | Kiaranakart Wholesale Private Limited | TITU9928040 | 40FT Spl RF | na | SERVICE-AT SITE | NA | CHARGEABLE | na | na |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV002%2F25 | NA: Thermoking MP-4000; NA: DAIKIN; -: Used; NO: SHAHBUDDIN; No: No | na | 2025-11-08 22:38 | service@crystalgroup.in | NO | [9 empty] | 2025-11-09 13:30 | service@crystalgroup.in | NO |  |  |  |  | 2025-11-09 13:30 | service@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV002%2F25
NOV003/25 | 2025-11-01 17:20 | crm@crystalgroup.in | Qwik Supply | Mangesh Vannere | 7020374749 | Site in charge | CICU1442240 |  |  | NA | Pune | Preventive Maintenance |  | Email | Pushpa
NOV004/25 | 2025-11-01 17:23 | crm@crystalgroup.in | Qwik Supply | Mangesh Vannere | 7020374749 | Site in charge | PCIU6015055 |  |  | NA | Pune | Preventive Maintenance |  | Email | Pushpa
NOV005/25 | 2025-11-01 17:28 | crm@crystalgroup.in | Gennova | Ganesh Late | 70660 00195 | Site in charge | CICU2093992 | As per the agreement this is 3rd visit |  | NA | Pune | AMC |  | Email | Pushpa | [54 empty] | 2025-11-10 13:40 | 04/11/0025 |  |  |  |  | CICU2093992 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/18br | 9.8/9.9/9.8 | 404/403/403 | Short | Pm service due. | Pm service completed with checked unit operation And found working as satisfactory. Photo & job order are submitted. | No | https://drive.google.com/open?id=1t7q4ZJGOZ2XF5oxw26KDnsbrJRZV9gtX | https://drive.google.com/open?id=1irihc6csj29Bj84hDDdUpVMRUMW5Cbhz |  | 129 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV006/25 | 2025-11-01 17:30 | crm@crystalgroup.in | Gennova | Ganesh Late | 70660 00195 | Site in charge | CICU2094005 | As per the agreement this is 3rd visit |  | NA | Pune | AMC |  | Email | Pushpa | [54 empty] | 2025-11-10 13:33 | 04/11/0025 |  |  |  |  | CICU2094005 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .6/17 6br | 9.8/9.9/9.9 | 402/403/402 | Short | Pm service due. | Pm service completed with checked unit operation And found working as satisfactory. .photo & job order are submitted. | No | https://drive.google.com/open?id=1YKz6pEzSWwMPMK3ow6B_tno94AHoFCxI | https://drive.google.com/open?id=1UFVe6XE94zGem_4CncT2N-lQLm7bWHKm |  | 129 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV007/25 | 2025-11-01 17:31 | crm@crystalgroup.in | Gennova | Ganesh Late | 70660 00195 | Site in charge | CICU2094010 | As per the agreement this is 3rd visit |  | NA | Pune | AMC |  | Email | Pushpa | [54 empty] | 2025-11-10 13:28 | 04/11/0025 |  |  |  |  | CICU2094010 |  |  |  | Thermo king | 3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/18br | 9.9/9.9/9.8 | 403/403404 | Short | Pm service due.. | Pm service completed with checked unit operation And found working as satisfactory. Photo & job order are submitted. | No | https://drive.google.com/open?id=12UwvzCvduEk77ilhuaG6MhJgtzjKp0Kx | https://drive.google.com/open?id=1ayLrffSD90rMUQGTnEgk48wonjiyYm-L |  | 129 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV008/25 | 2025-11-01 17:32 | crm@crystalgroup.in | Gennova | Ganesh Late | 70660 00195 | Site in charge | CICU2094026 | As per the agreement this is 3rd visit |  | NA | Pune | AMC |  | Email | Pushpa | [54 empty] | 2025-11-10 13:23 | 04/11/0025 |  |  |  |  | CICU2094026 |  |  |  | Thermo king | +3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/17br | 9.8/9.9/9.8 | 403/402/403 | Short | Pm service due | Pm service completed with checked unit operation And found working as satisfactory. Photo & job order are submitted. | Yes | https://drive.google.com/open?id=1XZbajckK1fYhIKQ2Snl2lc5vhEtaER6w | https://drive.google.com/open?id=1iM3zWpGnk-6QiXMGofrPdv-XzF4EG1kQ |  | 129 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV009/25 | 2025-11-01 17:33 | crm@crystalgroup.in | Gennova | Ganesh Late | 70660 00195 | Site in charge | CICU1938565 | As per the agreement this is 3rd visit |  | NA | Pune | AMC |  | Email | Pushpa | [54 empty] | 2025-11-10 13:17 | 04/11/0025 |  |  |  |  | CICU1938565 |  |  |  | Thermo king | + 3.5c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .4/6 & 11/19 | 9.8/12.3&9.9/12.4/& 9.8/12.5 | 304/405/494 | Short | Due for pm service | Pm service completed with checked unit operation And found working as satisfactory. Photo & job orders submitted | No | https://drive.google.com/open?id=11J-1wFY-W_y_reCf6zCLgYsBbJ1BobUM | https://drive.google.com/open?id=16FKFIHnsyaRqBqXJhx80PBxUaPx40HVL |  | 129 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV010/25 | 2025-11-02 14:17 | service@crystalgroup.in | SWITZ INTERNATIONAL | VIJAY | 9820223249 | SITE IN CHARGE | TITU8259465 | GAS TOP-UP |  | VIJY@INDIA.SWITZGROUP.COM | DAMAN | Complete Breakdown |  | Call | SITA RAM | 2025-11-02 14:20 | service@crystalgroup.in | SWITZ INTERNATIONAL | TITU8259465 | 20FT Spl RF | NA | SERVICE-AT SITE | NA | NA | LEAK | NA | GAS TOP-UP 5KG | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV010%2F25 | Thermoking MP-4000 | TK-MP4000 | NA |  | NA | Brand New | NA | AVINASH | Yes | BREAKDOWN | 2025-11-04 11:13 | crm@crystalgroup.in | YES | IN327 | 2025-11-02 | Consumables | SWITZ INTERNATIONAL |  | TITU8259465 | SITE
NOV011/25 | 2025-11-02 14:35 | service@crystalgroup.in | QWIK SUPPLY | ATUL VERMA | 9273494889 | SITE IN CHARGE | APRU5066497 | GAS TOP-UP |  | ATUL.VARMA@QWIK.CO.IN | SURAT | Complete Breakdown | GAS NEED TO ARRANGE | Call | SITA RAM | 2025-11-02 14:38 | service@crystalgroup.in | Qwik Supply | APRU5066497 | 40FT STD RF | NA | SERVICE-AT SITE | NA | NA | SAME | IMMEDIATE |  | GAS R134A | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV011%2F25 | NA: Carrier - Thinline; NA: CARRIER-THINLINE; -: JSGA623040296; NO: AVINASH; No: Yes | GAS NEED TO ARRAGE FOR REPAIR | 2025-11-04 11:30 | crm@crystalgroup.in | YES | IN326 | 2025-11-02 |  | SWITZ INTERNATIONAL |  | TITU8259465 | SITE |  |  | 2025-11-13 16:05 | crm@crystalgroup.in | YES | IN326 | YES |  | Stock | 2025-11-13 16:53 | crm@crystalgroup.in | YES | IN326 | COURIER | NA | NA |  |  | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV011%2F25
NOV012/25 | 2025-11-03 17:53 | crm@crystalgroup.in | Bamfood | Tanveer | 7620464560 | Site in charge | TDRU7155407 | Sensors need to be replaced |  | Na | Goa | Running with issues |  | Email | Pushpa | 2025-11-04 16:45 | technician@crystalgroup.in | Bamfood | TDRU7155407 | 40FT STD RF | 2011 | SERVICE-ON CALL | SALE | AMC | Compressor need to change | Immediate | Compressor daikin 1 n'os Compressor contractor 1 no's Supply sensor 2 no's Filter drier 1 no's Gas 5 kg R134a Vacuum pump required | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV012%2F25 | Daikin | DAIKIN | Na | Na | Na | USed | Na | AMAN | Yes | Compressor not working
NOV013/25 | 2025-11-04 14:49 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Rajpura | SJKU4000022 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | 2025-11-08 22:33 | technician@crystalgroup.in | Qwik Supply | SJKU4000022 | 40FT STD RF | Na | SERVICE-AT SITE | NA | FOC | Na | Na |  | No | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV013%2F25 | NA: Carrier-Primeline; NA: CARRIER-PRIMLINE; -: JSGA623040175; NO: Na; No: No | Na | 2025-11-09 12:57 | service@crystalgroup.in | NO | [9 empty] | 2025-11-09 12:57 | service@crystalgroup.in | NO |  |  |  |  | 2025-11-09 12:58 | service@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV013%2F25 | 2025-11-05 09:37 | 04/11/0025 |  |  |  |  | SJKU4000022 |  |  |  | Carrier | +2C Sup.+1.9C Ret.+2.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 1.7bar Discharge 10.8bar | R 8.6A B 9.2A Y 8.6A | 395V 395V 395V | Not done | Pm service and general inspection | Condenser motor bearing replaced and service | No | https://drive.google.com/open?id=1PVbzmVRY-xF1wydDHpUPTQ-PBPDLdpYP | https://drive.google.com/open?id=1MbMXkVGBfVK5ZxNE5GzqPsS-4jvRfWUH |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV014/25 | 2025-11-04 14:50 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Site in charge | CICU8118130 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | [54 empty] | 2025-11-05 09:27 | 04/11/0025 |  |  |  |  | CICU8118130 |  |  |  | Thermo king | -20C Ret.-18.6C Sup.-24.9C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.7bar Discharge 15.7bar | R 9.4A B 9.8A Y 9.4A | 386V 386V 386V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1E1uixDBqgHWDser0fI56Ei3CBuRBudx_ | https://drive.google.com/open?id=1Mt8mOCLEX1zjcmy2z_jH46dbdsqNcfvg |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV015/25 | 2025-11-04 14:52 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Site in charge | CXRU1045453 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | [54 empty] | 2025-11-05 09:31 | 04/11/0025 |  |  |  |  | CXRU1045453 |  |  |  | Daikin | -18C Ret.-17.6C Sup.-25.7A | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 29LPT Discharge 1485HPT | 12.8A 9.0A | 397V 397V 397V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1hU9aQhTAtuysnSGsMd3XunO6PCQVgA3c | https://drive.google.com/open?id=17Z40xLGX97DxL97YTNS9lAUNXBFrWZ5Z |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV016/25 | 2025-11-04 14:53 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Site in charge | TCLU1130265 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | [54 empty] | 2025-11-05 09:18 | 04/11/0025 |  |  |  |  | TCLU1130265 |  |  |  | Thermo king | +3C Ret.+3.1C Sup.+2.8C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6bar Discharge 14.3bar | R 10.4A B 9.6A Y 10.3A | 391 V 391 V 391 V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1PEZKaNpIf59EsxcV18OIQ6guKhSy1XXq | https://drive.google.com/open?id=11KVgKtZOccTbn1XU4YYoKVkIRUUOqVWO |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV017/25 | 2025-11-04 14:54 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Site in charge | CICU3876631 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | [54 empty] | 2025-11-05 09:13 | 04/11/0025 |  |  |  |  | CICU3876631 |  |  |  | Thermo king | -40C Ret.-34.3C Sup.-40.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.7bar Discharge 14.9bar | R 9.3A B 9.3A Y 9.8A | 395V 395V 395V | Not done | Pm service and general inspection | Battery replaced | No | https://drive.google.com/open?id=1CiOntv32DIv--JsyWxBYCwwrr9OBrb0D | https://drive.google.com/open?id=1FS2O_S7GX1-Z5bH8yuxPIpUaoR7DuP9f |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV018/25 | 2025-11-04 14:55 | crm@crystalgroup.in | Qwik Supply | Ranveer | +91 98726 09126 | Site in charge | CICU3876570 |  |  | NA | Rajpura | Preventive Maintenance |  | Email | Sitaram | [54 empty] | 2025-11-05 09:23 | 04/11/0025 |  |  |  |  | CICU3876570 |  |  |  | Thermo king | -40C Ret.-38.7C Sup.-42.3C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Suction 0.6Bar Discharge 15.6bar | R 10.5A B 10.2A Y 10.0A | 394V 394V 394V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1PigKgaTy2_Mom-6w3PnzvZgFyGXYFvYG | https://drive.google.com/open?id=1uxpUGuvYhQsEoOOCa2NVw65uHFXx6fyB |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV019/25 | 2025-11-04 17:39 | crm@crystalgroup.in | Amul Dairy | Saurav Kumar | 917261047555 | Site in charge | TRIU6644889 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Patna | Running with issues |  | Email | Pushpa | 2025-11-06 19:19 | service@crystalgroup.in | Amul Dairy | TRIU6644889 | 20FT | 2011 | SERVICE-ON CALL | NA | NA | gas leakage not found. unit maintain only plus 5C temprature. need to N2 test and gas charge | allign technician after complete lucknow | gas R134a 5 kg, N2 test require, Vacume required, if leak found brizing required | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV019%2F25 | NA: CARRIER-THINLINE; NO: NEMICHAND; No: Yes | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-11-07 10:45 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-07 10:45 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-13 13:02 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV019%2F25 | 2025-11-14 16:24 | 2025-11-14 |  |  |  |  | TRIU6644889 |  |  |  | Carrier | -5C Sup.-5.6 Ret.-6.8C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.5bar 9.7bar | 8.6A 8.6A 8.6A | 406V | Not done | As per clint unit have issue, temperature not meet set point. | After checking properly and found humidity sensor defective, after disconnect humidity sensor unit working fine and reached-18. | Yes | https://drive.google.com/open?id=1PCM_rTy7VDWQ384kWxdVMqIr4UpxasZs | https://drive.google.com/open?id=18M5gF1MmgEUfvyDKRKWieU0ojYqc46IF |  | 127 | Yes | No | Urgent | Humidity sensor Carrier contractor 12A | Humidity sensor 1nos Carrier connector 12A 1nos | technician@crystalgroup.in | REEFER
NOV020/25 | 2025-11-05 16:11 | crm@crystalgroup.in | Tata Advance | Sachin | 7337832756 | Site in charge | CBHU2811760 | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE |  | NA | Banglore | Running with issues |  | Email | Pushpa | 2025-11-06 19:23 | service@crystalgroup.in | Tata Advance | CBHU2811760 | 40FT | na | SERVICE-ON CALL | NA | NA | as discussed with clint unit working fine , no issue found | not required |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV020%2F25 | NA: CARRIER-THINLINE; NO: na; No: No | TEMPERATURE NOT ACHIEVED UP TO SET TEMPERATURE | 2025-11-07 10:43 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-07 10:44 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-09 12:54 | service@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV020%2F25 | 2025-11-09 21:22 | 2025-11-09 |  |  |  |  | CBHU2811760 |  |  |  | Thermo king | On call | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | On call | On call | On call | Not done | On video call with customer before not maintaining temperature | After details on video call unit working fine | No | https://drive.google.com/open?id=1OQ7wyShDEIwcdlwtI9tWR6rrf2HKGU_w | https://drive.google.com/open?id=1r6Pbyz3zED2A53fD36IWYc2l5j8qzUe3 |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV021/25 | 2025-11-05 16:12 | crm@crystalgroup.in | Tata Advance | Sachin | 7337832756 | Site in charge | CZZU6009100 | DISPLAY NOT VISIBLE |  | NA | Banglore | Running with issues |  | Email | Pushpa | 2025-11-08 22:31 | service@crystalgroup.in | Tata Advance | CZZU6009100 | 40FT | na | SERVICE-AT SITE | NA | NA | motor by pass | arranging spare | evp motor with blade, sheet key, display | Yes | mtor not norking | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV021%2F25 | NA: DAIKIN; NO: SHAHBUDDIN; No: Yes | DISPLAY NOT VISIBLE
NOV022/25 | 2025-11-06 15:14 | crm@crystalgroup.in | Qwik Supply | Amol Wagmare | 7620604435 | Site in charge | CISU1442240 |  |  | NA | Pune | Preventive Maintenance |  | Call | Shahbudin | 2025-11-09 12:43 | service@crystalgroup.in | Qwik Supply | CISU1442240 |  | na | PREVENTIVE MAINTENANCE | NA | NA | pm | pm |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV022%2F25 | NA: DAIKIN; NO: SHAHBUDDIN; No: No | Preventive Maintenance | 2025-11-09 12:51 | service@crystalgroup.in | NO | [9 empty] | 2025-11-09 12:52 | service@crystalgroup.in | NO |  |  |  |  | 2025-11-09 12:52 | service@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV022%2F25 | 2025-11-10 12:57 | 06/11/0025 |  |  |  |  | CISU1442240 |  |  |  | Thermo king | -40c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | .7/18 br | 10.1/10/10.1 | 413/414/413 | Short | Pm service due & door gasket damaged. With al 097 Internal light need to changed. | Pm service completed with clean unit & condenser coil with fresh normal pressure wter . Run unit checked operation and found compressor sensor reading abnormmal need to replaced. With internal light * Damaged door gasket repaired . | Yes | https://drive.google.com/open?id=1aZT7xfi9Au-lG8Yb0K7zWiJ_LDuuwkJO | https://drive.google.com/open?id=1DQNQviLXg35GFy2iuO0BSzmPTTbBYUUX |  | 129 | No | No | Can be done on next PM | Sensor & light | Internal light need to replaced with need to replaced compressor sensor tk mp 4000 | technician@crystalgroup.in | REEFER
NOV023/25 | 2025-11-06 15:15 | crm@crystalgroup.in | Qwik Supply | Amol Wagmare | 7620604435 | Site in charge | PCIU6015055 |  |  | NA | Pune | Preventive Maintenance |  | Call | Shahbudin | [54 empty] | 2025-11-10 13:04 | 05/11/0025 |  |  |  |  | PCIU6015055 |  |  |  | Daikin | -18c | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Need to replace |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 9/185psig | 9.9/10/9.9 | 413414/414 | Short | Pm due with Door damaged | Pm service completed with repaired damaged door.. Photo & job order submitted | Yes | https://drive.google.com/open?id=12GN9cPhgYeDTqUXj90TIcF6lMonFkEkn | https://drive.google.com/open?id=1waNihhOohWp5mLtwauoA8cZvqlv93GO5 |  | 129 | No | No | Can be done on next PM | Sheet key rep | Daikin shhet key | technician@crystalgroup.in | REEFER
NOV024/25 | 2025-11-06 16:06 | crm@crystalgroup.in | Michelin | Karthik | 7825827612 | Site in charge | KKFU6706142 | COMPRESSOR MAKING NOISE |  | NA | Chennai | Running with issues |  | Email | Pushpa | 2025-11-06 19:29 | service@crystalgroup.in | Michelin | KKFU6706142 | 40FT | na | SERVICE-ON CALL |  |  | clint request to visit technician at site , | working on it |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV024%2F25 | NA: DAIKIN; NO: na; No: Yes | COMPRESSOR MAKING NOISE | 2025-11-07 10:40 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-07 10:41 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-13 13:03 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV024%2F25 | 2025-11-16 14:28 | 2025-11-14 |  |  |  |  | KKFU6706142 |  |  |  | Carrier | 4 | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 0.4B 15.4B | 14.4A | 410V | Short | As per clint unit not getting on | After check and find extension socket not properly, unit working fine | No | https://drive.google.com/open?id=1TSXkKpwTxDdtfUat7I8W6MfR-tbliPQm | https://drive.google.com/open?id=1WSJh6MZb9I1cC2v0dRFur4mqIkZSzJZ8 |  | 130 | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV025/25 | 2025-11-06 16:09 | crm@crystalgroup.in | Qwik Supply | Karthik | 7825827612 | Site in charge | CXRU1033719 | COMPRESSOR MAKING NOISE |  | NA | Chennai | Running with issues |  | Email | Pushpa | 2025-11-06 19:27 | service@crystalgroup.in | Qwik Supply | CXRU1033719 |  | na | SERVICE-ON CALL |  |  | technician need to visit site | arranging technician to visit site |  | No | na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV025%2F25 | NA: CARRIER-THINLINE; NO: na; No: No | COMPRESSOR MAKING NOISE | 2025-11-07 10:42 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-07 10:42 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-13 13:03 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV025%2F25 | 2025-11-14 08:25 | 2025-11-12 |  |  |  |  | CXRU1033719 |  |  |  | Daikin | Na | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | Na | Na | Na | Not done | Na | As per complaint compressor making noise, but after check found normal function, unit working finr | No | https://drive.google.com/open?id=1SrIi4C0J_XWe7fHFI8n0_eJ6SbWnZZnp | https://drive.google.com/open?id=1PxsTfkGOWE6HUYsXNg3oWQjDicfdHw8l |  | Na | No | No | Can be done on next PM | Na | Na | technician@crystalgroup.in | REEFER
NOV029/25 | 2025-11-08 12:29 | crm@crystalgroup.in | QWIK SUPPLY | ATUL VERMA | 9273494889 | Site in charge | APRU5066497 | COMPRESSOR MAKING NOISE |  | NA | Surat | Complete Breakdown |  | Email | Pushpa | 2025-11-08 12:40 | technician@crystalgroup.in | Qwik Supply | APRU5066497 | 40FT STD RF | Na | SERVICE-ON CALL | NA | NA | Compressor need to change , | Arranging compressor | Compressor thin line 1 nos, Gas R134a 5kg, vacume pump, Hp switch, Compressor contractor 30A, Filter drier 1 nos | Yes | Due to electricity fluctuation | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV029%2F25 | NA: Carrier - Thinline; NA: CARRIER-THINLINE; -: JSGA623040296; NO: NEMICHAND; No: Yes | Compressor not working | 2025-11-08 16:16 | crm@crystalgroup.in | NO | [9 empty] | 2025-11-08 16:16 | crm@crystalgroup.in | NO |  |  |  |  | 2025-11-08 16:17 | crm@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV029%2F25
NOV030/25 | 2025-11-10 10:19 | crm@crystalgroup.in | Crystal Yard | Shubham | NA | NA | SJKU4000038 | Refurbishment |  | NA | JNPT | Refurbishment |  | Email | Sushma | 2025-11-12 15:52 | qualitycontrol@crystalgroup.in | Crystal Yard | SJKU4000038 | 40FT | CARRIER PRIMELINE | READINESS OF CONTAINER | NA | CHARGEABLE | PRIMARY UNIT HAS COMPRESSOR DEFECTIVE & SECONDARY HAS STEPPER MOTOR, ALSO THE SECONDARY COMPRESSOR FAULTY SUSPECTED. | NEED TO REPLACE COMPRESSOR & STEPPER MOTOR | PRIMELINE COMRESSOR, STEPPER MOTOR | Yes | NA | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV030%2F25 | CARRIER PRIMELINE | CARRIER-PRIMLINE | NA | NA | NA | USED | NA | SITARAM | Yes | Refurbishment
NOV031/25 | 2025-11-12 18:09 | sushma.poojari@crystalgroup.in | Qwik Supply | Gopal Krishna | 6307373723 | Store Manager | MYRU4518356 |  |  | gopal5.krishna@qwick.co.in | Lucknow | Preventive Maintenance |  | Call | Sitaram | 2025-11-15 08:10 | technician@crystalgroup.in | Qwik Supply | MYRU4518356 |  | Na | PREVENTIVE MAINTENANCE |  |  | Pm Pm | Pm |  | No | Pm | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV031%2F25 | NA: DAIKIN; NO: NEMICHAND; No: No | Preventive Maintenance | 2025-11-15 08:12 | technician@crystalgroup.in | NO | [9 empty] | 2025-11-15 08:12 | technician@crystalgroup.in | NO |  |  |  |  | 2025-11-15 08:13 | technician@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV031%2F25 | 2025-11-16 14:39 | 2025-11-09 |  |  |  |  | MYRU4518356 |  |  |  | Daikin | +18C Sup.+19.8C Ret.+18.6C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | 45LPT 1260HPT | 13.6A 13.6A 13.6A | 445V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1Qa6hs76kwOXgB9TMYA5MzMVBTI3aH35C | https://drive.google.com/open?id=1WC342ZAw2GFBtsvC_ZA65S6P60n6iqtr |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV032/25 | 2025-11-12 18:12 | sushma.poojari@crystalgroup.in | Qwik Supply | Gopal Krishna | 6307373723 | Store Manager | TCLU1903088 |  |  | gopal5.krishna@qwick.co.in | Lucknow | Preventive Maintenance |  | Call | Sitaram | 2025-11-15 08:10 | technician@crystalgroup.in | Qwik Supply | TCLU1903088 |  | Na | PREVENTIVE MAINTENANCE |  |  | Na | Na |  |  | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV032%2F25 | NA: DAIKIN; NO: NEMICHAND; No: No | Preventive Maintenance | 2025-11-15 08:12 | technician@crystalgroup.in | NO | [9 empty] | 2025-11-15 08:12 | technician@crystalgroup.in | NO |  |  |  |  | 2025-11-15 08:13 | technician@crystalgroup.in | NO | [6 empty] | https://docs.google.com/forms/d/e/1FAIpQLSesKfohNQciZb9KWxlULscnQpornxWhXjuDy0b033vLOe3yww/viewform?usp=pp_url&entry.626594502=NOV032%2F25 | 2025-11-16 14:45 | 2025-11-09 |  |  |  |  | TCLU1903088 |  |  |  | Daikin | -25C Ret.-24.8C Sup.-30.4C | Clean | Clean |  | Okay | Clean | Okay | Okay |  | Okay |  | Okay |  | Okay |  | Okay |  | Okay | Okay |  | Okay |  | Okay | Okay | Okay | Done | Clean |  | -20LPT 1050HPT | 9.1A 9.1A 9.1A | 445V | Not done | Pm service and general inspection | Attended routine checkup of container. Verified all operations are normal. Container functioning within range temperature. | No | https://drive.google.com/open?id=1WWvkgIO6bn3hFLRM6m_WUkvZ6MlNz3tr | https://drive.google.com/open?id=1aLlFwv9v1P75R9pOHp0bv9XwcGxNCxLy |  | 127 | No | No | Can be done on next PM | No | No | technician@crystalgroup.in | REEFER
NOV033/25 | 2025-11-13 10:06 | crm@crystalgroup.in | Qwik Supply | Mangesh Vannere | 7020374749 | Site in charge | PCIU6015055 | Sheet key issue |  | Mangesh.Vannere@ril.com | Pune | Running with issues |  | Call | Sitaram | 2025-11-13 10:23 | service@crystalgroup.in | Qwik Supply | PCIU6015055 | 40FT STD RF | Na | SERVICE-AT SITE | NA | NA | Sheet key defective | Arranging spare | Sheet key daikin | Yes | Need to replace | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV033%2F25 | Daikin | DAIKIN | NA | NA | NA | used |  | AMAN | Yes | Sheet key defective need to replace
NOV034/25 | 2025-11-13 10:31 | crm@crystalgroup.in | Qwik Supply | Mangesh Vannere | 7020374749 | Site in charge | CICU1442240 | TK compressor sensor |  | Mangesh.Vannere@ril.com | Pune | Running with issues |  | Call | Sitaram | 2025-11-13 13:49 | service@crystalgroup.in | Qwik Supply | CICU1442240 | 10 FT BLAST | Na | SERVICE-AT SITE | NA | NA | Need to replace compressor temperature sensor | Na | TK compressor temperature sensor 1 no's | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV034%2F25 | NA: Thermoking; NA: TK-MP4000; -: Brand New; NO: AMAN; No: Yes | Sensors defective
NOV039/25 | 2025-11-15 11:14 | crm@crystalgroup.in | Eugia Steriles | Deepak | 8924352890 | Site in charge | CICU2093987 | gas level low |  | Na | Vizag | Running with issues |  | Email | Pushpa
NOV040/25 | 2025-11-15 11:17 | crm@crystalgroup.in | DRL biologist | Suresh | 9908125456 | Site in charge | TITU9930074 | MOTOR MAKING NOISE |  | NA | Hyderabad | Running with issues |  | Call | Sitaram
NOV043/25 | 2025-11-17 17:18 | crm@crystalgroup.in | kaira District Cooperative Milk Producers' Union Ltd | Anuran banerjee | 9163870479 | SIte in charge | TRIU6616911 | Need to change motor |  | NA | Beghusrai | Running with issues |  | Call | Sitaram | 2025-11-17 17:24 | technician@crystalgroup.in | kaira District Cooperative Milk Producers' Union Ltd | TRIU6616911 | 20FT STD RF | Na | SERVICE-AT SITE | NA | CHARGEABLE | Motor defective | Na | Evaporator motor singal phase carrier | Yes | Na | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV043%2F25 | Carrier - Thinline | CARRIER-PRIMLINE |  | M3X60329564 |  | Used |  | NEMICHAND | Yes | Evp motor deactivate
NOV045/25 | 2025-11-18 12:05 | crm@crystalgroup.in | Swadesh Milk | RAJESH UPADHYAY | 8077759700 | Site in charge | NYKU7932356 | Complete Breakdown |  | NA | Lucknow | Complete Breakdown |  | Call | Sitaram | 2025-11-18 13:19 | technician@crystalgroup.in | Swadesh Milk | NYKU7932356 | 40FT STD RF | Na | SERVICE-AT SITE | SALE | CHARGEABLE | Same | Immediate need to repair | Compressors contractor 30A 4 nos carrier 12A contractor 4 nos Defrost sensor carrier 1 nos HTT carrier 1 nos | Yes | Same | https://docs.google.com/forms/d/e/1FAIpQLSfQWbOH4eQbo0gS6bP_PYfSINndMQwnvh88xI1O4H6C7pPpTg/viewform?usp=pp_url&entry.1819116387=NOV045%2F25 | NA: Carrier; NA: CARRIER-THINLINE; -: Used; NO: NEMICHAND; No: No | Not working due to compressors contractor burnt